Request for Proposal (RFP):

MIC2 HABBOUSH SERVICE CENTER

civil Works, ELECTRICAL & Lighting,

Network Cabling and HVAC

MOBILE INTERIM COMPANY NO.2 S.A.L.

Po.box 175051 Beirut-Lebanon

Contents

1	Scope of Work	3

2	Technical Specifications	4

2.1	CEILING	4

2.2	FLOORING	4

2.3	WALLS	5

2.4	PAINTING	5

2.5	PLUMBING & SANITARY	5

2.6	ELECTRICITY & LIGHTING	8

2.7	NETWORK CABLING:	12

2.8	HVAC	13

3	Appendices	13

3.1	Annex (1)	13

3.2	Annex (2)	14

3.2.1	PREAMBLE	14

Scope of Work

The primary objective of this RFP is to select the bidder(s) experienced in 3D layouts design and for the provision of the Civil, Electrical/Network Cabling and HVAC Works as per the Technical Specifications and preliminary layout enclosed in this RFP Habboush service centers

The preliminary layouts, enclosed in Annex (1) related to Appendix 1 “Technical Specifications”, are for the existing Service Centers and represent an example to give Bidders an idea of the scope of work. Final design/layout for all Service Centers and the related BoQs (Annex 2 of Appendix 1 “Technical Specifications”) shall be completed and submitted by the Bidders following the mandatory site visits.

The Scope of Work is mainly two parts:

- Item#1: 3D layout design for Habboush service center based on the enclosed preliminary layout “Site visits will be conducted in due time”.

- Item#2: Implementation of the above design including civil, electrical, lighting, HVAC works

Accordingly, the Bidders shall provide offers for the Civil, Electrical & Lighting, Network Cabling and HVAC Works to “MIC 2” for its new and existing Service Centers and they should submit their Commercial and Technical offers including 3D layout design, floor layouts and elevations along with their price list (per m² and per unit price) as per MIC2 design and as per the below technical specifications whereby, suppliers need to comply with.

Moreover, suppliers must perform a site visit prior to RFP submission for adjusting the design, which will affect the BOQ & Technical Specifications.

Bidders should conform to the timeline and plan proposed by MIC2 for the implementation of the new RSCs under the condition that the maximum period to finalize the Civil Works shouldn’t exceed 3 months.

Suppliers will be paid according to the approved As Built upon the completion of each project and MIC2 has the right to change, edit, replace and delete any of the items listed in the Technical Specification/BOQ based on the approved design and/or needs accordingly.

Technical Specifications

## CEILING

- Provide and install Plain Gypsum Concealed False ceiling at specified height, made of 1/2” thick Gypsum board placed on aluminum “T” frame, hung to structural ceiling with hangers.

- Provision of light access holes, AC as 10cm from each side and 30cm from controller side, grill openings, light openings or pelmets to be complete.

- Manufacture and supply of wooden false ceiling at specified location and height made of 18mm water resistant mdf wood coated with High Pressure Laminate sheets Polyrey ref B170 BRIHG Color Blanc Absolu, 1.2mm thickness. This includes suspension system, applying openings for lighting fixtures, all types of plugs, screws, glues, scaffolding…. And all type of machinery required completing the work according to drawings.

- Provide and install 60cm x 60cm suspended drop False ceiling at specified height, placed on aluminum “T” frame, hung to structural ceiling with hangers, inside the server room, Kitchen and WC blocks.

- Provision for Exhaust fan openings, to be complete as per design and drawings.

## FLOORING

- Preparation of the sub-base, to be well-dressed to the desired level. Loose spots shall be excavated till the hard surface is reached, then well wetted and cleaned thoroughly.

- To lay cement mortar, thickness 30mm average with white tile adhesive.

- Supply and installation of White Ceramic tiles different sizes, 6mm thick, including dressing and cutting edges to required size and right angles, sorting and laying to required level/slope in approved pattern on a bedding of 50-75mm thick…. Size : 60mm x 60mm.

- Finishing the joints with matching color curing, machine polishing, perfect matching and leveling of joints, substantiated by hand-polishing wherever required.

- Supply and installation of 80mm plinths all around flooring, same specifications as above.

- Supply and installation of White ceramic tiles,45cm x 45cm,  6mm thick, for WC, kitchen, service room, WC walls and Kitchen backsplash.

## WALLS

- Manufacturing and installation of wall, made from Gibson board as per drawing to open windows to show screen behind. The wall to be mounted on the screen steel structure chassis, in coordination with the screen provider.

- The wall to be completed from the back by 6 hinged Laminated wooden doors (250cm x 43cm) with large grilling surface as per approved design.

- The wall to be completed by a hidden door, made from mdf wood to close a storage area, with large grilling surface.

- Painting the door and remaining panel in polyurethane glossy finish, applying of primer and 2 coats in smooth spraying, including rubbing the surface with rubbing brick / sand papers, and plaster filling.

- Wooden canopy placed on up and down sides of the wall to handle indirect led strips lighting, along with a groove of 700mm x 700mm Painting the canopy in white as per drawings.

- Supply manufacturing and installation of a 9 locker wall unit made from wood, painted polyurethane spray finish white with 6mm clear glass lockable doors having high quality locks and hitches. With Electricity outlets in each locker.

- Supply, manufacturing and installation of 5 white back walls of 1200mm wide each, fixed on wooden channels of 95mm, getting a continuous unit from the ceiling to the ground, with same materials Each wall to be made of 18mm water resistant mdf wood and 100mm depth, with 20mm of decorative hollow joint coated with High Pressure Laminate sheets Polyrey ref B170 BRIHG Color Blanc Absolu, 1.2mm thickness the entire assembly to be concealed as one element. The set to lay directly on ground.

- Providing & fixing 12 mm thick tough fully tempered glass partition in combination of fixed/open able glass up to false ceiling & fixed to floor by glass downwards into tile floor. Operable glass to be supported on special patch fittings at directed locations with open able door operated on Patch fittings having upper/lower/side patch with EPC lock, 300 mm handle & strike plate of make DORMA

## PAINTING

- Supply and paint high quality Emulsion PVA-Based Paint, for all internal walls, and gypsum ceilings, on ground and first level, including one priming coat and three finishing coats, Color off white. Painting to other works shall be included in the related itemized bills.

## PLUMBING & SANITARY

- Supply and install White “LECICO” model type wall mounted toilet with P trap complete with concealed flush tank fittings, chrome plated stop valve and side tap, including flush tank, water tap, seat with cover, stainless steel hinges, stainless steel toilet paper holder for single roll fixed to wall, hand set bidet comprising chrome plated shower type sprayer and flexible hose.

- Supply and install White “LECICO” model semi pedestal 60cm Wash Basin, complete with all fittings, valves, chrome plated siphon trap, the price also includes “Grohe” model mixer, mirror 400mm x 600mm with stainless steel frame and any other necessary needed part.

- Supply and install stainless steel single bowl kitchen sink, complete with chrome plated mixer for kitchen sinks.

- Supply, installation and testing of 2” UPVC drainage and ventilation pipes down to manholes with all requires fittings including excavation, back filling, incasing with concrete and roof vent caps and connections.

- Supply, installation and testing of HAVC drainage pipes down to manholes with all requires fittings including excavation, back filling, incasing with concrete and roof vent caps and connections.

- Supply and install precast Manholes of various diameters and to any depth, including excavation, concrete works, back filling, cement plaster, benching, rubber gaskets, iron capacity cover and all necessary works to comply with drawings, specifications and site inspection for quotation

- Heavy duty soap dispenser, stainless steel, with all needed fixing accessories.

- Heavy duty towel paper holder for single roll, stainless steel, to be fixed at wall, with all needed fixing accessories.

- Heavy duty towel holder.

- Exhaust fan, with all needed fixing accessories (800 cfm for the Kitchenette).

- Providing, fixing, jointing and testing PPR pipes, for all the water supply and drainage, make pressure pipe for cold/hot water inside building including fittings, sockets, tees, elbows, bends, crosses, reducers, adaptors, plugs and union etc… supported on walls or suspended from slab or run in chases include pipe hangers, supports, cutting and making good the chases and holes.

- Generator

- In addition to the commercial power, redundant AC power supply shall be provided automatic standby generator with the power of 100 KVA, regulated three phases and neutral 380/220VAC, 50 HZ power.

- The equipment shall be suitable for operation in the temperature, humidity, dust and other conditions expected on site, within the geographical area of Lebanon.

- The following information shall be listed on a composite data sheet for the diesel generating set manufacturers:

- Maximum ambient temperatures.

- Voltage and phases at 50 cycle’s frequency.

- Maximum continuous KVA at 0.8 power factor.

- Minimum continuous KVA at 0.8 power factor.

- Cooling system (according to country requirements).

- ENGINE AND ALTERNATOR REQUIREMENTS

- The engine and alternator unit shall be mounted on a heavy base frame by means of rubber or springs anti-vibration mountings.

- The engine shall be of a direct injection fuel diesel type.

- The engine shall be equipped with suitable capacity radiator according to the local climate conditions with engine driven fan complete with protection guards filled with necessary antifreeze and coolant liquid.

- The alternator shall be brush less self-exciting, self-regulating with topical impregnation with a three phase voltage output of 380/220VAC of 50HZ frequency, insulation class (H), protection IP23 and a response to load transient changes such that for a sudden variation of the load at constant speed, the voltage is reestablished to 3% less than 500 milliseconds. This response shall be stated the manufacturer’s data sheets provided by contractor.

- Warranty period for a minimum of one year.

- CONTROL EQUIPMENT

- An alternator circuit breaker shall be provided by means of switching the generator output and automatically disconnecting the load in the event overload and short circuit.

- A control panel that shall provide all operating, monitoring, and control functions for the generator set.

The following functionality shall be integral to the control panel:

-  Remote start/stop control

-  Local run/off/auto control

-  Emergency stop push button

-  Cool down timer

The control panel shall provide the following digital readouts for the engine and generator.

-  Generator AC volts (Line to Line, Line to Neutral)

-  Generator AC current (Per Phase)

-  Generator AC Frequency

-  Engine oil pressure

-  Engine coolant temperature

-  Engine RPM

-  Battery volts

-  DC alternator volts

-  Engine hours

The control panel shall monitor and provide alarm indication and Genset shutdown for the following:

-  Low oil pressure

-  High coolant temperature

-  Low coolant level

-  Generator over voltage

-  Generator under voltage

-  Generator over frequency

-  Generator under frequency

-  Generator over current

-  DC alternator failure

-  Low battery voltage

-  High battery voltage

## ELECTRICITY & LIGHTING

- PANELBOARD: Supply, install and connect where indicated on the drawings a complete Panel board, including Schneider circuit breakers, switches, relays, contactors, surge arresters, auxiliary equipment and all other incidentals required to provide a complete installation.

- AUTOMATIC TRANSFER SWITCH

- Introduction

ATS shall provide a continuous electrical power from the three power sources (main EDL power, standby generator and subscription) to Service Center, and shall be designed for the same size of generator. (100KVA)

The ATS panel shall be an air and water proofed sheet steel cabinet. Mains and generator contactors shall be four poles type, electrically and mechanically interlocked in such a manner as to prevent a parallel connection of the mains and alternator supplies.

- Control Functions

- The priority for Main Electricity.

- Generator starts upon failure of main electricity.

- Sequencing between two generators upon EDL failure.

- Switching between generators upon failure.

- ATS Elements- Control Panel

- A controller that shall provide all operating, power monitoring, and control functions for the ATS including the following:

- Controlling of the three power sources (Mains and two generators) as mentioned above in (Control functions)

- Four operating modes: Auto, Mains, G1, G2, OFF

- Measurement and display of the voltage and frequency of three power sources

- Measurement and display of the current on the load side

- Measurement and display of the power on the load side

- All three power inputs shall be monitored and protected for over/under voltage, phase sequence, and phase presence

- All three power inputs shall be monitored and protected for over/under frequency

- Contactors shall be UL 508 compliant and CE certified/RoHS compliant

- Rated Operational Voltage, Ue 690V

- Rated Insulation Voltage, Ui 1000V

- Rated Frequency 50Hz

- Rated Impulse Withstand Voltage, Uimp 8kV

- Battery 50A

- Two battery chargers 12v/15A

- Signals and indication alarms

- The following indication signals shall be provided on the front cover of the ATS panel:

- EDL Alive.

- EDL on load.

- Gen. Alive.

- Gen. on load.

- Three phase indication.

•	The following alarms with their related signal lamps shall be provided:

- EDL failure.

- Generator failure

- Fuel low alarm.

- MDB

- Supply and installation of two MDBs, one for normal power (EDL/GEN), and the other for UPS power.

- Supplier shall design and provide an SLD for each MDB, taking into consideration additional 20% of spare circuit breakers for future expansion.

- The main distribution boards shall be suitable for operation on 3 phase, 4wire, 50Hz, 415 volts A.C. supply, and shall be of the type suitable for accepting single, double and triple pole M.C.Bs in any combination. The neutral block shall have the same number of ways as the maximum number of single pole breakers that can be fitted.

- M.C.Bs as fitted in distribution boards shall be of the thermal magnetic type. They shall comply with BSEN 60898 or IEC 898 having M10 short circuit rating with Type C, single or triple pole types.

- Each distribution board shall have an earth connection bar mounted within the board and shall have a minimum number of cable terminations equal to the number of circuits that the distribution board had been designed to take.

- All circuit breakers should be labeled, also all sockets and switches should be labeled accordingly.

- Cables and Cable trays

- Cables

- Cabling system is divided into power, control and grounding cables

- Cables shall be suitable for installations in dry, damp or wet locations, indoors or outdoors

- The ambiance temperature as well as the load for cable accumulation shall be taken in account as per the country requirements.

- Power cables sizes shall be calculated according to the load requirement and shall be approved by MIC2...

- Power cables shall be used for EDL, ATS, MDB, generators, A/C…etc.

- Power cables from main power sources (EDL&GEN) to ATS and from ATS to MDB should be 3x35mm2+N

- Main power sources cables till MDBs shall be Armored PVC and XLPE insulated, and shall be 600/1000 Volt grade to BS 6346 or 5467

- The control cables between ATS and alarm box for external alarms (fuel low, mains fault, gen. Fault,..) shall be of 8*0.75MT mm2 (4 pairs) NYMHY

- The control cable between the ATS and the generator shall be NYMHY type (4*2.5mm2)

- The battery chargers cable (between charger and battery) shall be NYMHY type (2*4mm2)

- Grounding cables shall be yellow/green colors with different sizes according to the site requirements (NYA 1*2.5, 1*4, 1*6, 1*35, 1* 50mm2)

- All power cables shall be CE/UL/BS approved

- All cables in the ATS and MDBs should be labeled.

- Cable Trays

- Cable trays shall be hot dip galvanized, installed to carry and protect the power, control and grounding cables with the following dimensions: Height 60mm, Width 200-300mm, Length 3000mm and Thickness 0.75mm.

- The cover of the cable trays shall be hot dip galvanized, thickness 0.8-1.5 mm.

- No sharp edges in the cable trays and covers are permitted.

- All cable tray accessories (elbows, connectors, supports…) shall be of the same material of the cable trays.

- Cable tray support shall be 70cm apart for horizontal installation and 100cm apart for vertical. Supports shall be above 5cm height and protected from the water areas.

- All cables trays shall be CE/UL/BS approved

- Supply, install and connect multicolor wiring unshielded PVC and XLPE insulated cable including glands, cable termination, grounding wires, fixing materials, support boxes, accessories and all other incidentals required to provide a complete installation as specified. (Length may vary according to site requirements).

- Furnish, install and connect a complete lighting installation, including wires, accessories, conduits, boxes and all other incidentals required to provide a complete installation as shown on drawings plus Selected points as Emergency lighting.

- Furnish, install and connect the following wiring devices LeGrand, including cover plates, supports, boxes, conduits, wires, fixing accessories and all other incidentals required to provide a complete installation as per site inspection: Lighting single button keys, Lighting double direction button keys, Wall Sockets, (1 EDL - 2 Data - 2 UPS), Floor sockets, (1 EDL - 2 Data - 2 UPS), CCTV connection, QMS Data points, WIFI points, TV+ VGA, Access reader points, Fire Alarm System detections, Fire Alarm System Points, detectors, ( keys & horns) to be determined by supplier.

- Electrical cables (to be determined after site inspection), Main cable 3*35 + N + Ground, Ac 3ph Cable to roof 4 * 4 mm + Ground, Ac 3ph 4*4mm + Ground, Cable Ac 4*4mm + Ground, Cable ATS + MTS from Generator location to ATS + ground (to check on site), IT Cables, Cabling patch cords 1meter, Cabling patch cords 3 meters WM Syslink Data, Cabinet 60x60 9U with Fan, Provide data cable between Ogero box and technical room, dedicated to the PSTN line.

- Outlets Ac Mono 2* 2.5mm based on site inspection.

- Supply and install cables and sockets for LCD screens, video walls and interactive touch screens “Kiosk model”

- Supply and install cables for Smart QMS

- Supply and install cables for Microsoft surface interactive Multi-touch table located on the 1st floor

- Supply and install cables for WIFI network

- Provide a reservation for empty tubes, from server room to Cabinets, Manager Office and to Screen Room.

- Supply and install Data Patch Panel 24 Ports Termination of all ports.

- Recessed track mounting to support directional led 18w spots, color white or black.

- Semi-recessed profile track, LED 12w Color white, Dim : 1200mm.

- Recessed Fluorescent tubes stripping, same as design and drawing, with double sided light covered by sand blasted glass & Cost of cut to shape sand blasted glass to be supported by gypsum tranches sides.

- 2x60watt tube light box type Philipp’s hanging with cables, completed set.

- Recessed square spots

- Mirror light, decorative set, all included

- Indirect lighting by led strips, including all accessories, transformers, starters…

- Motorized system for main facade sunscreen with somfy motorized roller shutters

- Supply and install top and bottom wooden kitchen cabinets. Cabinet’s top shall be with granite 30mm thick with seen edges. Cabinet sides, elevations, partitions, shelves and drawers shall be of water resistant mdf 18mm thick wood, laminate with 0.8mm thick Formica sheet externally and internally, including ironmongery, handles and locks. Price to include: Compact midsize refrigerator, to be built in the kitchen cabinets Provide and installation of 25liters Microwave to fit in the upper part of the cabinet kitchen.

- Workstation desks:

Supply and fixing of the workstation desks on metal legs (L145cmx W80cmxH80cm) with all fixing accessories, set of 3 drawers unit with central lock on wheels, electrical hardware and ironmongery, made of 1.8cm water resistant High Pressure Laminate sheets, With semi partition wall for electrical wiring - in addition to a side wooden partition (70x70x3.6cm)- Color of desks off-white, please include samples of wood and models. (Desk front panel size should be extended to floor) as per approved design.

- Managerial "L" shape desk on metal legs with all fixing accessories (160 x 80 x 75 cm + extension 80 x 80 x 75 cm) +set of 3 drawers unit with central Lock-Including coffee table as per approved design.

- Supply and filling synthetic resin into a designed pylon mold, vacuumed to extract air bubbles. Cast to be sanded, shaped, machined, drilled, taped and painted glossy white finish As per drawings/site visit and 3d rendering look h x 750mm diameter.

- Supply and fixing of the semicircular counter, with all fixing accessories, drawers, shelves electrical hardware and ironmongery.  Made from 18mm water resistant mdf wood painted white polyurethane spray paint semi glossy finish Round shape to be cut on router.

- Cabinets: Supply and fixing of the workstation back cabinets dim: L120cmxW50cmxH80cm with all fixing accessories, 3.6cm shelves thickness and ironmongery, made of 1.8cm water resistant High Pressure Laminate sheets as per approved design. Color off-white, please include samples of wood and models.

- Waiting Sofa: Manufacturing of custom size Sofa, double side seat from wood chassis and steel legs with super high density foam in good quality of imitation leather, all complete as per drawings/site visit.

- Waiting area: 2 x 2 seater benches + 2 x 3 seater benches (Color gray or silver) sample/models needed

- Could be operated by remote control.

## NETWORK CABLING:

For the cabling, bidders should ensure the below:

Cabling termination:

  - All cabling should be terminated on patch panels in the cabinet

  - For the end user side the termination should be done using network outlets.

- Cable organizer should be provide for each patch panel. (with a cover on the front end)

- 4 additional cables organizers should be provided for the current installed switches. (with a cover on the front end)

- All cabling should be labeled.

- All cabling should be tested,

- Detailed test report should be provided prior to any acceptance.

- All cabling should be at least UTP Cat 6. (3M brand is a plus, or equivalent quality)

- Bidder to provide also all needed factory terminated patch cords (3M brand)

- Supplying and installing cables for LCD screens and video walls

- Supplying and installing network cables for Smart QMS

- Supplying and installing network cables for WIFI connection

- Supplying and installing network cables for interactive touch screens “Kiosk model”

- Supplying and installing network cables for Mutli-touch table

## HVAC

- DX A/C UNITS Carrier, Lenox, Gree or equivalent split, cassette, vertical, horizontal ceiling and/or floor type system Heat pump, Ducted Type Supply, install and test the following split units including evaporator blower unit and condensing unit with all steel support, vibration isolators, wiring, fittings, thermostats, controls, drainage(not less than 1” thickness)/coring for each unit and all accessories as specified as shown on drawings 60000 BTU/hr R 410 or R32, 48000 BTU/hr R 410 or R32, 36000 BTU/hr R 410 or R32, 18000 BTU/hr R 410 or R32, 12000 BTU/hr R 410 or R32.

- COPPER PIPES Refrigerant pipe works including all fittings, additional refrigerant and insulation (size to be as recommended by A/C manufacturer) complete RL/RS refrigerant pipe. Cable trays should be installed when needed. Please refer to drawings and site inspection for quotation.

- DUCT WORK Supply and installation of duct for the air conditioning made of galvanized steel sheets G90 conforming to the ASHRAE norms, and SMACNA regulation, including connections to fans, to flexible ducts, and grilles, hangers, canvas, seams, dumper, 25mm thickness of fiber glass insulation, internal duct clean liner for sound attenuation in concealed gype, silencers for sound absorption, Plenum box with internal acoustic lining as per final approved drawings & design.

- Supply & installation of 1 inch PVC pipes for each of the units & include all related accessories (Elbow, coupling, galvanized metal clamps with rubber…etc.).

- Supply & installation of Disconnect Switch and power cables to each of the above HVAC units.

- Supply & Installation Kitchen and washrooms Ventilations according to size.

- Supply and install fiber glass insulation 25mm thick.

- Supply and install of silencers for sound absorption.

- Plenum box with internal acoustic lining Size 250mm x 250mm.

- Linear Bar Grilles (LBG) / double deflection.

- Supplier to verify and confirm AC units dimensions prior to installation.

Appendices

## Annex (1)

- Habboush RSC Preliminarily Layouts (3 floors)-enclosed

## Annex (2)

BOQ and Technical specifications (to be finalized and approved following the site visits and the design submission)

### PREAMBLE

- These Bills of Quantities contain pages numbered consecutively as indicated in the index. Before the contractor submits his tender he should check the number of pages, and if any are found to be missing or duplicated, or the figures or writing indistinct, he should apply to the quantity surveyors in respect of errors in a tender due to the foregoing.

- On no account should these documents be used for placing orders for materials.

The contractor may do so at his own risk.

- The Bill of Quantities shall be read in conjunction with the instructions to bidders, General and special conditions of Contract, Technical Specifications and Drawings.

- The quantities given in the Bill of Quantities are estimated and provisional, and are given to provide a common basis for bidding. The basis of payment will be the actual quantities of work ordered and carried out, as measured by the Contractor and verified by the Engineer and valued at the rates and prices bid in the priced Bill of Quantities, where applicable, and otherwise at such rates and prices as the engineer may fix within the terms of the Contract.

- The rates and prices bid in the priced Bill of Quantities shall include all construction Plant, Labor, supervision, materials, erection, maintenance, insurance, profit, taxes and duties, together with all general risks, liabilities, and obligations set out or implied in the Contract.

- General directions and description of work and material given in the Technical drawings and specifications are not necessarily repeated in the Bill of Quantity. The BOQ forms stay the integral parts of the bid and contract.

- The tenderer is deemed to have visited the site and fully acquainted himself as to the location of each of the items and works to be carried out and he also deemed to have surveyed the actual condition of the site and building and made his own assessment of the type of works prior to submitting his offer.

- Surveying new/existing locations as well as providing the related designs are considered as killing factors in addition to other items listed in the SOC.

#### GENERAL ITEMS