1.	Concrete Works

### 1.1	Reinforced concrete

Reinforced concrete shall be used for beams, slabs,..

The quantity of cement shall be 350kg/M3

Allowable strength of concrete shall not be less than 25N/mm2.

Allowable tensile strength of reinforcement steel shall not be less than 400 N/mm2.

ACI code is the reference of the concrete works.

#### 1.2	Plain concrete

A plain concrete with nominal reinforcement (6Ø6mm/m both directions, or 6Ø8mm/m in both directions as advised), average thickness 6cm,shall be used for paving yards, screeding and other purposes that may be assigned.

1.3	Concrete slab on grade

##### Concrete slab on grade shall be used for the installation of generators on ground according to the following:

Removal of the existing soil.

A ground beam around the perimeter of the slab for protection & leveling.

A layer of compacted soil shall be provided (average thickness 35cm)

A blinding concrete layer for ground leveling (average thickness 10cm) 200kg/M3

A main concrete slab of thickness 20cm with 350kg/M3.

Reinforcement: lower & upper layer 6Ø14/m in both directions.

1.4	Block Work

Blocks shall be carefully cut to size.

Walls shall be bonded according to the best constructional practice.

Courses shall be properly leveled.

1.5     WATERPROOFING

Preparation

Surface preparation: Surfaces to receive waterproofing shall be dry, clean, and free of dust, dirt, oil, harmful curing compounds, or other foreign matter which may impair the bond or performance of the waterproofing and drainage system.

Concrete surface preparation: Surfaces shall be smooth, free of depressions, voids clean and free of harmful curing compounds and other surface contaminants which may impair the bond or performance of waterproofing and drainage system.

Membrane installation:

Primer: Apply primer to concrete substrate. Let primer dry for approximately 30 minutes or when dry to the touch. Re-prime surface if primed area has been left exposed for 24 hours.

Substrate preparation:

Seal cracks (3.2mm wide or less) in concrete with minimum thick coat of liquid membrane.

Horizontal to vertical transmissions and footings: Apply a minimum 19mm

fillet of liquid membrane at all inside horizontal corners & vertical to horizontal

transition. Side laps minimum 10cm, end laps minimum 15cm.

1.6	Walls

Walls shall be constructed of 20cm hollow block, smoothly plastered & painted.

1.7	Paint

- A sealer layer shall be applied first then smoothed.

- Primer coat shall be applied.

- Two layers of white emulsion paint shall be applied.

- Material shall be of approved quality (TINOL.SIPES, DUTCH BOY, or Equivalent.)

1.8	Plastering

  - All plastering works shall be even & true, and shall provide a smooth, hygienic

  - Crack-free surface suited to the application of the specified decoration finish.

  - Surfaces to be plastered shall be clean of dust. They shall be dashed with a wet cement & sand mix (1:2).Plastering thickness shall be 13mm.

2. Fence & Gate

- Steel fence shall be made of main steel columns 80x80mm with 8mm plate (20x20) cm with 125cm spacing.

- Fence height 2m

- Main fence steel shall be made of steel bars/angles (40x40)mm with 10cm spacing

- Painting shall be applied according to standards & using approved material. (2 primer coats of zinc rich primer & 2 final coats of  epoxy paint)

3. Steel Tent

- Steel tent shall be made of main steel columns 80x80mm with 8mm plate (20x20)cm

- Main beams 80x40mm

- Secondary beams 60x30mm

- Roofing made up of pre-painted galvanized sheets 8/10mm

- Painting shall be applied according to standards & using approved material. (2 primer coats of zinc rich primer & 2 final coats of  epoxy paint)

4.  Fuel Tank

- Bulk storage tank shall be made of black steel and fitted with filling line or opening on top (50 x 50cm), vent to atmosphere, earth connection and fuel level tube, drain valves, delivery lines and an alarm system. Top opening shall be enforced enough to prevent easy break.

- Tank shall have a thickness of 3mm and cross-supported internally at 3 levels horizontally and one vertically.

- Fuel tank electrical level meter shall be installed at 65cm height from the bottom of the tank, and shall transmit an NC alarm to the ATS panel.

- All interconnections between engine and fuel tank shall be made of black carbon steel. Painted twice with zinc phosphate primer and acrylic paint.

- Water separator connected between engine and fuel delivery line.

5. Generator

In addition to the commercial power, redundant AC power supply shall be provided from two automatic standby generators: one with the power of 135KVA and the other with the power of 80KVA regulated three phases and neutral 380/220VAC, 50 HZ power.

The equipment shall be suitable for operation in the temperature, humidity, dust and other conditions expected on site, within the geographical area of Lebanon.

The following information shall be listed on a composite data sheet for the diesel generating set manufacturers:

- Maximum ambient temperatures.

- Voltage and phases at 50 cycle’s frequency.

- Maximum continuous KVA at 0.8 power factor.

- Minimum continuous KVA at 0.8 power factor.

- Cooling system (according to country requirements).

5.1 ENGINE AND ALTERNATOR REQUIREMENTS

- The engine and alternator unit shall be mounted on a heavy base frame by means of rubber or springs anti-vibration mountings.

- The engine shall be of a direct injection fuel diesel type.

- The engine shall be equipped with suitable capacity radiator according to the local climate conditions with engine driven fan complete with protection guards filled with necessary antifreeze and coolant liquid.

- The alternator shall be brush less self-exciting, self-regulating with topical impregnation with a three phase voltage output of 380/220VAC of 50HZ frequency, insulation class (H), protection IP23 and a response to load transient changes such that for a sudden variation of the load at constant speed, the voltage is reestablished to 3% less than 500 milliseconds. This response shall be stated the manufacturer’s data sheets provided by contractor.

- Warranty period for a minimum of one year.

5.2 CONTROL EQUIPMENT

An alternator circuit breaker shall be provided by means of switching the generator output and automatically disconnecting the load in the event overload and short circuit.

A control panel that shall provide all operating, monitoring, and control functions for the generator set.

The following functionality shall be integral to the control panel:

-  Remote start/stop control

-  Local run/off/auto control

-  Emergency stop push button

-  Cool down timer

The control panel shall provide the following digital readouts for the engine and generator.

-  Generator AC volts (Line to Line, Line to Neutral)

-  Generator AC current (Per Phase)

-  Generator AC Frequency

-  Engine oil pressure

-  Engine coolant temperature

-  Engine RPM

-  Battery volts

-  DC alternator volts

-  Engine hours

The control panel shall monitor and provide alarm indication and Genset shutdown for the following:

-  Low oil pressure

-  High coolant temperature

-  Low coolant level

-  Generator over voltage

-  Generator under voltage

-  Generator over frequency

-  Generator under frequency

-  Generator over current

-  DC alternator failure

-  Low battery voltage

-  High battery voltage

5.4 SOUNDPROOF ENCLOSURE

- The sound pressure level attenuation shall be obtained by the combination of the noise reduction devices fitted on the air inlet/ outlet and of acoustic noise absorption panels fitted on the wall of the generator set cabinet.

- The sound pressure attenuation shall not exceed 65 dB when measured at a distance of one meter from the generator set cabinet.

- Insulation with fiberglass density 49 kg/m3, thickness 8cm.

- Critical muffler shall be connected by stainless steel flexible with generator.

- Paint: primer antirust finishing synthetic.

- The cabinet shall have one door from each side enough for the easy maintenance.

- Thickness of the cabinet shall be made of 2mm steel sheet.

- Suitable anti-vibration pads shall be installed under the sound proof cabinets.

5.5 Generator Area Preparation

| Generator area | Unit | Qty |
| --- | --- | --- |
| Concrete slab 20cm (MIC2 specs) | M2 | 20 |
| Steel fence/gate (MIC2 specs) | M2 | 50 |
| Steel tent made up of resin sheets 3mm,including 3 LED lighting (2x120)cm | M2 | 20 |
| Supply & installation of generator135 KVA including Control Panel with silencer - MIC2 specs | each | 1 |
| Supply & installation of generator 80 KVA including Control Panel with silencer - MIC2 specs | each | 1 |
| Supply & installation of Fuel Tank (2000) | each | 2 |
| Supply & installation of ATS (as per MIC2 Specs) | each | 1 |
| Supply & installation of power cables including support masts; Galvanized tray, (Based on Survey) - cables minimum cross section should be in line with the cable length and expected load. | L.S | 1 |
| Supply & installation of grounding system including surge arrestors, bars & cabling and all accessories needed (with ground resistance 5ohms) (according to NF C 17-100 & NF C 17-102) | each | 2 |

6. AUTOMATIC TRANSFER SWITCH

6.1. Introduction

ATS shall provide a continuous electrical power from main power (EDL) and standby generators to Warehouse, and shall be designed for the same size of generators.

The ATS panel shall be an air and water proofed sheet steel cabinet. Mains and generator contactors shall be 4 poles type, electrically and mechanically interlocked in such a manner as to prevent a parallel connection of the mains and alternator supplies.

6.2. Control Functions

- The priority for Main Electricity.

- Generator starts upon failure of main electricity.

- Sequencing between two generators upon EDL failure.

- Switching between generators upon failure.

- Switching between generators depending on load.

6.3. ATS Elements- Control Panel

- A controller that shall provide all operating, power monitoring, and control functions for the ATS including the following:

-Controlling of the three power sources (Mains and two generators) as mentioned in     Control functions (6.2)

-Four operating modes: Auto, Mains, G1, G2, OFF

-Measurement and display of the voltage and frequency of three power sources

-Measurement and display of the current on the load side

-Measurement and display of the power on the load side

-All three power inputs shall be monitored and protected for over/under voltage, phase sequence, and phase presence

-All three power inputs shall be monitored and protected for over/under frequency

- Contactors shall be UL 508 compliant and CE certified/RoHS compliant

- Rated Operational Voltage, Ue 690V

- Rated Insulation Voltage, Ui 1000V

- Rated Frequency 50Hz

- Rated Impulse Withstand Voltage, Uimp 8kV

- Battery 50A

- Three battery chargers 12v/15A

6.4. Signals and indication alarms

•	The following indication signals shall be provided on the front cover of the ATS panel:

- EDL Alive.

- EDL on load.

- Gen. Alive.

- Gen. on load.

- Three phase indication.

•	The following alarms with their related signal lamps shall be provided:

- EDL failure.

- Generator failure

- Fuel low alarm.

MDB

- Supply and installation of two MDBs, one in the Warehouse area, and the other in the Archive area.

- Supplier shall design and provide an SLD for each MDB, taking into consideration additional 20% of spare circuit breakers for future expansion. In addition, to consider that in each area will be installed a 15KVA UPS (three-phase input, single-phase output).

- The main distribution boards shall be suitable for operation on 3 phase, 4wire, 50Hz, 415 volts A.C. supply, and shall be of the type suitable for accepting single, double and triple pole M.C.Bs in any combination. The neutral block shall have the same number of ways as the maximum number of single pole breakers that can be fitted.

- M.C.Bs as fitted in distribution boards shall be of the thermal magnetic type. They shall comply with BSEN 60898 or IEC 898 having M10 short circuit rating with Type C, single or triple pole types.

- Each distribution board shall have an earth connection bar mounted within the board and shall have a minimum number of cable terminations equal to the number of circuits that the distribution board had been designed to take.

7. Cables and Cable trays

7.1. Cables

- Cabling system is divided into power, control and grounding cables

- Cables shall be suitable for installations in dry, damp or wet locations, indoors or outdoors

- The ambiance temperature as well as the load for cable accumulation shall be taken in account as per the country requirements.

- Power cables sizes shall be calculated according to the load requirement and shall be approved by MIC2..

- Power cables shall be used for EDL, ATS, MDB, generators, A/C…etc.

- Main power sources cables till MDBs shall be Armored PVC and XLPE insulated, and shall be 600/1000 Volt grade to BS 6346 or 5467

- The control cables between ATS and alarm box for external alarms (fuel low, mains fault, gen. Fault,..) shall be of 16*0.75MT mm2 (8 pairs) NYMHY

- The control cable between the ATS and each generator shall be NYMHY type (4*2.5mm2)

- The battery chargers cable (between charger and battery) shall be NYMHY type (2*4mm2)

- Grounding cables shall be yellow/green colors with different sizes according to the site requirements (NYA 1*4, 1*6, 1*35, 1* 50mm2, 1* 90mm2)

- All power cables shall be CE/UL/BS approved

7.2. Cable Trays

- Cable trays shall be hot dip galvanized, installed to carry and protect the power, control and grounding cables with the following dimensions: Height 60mm, Width 200-300mm, Length 3000mm and Thickness 0.75mm.

- The cover of the cable trays shall be hot dip galvanized, thickness 0.8-1.5 mm.

- No sharp edges in the cable trays and covers are permitted.

- All cable tray accessories (elbows, connectors, supports…) shall be of the same material of the cable trays.

- Cable trays are installed between gensets, ATS, A/C and MDB.

- Cable tray support shall be 70cm apart for horizontal installation and 100cm apart for vertical. Supports shall be above 5cm height and protected from the water areas.

- All cables trays shall be CE/UL/BS approved

8. Warehouse

The entrance of the Dekweneh warehouse must be cleared from cars and cable reels to facilitate the in and out, as well as the area behind the entrance should be cleaned from the scrap cables.

  - Warehouse General Requirements

- The warehouse (walls, ceiling, ground, doors, and windows) should be completely sealed to prevent dust, rain and animals from entering the premise.

- The surrounding of the Ericsson warehouses should be clear and safe in order to avoid any kind of incidents.

- The height is acceptable, but there is clear area all around the ceiling open and needs to be repaired to prevent equipment from rain, dust or birds, etc…

- Full electrical and lightning installation is necessary.

- Closed facility within the warehouse for the purpose of :

  - Office – Capacity at least 3 persons

  - Area around 100 m2 and a minimum of 2.3 meters height to be sealed closed, and safe for SIM Card storage purpose.

  - Toilets

| Main warehouse (29x57)m | Unit | Qty |
| --- | --- | --- |
| General clean-up including removal of all material inside the existing warehouse (1650M2) & transportation the material to another location within the compound and properly store them as per MoT request. Properly clean the surrounding areas by removing all debris and material (wheels, cars, cables...) (estimated area 900M2) | L.S | 1 |
| Floor treatment by high-speed trowel machine, concrete repair where necessary & apply 2 coats of epoxy paint for flooring. The floor treatment should be done in accordance of the expected load to be stored (refer to racking requirements) | M2 | 1600 |
| Roof repair by replacement the damaged asbestos sheets (estimated 30pcs) & ensure proper sealing of the roof elements | L.S | 1 |
| Construction of two roof ridges (for natural ventilation (300x150) cm with water leakage protection. Fitted with heavy duty mesh against birds and another animals. | each | 2 |
| Supply & installation of sky light sheets to replace the damaged ones (size 200x100)cm - matching the specifications of the currently installed ones | each | 24 |
| Supply & installation of access stairs to mezzanine area (H=320xm, W=1.20m, steps landing 25cm, platform) and handrail. Made up of main beams HEA160 and checkered plates of minimum 3 mm, and painted | each | 1 |
| Supply & installation of 60 cm access ladder (Galvanized) with Gage to roof with protection | each | 1 |
| Closing the area (wall-roof) by aluminum façade (made up of single pane glass (triplex 8mm, profile Technal GX technical specifications with Technal original accessories. Fitted with heavy duty mesh against birds and another animals. | M2 | 294 |
| Lighting the whole area including emergency light (suspended light - LED) (including layout & design) 100lumens/m2 and as per warehouse lighting standards. | L.S | 1 |
| Electrical installation (19 sockets, MDB panel IP55, skirting) for the whole area, including layout.(3 socket sets in each (2UPS,1EDL,2 Data) for offices;10 sockets (2 module) properly distributed for warehouse area. All material should be from UL, ASTM, NSE, or BS listed suppliers | L.S | 1 |
| Establish MW connectivity including (masts, antenna installation, cable tray, IF cables) | each | 1 |
| Supply & installation of conventional fire detection system for the warehouse area (UL) (no less than 100 detectors); including study & design. | L.S | 1 |
| Supply & installation of water mist fire system covering all warehouse open areas with at least 10 zones. All related tanks, pumps, accessories, needs to be provided and should be dimensioned according to the warehouse size to ensure full protection. | L.S | 1 |
| CO2 and ABC fire extinguishers to be provided as per the technical specs. - 6 ABC powder 50kg, - 30 ABC powder 20LBS, - 10 CO2 15lbs | L.S | 1 |

| SIM card & storage area |  |  |
| --- | --- | --- |
| HBW 20cm for partition for SIM cards & GS storage area | M2 | 60 |
| Roofing for the room (made up of sandwich panels 5cm) | M2 | 75 |
| Plastering (13mm thickness) | M2 | 200 |
| Painting (As per MIC2 specs) | M2 | 200 |
| Fire rated door 2hrs (200x220)cm, double leaf, with all accessories needed (Sashlock, stragal, stop,threshold,..) | each | 2 |
| Tiling (ceramic tiles 30x30cm) | M2 | 300 |
| Lighting the whole area including emergency light (15x5)m (including layout & design) 300lumens/m2 and as per storage lighting standards. | each | 2 |
| Air condition (split system, friom 410) 18000 BTU (ASTM,UL, or CE listed supplier) | each | 4 |
|  | each |  |

| Office area (Ericsson Warehouse) |  |  |
| --- | --- | --- |
| Existing Office area (470x480)cm renovation;(including false ceiling 22M2,lighting,A/C (split system, friom 410) type 12000BTU (ASTM,UL, or CE listed supplier),paint | L.S | 1 |
| Renovation for service area (sanitary & plumbing works for WC & kitchenette (including water tank, heater, water tap, mixer, wash basin, mirror, WC seat, lighting..) | L.S | 1 |
| False ceiling made up of gypsum board (fire rated, with insulation) | M2 | 45 |
| Supply for the needed furniture for 2 employees (Desk, Chair, Drawers, Cabinet) as per the Technical Specifications | each | 2 |

  - Ericsson Racking System

Approximately 1/4th of the Ericsson Warehouse should remain open space to be used for dishes, cables Rolls, and huge equipment.

Pallet Details:

Dimension: 1200x800

Weight: 1000 Kg

Height: 1000 to 1800

Heavy Duty Racking with Safety Accessories/Protections:

67 units 2700x1100x6000

- First level pallets can be placed on the floor with total 4 levels (GF, 1, 2, 3)

- 3000 KG load per level

- 12 Pallets per Unit

24 units 1850x1100x6000

- First level pallets can be placed on the floor with total 4 levels (GF, 1, 2, 3)

- 2500 KG load per level

- 8 Pallets per Unit

Total required Pallets: 996 Pallets

Warehouse Storage Long Span Shelving for small spare parts and accessories including Steal Stairs

20 units 1850x600x5000

- Total 9 levels with Steal Decking Galvanized shelves

- 500 KG load per shelf

4 units 1550x600x5000

- Total 9 levels with Steal Decking Galvanized shelves

- 500 KG load per shelves

16 units 1850x450x5000

- Total 9 levels with Steal Decking Galvanized shelves at 2500 cm and the 2500 cm open space

- 500 KG load per shelf

4 units 1550x450x5000

- Total 9 levels with Steal Decking Galvanized shelves at 2500 cm and the 2500 cm open space

- 500 KG load per shelf

4 units 1850x450x5000

- Total 4 levels Steal with Decking Galvanized shelves at 2500 cm and the 2500 cm open space

- 500 KG load per shelf

Warehouse Storage Shelving for smaller spare parts and accessories

53 units 1200x410x2500

- Total 5 levels Steal Decking Galvanized shelves

- 150 KG load per shelf

  - Forklift

- Lift Height	 		6M

- Power type	 	Electrical

- Rated capacity kg	800 KG at 6M

- Load center	          	mm	500

- Min Lifting height 	mm	5000

- Fork size	LxWxT	          	mm 1070×150×50

  - Pallets to be Purchased

- 1000 wooden Pallets 1200x800

  - Archives Warehouse

- The archive must be designed to accommodate around 250,000 box files on shelves, (150 000 existing + 75 000 in the upcoming 5 years) and must be protected from collapse, water leak, moister, dust and fire.

- Supply & installation of Pre-galvanized steel or painted steel shelving system

- Shelves must be resistance to dampness, humidity, rust, water, fire & damaging heat

- Each row should fit a box file standing upright (H32 cm x W8 cm x D29 cm)

- Each box file could weigh up to 4kg

- Shelving should have adequate load-bearing for the weight of the archive material, depending on amount of shelves in each column and amount of box files per shelve and above

| ARCHIVE | Unit | Qty |
| --- | --- | --- |
| General clean-up including removal of all material inside the existing warehouse (1000M2) & transportation the material to another location within the compound and properly store them as per MoT request. Properly clean the surrounding areas by removing all debris and material (wheels, cars, cables,.) (estimated area 200M2) | L.S | 1 |
| Electrical installation (14 sockets, MDB panel IP55, skirting,) for the whole area (20x10)mx3 and (20x20)x1,including layout.(2 socket sets: (2UPS,1EDL,2 Data) for offices;8 sockets (2 module) for warehouse area. All material should be from UL, ASTM, NSE, or BS listed suppliers | L.S | 1 |
| Lighting the whole area including emergency light (5 areas, 200M2 each) (including layout & design) 200lumens/m2 and as per archive lighting standards. | L.S | 1 |
| Relocation of the A/C installation (units, all parts.) from old warehouse & reinstallation including duct, power, ground. | L.S | 1 |
| Supply & installation of A/C units duct type (ASTM,UL, or CE listed supplier) for the remaining area (20x10)m each,(including layout & design) with heater & thermo for dehumidifier | each | 3 |
| Rehabilitation of the existing doors to make it fire-rated (2 hours) by adding sheets (including paint, locks ,handles, tent above) | M2 | 60 |
| Waterproofing membrane 4mm granule SBS | M2 | 1000 |
| Roofing for the room exposed area (made up of sandwich panels 5cm) including steel structure. | M2 | 100 |
| Relocation of Karantina shelving system (17x13)m to the new location including (design & layout) & replacement of damaged parts with same materials.(by specialized expert company) | L.S | 1 |
| Supply & installation of new shelving system for the new areas matching with the old design and Technical (Loading and Materials) Specifications. (20x10)m each.(by specialized expert company) (Shelve load capacity 60kg/shelf meter). | each | 3 |
| Closing Area to accommodate 2 permanent employees for sorting & filing, including (10M2 double gypsum wall 10cm with 5cm insulation material; one fire rated door 90x220xm 2hrs,smoke sealed dust proof; roofing 9M2 made of fire rated material; flooring cover 9M2 (tiling or antistatic carpet 2mm);A/C split system (ASTM,UL, or CE listed supplier) type 12000BTU;Sockets;lighting 2 LED fixtures; | L.S | 1 |
| Supply for the needed furniture for 2 employees (Desk, Chair, Drawers) as per the Technical Specifications | each | 2 |
| One Electric ladder lift & Two normal step ladders to reach the upper shelves level | each | 1 |
| Relocate All Stored archives at MIC2 existing warehouse to the new warehouse, while properly storing them in the new Location. The Scope includes arranging for all needed labor and machinery (forklift, etc…) | L.S | 1 |

9. Fire Protection Systems

9.1 Fire System in Main Warehouse

Supply & installation of conventional fire detection system for the warehouse area (UL) (no less than 100 detectors); Bidder to provide study & design.

Supply & installation of water mist fire system covering all warehouse open areas with at least 10 zones. All related tanks, pumps, accessories, needs to be provided and should be dimensioned according to the warehouse size to ensure full protection. Bidder to provide study & design.

CO2 and ABC fire extinguishers to be provided as per the technical specs.

•	6 ABC powder 50kg,

•	30 ABC powder 20LBS,

•	10 CO2 15lbs

ABC fire extinguishers:

ABC Powder Gas Cartridge Type extinguishers are preferred where the fire extinguishers are deployed in severe conditions - usually outdoor. They are preferred in industrial applications and enable quick and simple refilling after discharge.

ABC Powder is most versatile type of firefighting equipment, dry powder fire extinguishers are the most popular choice because of their capability for protection against light, ordinary and high Hazards. ABC dry chemical powder fire extinguishers are suitable for use on Class A (ordinary solids), Class B fires (flammable liquids) and Class C (gas and vapors) fires.

The ABC type Portable Gas Cartridge Type fire extinguishers can also be used on electrically actuated fires. Dry powder fire extinguishers carry a blue color band which is clear and easy to see in the event of any emergency.

ABC extinguishing agents shall undergo stringent quality checks ensuring the highest percentage of essential base ingredients found in the Fire Extinguisher industry.

Dry powder pressure fire extinguishers shall be filled with silicon coated mono ammonium phosphate dry chemical powder with MAP 50% or MAP 90% as per standard requirements.

ABC powder fire extinguisher, temperature range shall be from -30°C to +60°C, manufactured in accordance to EN 3-7:2008 and certified according to the directive for pressure equipment PED 2014/68/EU. It shall be suitable for use on fire involving electrical voltages up to 1000 V, at a distance of 1 meter.

Technical specifications:

- CYLINDER: Alloy steel, deep drawing, tested at 27 bar, with clip, epoxy-polyester powder painting, Red Ral 3000.

- EXTINGUISHING AGENT: ABC Powder - MAP 40 %.

- PROPELLANT: Dehumidified air or N2, 15 bar at 20℃.

- VALVE: M. 58x2, lightweight aluminum alloy AA6061 body, with external check valve, levers with red painting Ral 3000.

- USE: A B C fire rating (solid materials, flammable liquids, flammable gas).

- BRACKET: Wall-mounted bracket for fire extinguisher with clip, red painting, in standard equipment.

- DISCHARGE TIME: Less than 25s

CO2 fire extinguishers:

CO2 Fire extinguishing system is used where contamination and/or cleanup are a concern, such as data centers, labs, telecommunication rooms…

CO2 fire extinguisher, shall be able to operate in a temperature range from -30°C to +60°C, manufactured in accordance to EN  3-7, and certified according to the directive for pressure equipment PED2014/68/EU.

Technical Specifications:

- Fire Rating: 113 B

- Extinguishing Agent: Co2 99,99%

- Temperature Range: -30°C +60°C

- Discharge Time: less than 20 sec.

- Valve Tightening Torque: Minimum 95 Nm, Maximum 130 Nm

- Cylinder Pressure Test: PT 250 bar

- Cylinder Material: Alloy steel

- External/Internal Treatment: Sandblast and epoxy-polyester powder painting, Red Ral 3000

9.2 Fire System in Archives Warehouse & SIM card / Storage Room

| Relocation of the fire system including replacement of damaged parts, testing,… | L.S. | 1 |
| --- | --- | --- |
| Supply & installation of FM200 fire system for the new archive areas & SIM card/Storage Room ( UL listed/FM approved listed company) | L.S. | 1 |

    - The archive warehouse should be completely tights to support the installation of a special fire system (FM200).

    - Special fire system (FM200) for documents (must be installed prior to documents allocations).

    - FM-200 fire suppression system shall be used in equipment rooms and shall be in accordance with NFPA2001 standard for the design, installation and maintenance of clean agent fire suppression systems for telecom and battery rooms.

    - FM-200 system should serve the Archive warehouse (to identify the surface) area as shown into drawing.

    - The distributor/installer shall be trained by the manufacturer to calculate/design, install, test and maintain the FM-200 fire suppression system shall be able to produce a certificate stating such on request

    - FM-200 agent cylinders shall have a level indicator, supervisory pressure switch and pressure gauge

    - Reserve cylinder for each system Is needed

    - Engineered discharge nozzles for use with the FM-200 system shall be made of Brass and shall be located in the space per the manufacturer’s guidelines, Nozzles can have either a 180 or a 360- degree discharge pattern

    - FM 200 agent shall be confined in steel cylinders under pressure with enough concentration to suppress an occurring fire and fixed to the wall by means of cylinder bracket assembly and resting on hot dipped galvanized steel base plate

    - The cylinder shall have a removable control head, solenoid, electrical actuator

    - Actuators shall have 2 operating methods electrical and manual, to bypass any time delay

    - Supplier must provide a complete Electrical and Mechanical system with all related material and accessories that shall be UL listed/FM approved

    - All pinging and fittings shall withstand operating pressure as well as related accessories such as discharge head with set –release indication, flexible hoses, nozzles, multi-jets and valves and shall be installed in accordance with NFPA  2001, approved piping standards and FM-200 system manufacture’s requirements

    - FM-200 concentration ratio shall conform to NFPA2001 manual code and not less than 7%

    - Electronic control panel with time delay capability of 60 seconds to ensure a proper time of evacuation before the ordering of the FM 200 release, having a backup power batteries of 24 hours

    - Two auxiliary contacts shall be provided for alarm signaling and a supervised abort circuit (first alarm relay for signaling and second alarm relay to shut down the AC units 60 seconds before cylinder discharge). External Horn/siren shall sound along with the first and the second alarms

    - Fire alarm to be connected to the alarm Box

    - Cables shall be fire proof

    - System design shall be based on cross zoning release system

    - Detection zones shall cover all areas including under raised floor.

    - Strobe light shall be installed as a visual indication

    - Abort and manual stations shall be installed close to the exit door

    - Warning signs shall be posted at all areas protected by FM 200

    - The system shall be tested and commissioned by concerned representatives

    - Warranty shall be for a minimum of one year from date of acceptance.

    - Shut down control of all AC available units in the area

    - Supplier must check and confirm quality of isolation prior to the installation and acceptance of the offered FM-200 fire suppression system including walls, doors, windows, grills

    - System design and layout with all related documentation shall be provided by supplier according to site survey.

    - Supplier must provide a copy of the FM200 system Information Sheet filled up with all required data.

    - Supplier must provide a Complete documentation of the system showing both the Technical Specification and the Certification accordingly.

    - CO2 and ABC fire extinguishers to be provided.

    - 100% isolation for the Archive areas from air & water, and a successful integrity test must be accomplished by the supplier

    - Conduct a pressure and leakage test to verify closure requirements and the integrity of the design as per NFPA 2001

    - Bidder must be certified to provide the integrity test results, in addition to the below listed information once test is completed:

o   Locate potential leaks and its magnitude, if any.

o   How long the enclosure can hold the agent and Peak Pressure? If discharged.

o   If agent cannot be retained at a minimum of 10 minutes, then enclosure should be re-tested to confirm an acceptable level of Integrity has been achieved.

10. Offices Furniture:

- Desk: (160x80x73H) or (130x80x73H), 2.5cm thick melamine top in white matt and PVC edges, silver beta metal legs with beam for electrification with modesty panel extended to the floor in 1.8cm thick melamine board

- Chair: Medium back chair, tilt mechanism, with fixed arms and mesh back, black color

- Drawers: Set of 3 drawers on wheels with locks, central lock for the 3 drawers, white matt melamine board

- Cabinet: (90x42x80H) or (120x42x80) with shelves, made of white matt melamine board with locks, 5cm legs

11. Antenna Mounts

11.1 GENERAL DESCRIPTION

Antenna mounts shall be used to support the GSM and microwave antennas on roof top buildings and towers. As well, steel mounts with specified sizes shall be used to support the Micro cells and Repeaters.

11.2 GENERAL DETAILS

Antenna mounts shall have different sizes as specified on the site drawings.

Mainly the sizes are:

- Radio and MW antennas shall be installed on 4m, 6m, 8m, and 9m height masts as specified

- Mast diameters shall be 3”, 4” & 5” as specified

- Wall thickness of masts shall be 4mm

Poles and related members shall be hot dip galvanized according to BS and ASTM standards, or equivalent with a minimum coating thickness of 85-100 microns, preferably of Dalmin made or equivalent. Poles shall be supported by two arm stiffeners or as specified in the drawings .All antenna mounts shall have the required HDG access steps mounted as per the drawings. All steps shall be removable. Masts designs and drawings shall be provided by contractor for approval. Designs shall be according to ASTM, EIA/ TIA standards regarding wind speed.

11.3 WARRANTY

Warranty period must be for a minimum of 5 years.