## Sheet1
JUSTICE
SYSTEM | BRAND | DETECTORS | FM 200 AGENT | CONTROL HEAD | ABORT | NOZZLE | SOUND/STROBE | MANUAL STATION | LOCATION
FM200 + ANALAZER | SCORPIO+ FENWAL HSSD ANLAZER | 18 | 259 + 216 + 147 LB | 1 |  | 9 | 1 | 3 | MSC1
FM200 + ANALAZER | FENWAL ANALASER 50 TFP | 14 | 461 LB | 1 |  | 3 | 1 | 1 | GATEWAY
FM200 | KIDDE /AEGIS | 8 | 90 + 70 LB | 2 | 2 | 4 | 2 | 2 | IN + COORIDOR
FM200 | KIDDE /AEGIS | 2 | 68 LB | 1 | 1 | 1 | 1 | 1 | BATTERY ROOF
FM200 | KIDDE /AEGIS | 4 | 176 LB | 1 | 1 | 2 | 2 | 1 | DATA CENTER
FM200 | KIDDE /AEGIS | 4 | 49 LB | 1 | 1 | 2 | 2 | 1 | POWER ROOM
JDEIDEH
SYSTEM | BRAND | DETECTORS | FM 200 AGENT | CONTROL HEAD | ABORT | NOZZLE | SOUND/STROBE | MANUAL STATION | LOCATION
FM200 | AEGIS | 4 | 82LB | 1 | 1 | 2 | 1 | 1 | MSC2 BATTERY
FM200 + ANALAZER | FENWAL ANALASER 200TFP | 10 | 414 LB | 1 |  | 4 | 2 | 1 | MSC2
FM200 | SCORPIO | 10 | 386 LB | 1 |  | 4 | 2 | 1 | MSC3
FM200 | SCORPIO | 2 | 115 LB | 1 | 1 | 1 | 1 | 1 | MSC3 BATTERY
FM200 + ANALAZER | FENWAL ANALASER 50 TFP | 10 | 313 LB | 1 |  | 2 | 1 | 1 | GATEWAY
FM200 | AEGIS | 2 | 142 LB | 1 | 1 | 1 | 2 | 1 | POWER ROOM
FM200 | AEGIS | 8 | 358 LB | 1 | 1 | 3 | 2 | 1 | DATA ROOM
BIRHASSAN
SYSTEM | BRAND | DETECTORS | FM 200 AGENT | CONTROL HEAD | ABORT | NOZZLE | SOUND/STROBE | MANUAL STATION | LOCATION
FM200 | AEGIS | 2 | 94 LB | 1 | 1 | 1 | 1 | 1 | BATTERY ROOM
FM200 | AEGIS | 12 | 161 + 69 LB | 2 | 2 | 6 | 1 | 2 | ENTRANCE + ups
FM200 | AEGIS | 18 | 372 + 103 LB | 2 | 2 | 7 | 1 | 2 | MSC4 + EXTENSION
FM200 | KILSEN/NK 703 | 2 | 37,5KG | 1 solenoid | 1 | 1 | 2 | 1 | POWER ROOM
TRIPOLI SWITCH
SYSTEM | BRAND | DETECTORS | FM 200 AGENT | CONTROL HEAD | ABORT | NOZZLE | SOUND/STROBE | MANUAL STATION | LOCATION
FM200 | AEGIS | 16 | 398 + 280 LB | 2 | 1 | 8 | 2 | 1 | RACK ROOM
FM200 | AEGIS | 2 | 145 LB | 1 | 1 | 1 | 2 | 1 | POWER ROOM
SAIDA SWITCH
SYSTEM | BRAND | DETECTORS | FM 200 AGENT | CONTROL HEAD | ABORT | NOZZLE | SOUND/STROBE | MANUAL STATION | LOCATION
FM200 | AEGIS | 6 | 220 LB | 1 | 1 | 3 | 2 | 1 | RACK ROOM
FM200 | AEGIS | 2 | 113 LB | 1 | 1 | 1 | 2 | 1 | POWER RACK