## Grade of Compliance Range
| RFT Scoring Sheet | Reference Number | SF-CF-87
|  | Owner | PRO/PMO
|  | Revision Code | 3.0
|  | Implementation Date | 2024-05-01
Grade of Compliance range from 0 to 15 with a step of 1 unit:
15 : Compliant with additional value, not initially included in the requirements
10 : Fully compliant
4 - 5 - 6: Partially compliant
0 : Not compliant
K : Disqualification
** Project owner should describe how each grade will be selected (0/4-5-6/10/15), and if there is any formula or margins to be mentioned.

## Technical Scoring
| RFT Scoring Sheet | [11 empty] | Reference Number |  | SF-CF-87
[13 empty] | Owner |  | PRO/PMO
[13 empty] | Revision Code |  | 3.0 | 3.0
[13 empty] | Implementation Date |  | 2024-05-01 | 2024-05-01
Project Name | DEKWANEH WAREHOUSE - Air-Conditioning Precision |  | * For Requirements defined as ''Killer'', a ‘’Fully Compliant’’ score should be the sole acceptable outcome. Failing to obtain a ‘’Fully Compliant’’ score on the requirements defined as Killers, will mandate immediate disqualification for bidders.
Article | Requirements | Weight | Responsible Entity | Supplier 1 | Supplier 2 | Supplier 3 | Supplier 4 | Supplier 5 | Supplier 6 | Remarks | Supplier 1 Final | Supplier 2 Final | Supplier 3 Final | Supplier 4 Final | Supplier 5 Final | Supplier 6 Final
| 1 GENERAL | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1.1 SUMMARY | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Section includes precision air conditioning units and control panels. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1.2 REFERENCES | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Air-Conditioning, Heating, and Refrigeration | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. ASHRAE 15 – Refrigeration system safety | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. ASHRAE/IESNA 90.1-10 – Energy Standard for Buildings except Low-Rise Residential Buildings | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. ARI 210/240 - Performance Rating of Unitary Air-Conditioning & Air-Source Heat Pump Equipment. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 4. ARI 340/360 - Performance Rating of Commercial and Industrial Unitary Air Conditioning & Air-Source Heat Pump Equipment. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Electrostatics | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. DIN EN 61340-5-1 - Protection of electronic devices from electrostatic phenomena - General requirements | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1.3 SUBMITTALS | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Operation instructions manual | 1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1.4 WARRANTY | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Equipment | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. The supplied products shall be covered by full supplier warranty for a minimum period of one (1) year from delivery to site at a full repair and replacement service. | 0.2% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Warranty shall include all defected spare parts and workmanship. | 0.2% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Services | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Installation and dismantling | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| a. The supplier is responsible for the dismantling, hoisting, transportation and re-installation for parts that cannot be repaired or replaced on site | 0.2% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Part replacement/repair | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| a. For any part replacement or repair service the warranty for the repaired or new part shall be a minimum of 6 (six) months from the date of receipt of the repaired or new part. In case a part was repaired twice already under this warranty and the equipment becomes faulty again within up to six months the Operator on its discretion may request replacement of the complete equipment | 0.2% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. Major defect | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| a. In case of major defect in the supplied products, the Operator reserves the right to reject the equipment. The supplier shall replace the defected system/parts under no cost from the Operator, including dismantling, hoisting, transportation and re-installation. | 0.2% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2 PRODUCTS | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.1 MANUFACTURERS | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Manufactured in a company certified according to DIN ISO 9001/ EN 29001 | 5% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.2 COOLING CAPACITY | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. At 42°C Ambient Temperature, total cooling capacity: 7.2 KW | 25% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.3 INDOOR UNIT | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. General | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Incorporated controller for auto restart operation of the A/C unit | 1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Entire maintenance accessibility from the front | 1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Specifications | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Cold production in the unit | 2% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. One open refrigerant circuit | 0.3% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. One evaporator | 0.2% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. Condensation by external air-cooled condenser | 0.2% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 4. Dehumidification by reducing the refrigerant mass flow and the fan speed | 0.2% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5. Hot gas and liquid line end pointing downwards in the unit | 0.2% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 6. Connection to piping on site by soldered connections | 0.5% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 7. Connections can be individually shut off | 1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| C. Air Conduction: Upflow | 2% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 4. Self-supporting construction | 1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5. Frame parts are made of galvanized steel or high-quality powder coating | 0.2% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 6. Panels and doors can be removed on all sides | 0.2% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.4 T/RH Sensor | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. The temperature and relative humidity sensor shall be built in the indoor unit for room air control. | 2% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 FILTER | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Located on suction side | 0.4% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Self-extinguishing according to DIN 53438 (fire class F1) | 0.4% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| C. Filter exchange from the front | 0.4% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| D. Filter monitor installed in the unit | 0.4% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| E. Filter quality: DIN EN 779 G4 | 0.4% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.6 FAN | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Installation Type | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Inside indoor unit | 1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Features | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. High performance electronically commutated (EC) radial fan | 0.2% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Direct driven fan | 0.2% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Maintenance-free | 0.2% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. Electronically commutated (EC) motor with integrated electronic for connection to a microprocessor system | 0.2% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 4. Standard soft start | 0.2% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| C. Technical Data | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Power supply: 220V – 1p or 380V – 3ph ¦ 50-60Hz | 0.2% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Number of fans: 1 | 0.2% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| D. Speed Controller | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Adjustment of the pressure for maximum speed | 0.3% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Minimum speed: 45% (50Hz) | 0.3% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.7 EVAPORATOR COIL | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. High-capacity evaporator | 4% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Targeted draining of the condensate into the condensate pan even with high air flow velocities | 0.5% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| C. Self-supporting aluminium frame | 0.5% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.8 REFRIGERANT | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Standard: R407C or R134a or R410a | 1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.9 REFRIGERATING UNIT | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Hermetic scroll compressor, mounted in the unit with anti-vibration dampers | 0.3% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Ester oil charge | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Soldering connection | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. Sight glass for oil level | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Low pressure switch with automatic reset | 0.3% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| C. High pressure switch with manual reset | 0.3% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| D. Receiver | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Safety valve | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Shut off valve liquid line | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| E. Filter dryer | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| F. Sight glass with humidity indicator | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| G. Electronic expansion valve with pressure and temperature sensor in the suction line | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| H. Shut off valve pressure line | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| I. Shut off valve liquid line | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.10 SCROLL-COMPRESSOR | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Hermetic design | 1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Suction gas cooling | 1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| C. Internal oil management | 1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| D. Maintenance-free | 2% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.11 TUBE INSULATION | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Highly flexible until - 40°C | 0.3% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Resistance classification R 90 | 0.3% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| C. UV-proof, non-ageing and water-proof | 0.4% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.12 PRESSURE SWITCHES | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Low-pressure and high-pressure switches (preferably adjustable) | 0.5% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. High pressure switch: manual reset | 0.5% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| C. Low pressure switch: automatic reset | 0.5% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| D. Condensation temperature > 56°C | 0.5% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.13 ELECTRICAL HEATING | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Heating power: max 4 kW | 0.5% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Two stage electrical heating | 1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| C. Per stage one circuit breaker in the electric box | 0.5% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| D. Overheat protection for each stage at the frame, which interrupts the control circuit at a trigger temperature of 60°C | 1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| E. The operation of the heating is controlled by the controller | 1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.14 STEAM HUMIDIFIER - ELECTROLOSYS | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. General | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Steam humidifier, installed in the unit for the entirely automatic production and delivery of odourless, demineralized and germ-free steam consisting of: | 0.5% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| a. Steam cylinder with 3 electrodes | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| b. Steam distribution lance | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| c. Level sensor | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| d. Control board with microprocessor | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| e. Inlet and outlet solenoide valve | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| f. Including contactor and circuit breaker in the A/C unit's electrical box | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Controls | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Indication of the humidification capacity by LED flash cycles | 0.4% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Alarm display by LED flash cycles | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. Alarm forwarding and evaluation by the controller | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 4. Manual draining by press button on the control board | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| C. Technical Data | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Steam capacity: 3 kg/h | 0.5% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Pre-adjustable maximum steam capacity: 25-100 % of the nominal capacity | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.15 STEAM HUMIDIFIER – INFRA-RED | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. General | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. The infrared humidifier design consists of quartz lamps mounted above a stainless steel water reservoir. | 0.5% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. The lamps never come in contact with the water. | 1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. When humidification of room air is required, infrared rays generate water vapor—without impurities or odor, within seconds. | 1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.16 ELECTRIC CABINET | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Accessible from the front | 2% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Installed main switch operable and lockable from the outside | 1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| C. All wires are coded | 2% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.17 POWER SUPPLY | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. 380-400 Vac, 3ph, 50 Hz with N and PE protective conductor | 1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.18 CONTROLLER | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. General | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. System for control of A/C units | 1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Installed in the electrical cabinet | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. Supply voltage: 24 V (±15%) VAC | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 4. I/O-board interface: EIA485 (RS485) | 1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5. Sensor inputs: 4 | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 6. Alarm inputs: 11 – status display via LED's | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 7. Analog outputs: 4 | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 8. Digital outputs: 7 – status display via LED's | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Display | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Large backlit LCD display | 1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Graphical display of stored data | 0.5% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. Visual and acoustic signals of events | 0.5% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 4. Menu in English language | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| C. Features | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Automatic or manual start after power loss, unit start time delay also selectable for individual components. | 1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Runtime equalization and sequencing of 2 compressors in a unit with 2 refrigerant circuits | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. Recording of up to 200 alarms with time and date | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 4. Temperature and humidity recording up to 1440 data points, freely scalable within 1 to 60000 minutes | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5. One (1) common alarm | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 6. Serial RS485 interface available for connection to user interface | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 7. Sequencing of all connected Controllers | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 8. Alarm priority configuration | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| D. Interfaces | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. RS485 - for internal I/O-Bus | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| E. Control Functions | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Cooling, heating, humidification, and dehumidification | 1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Control and supervision of limit values for condensation pressure, temperature and humidity with supply air or return air limitation. Mean average value control when more than one sensor of the same type is used. | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. Supervision of following signals: airflow, compressor, heater, fan speed, condensation pressure, filter, humidifier, water detector, phase supervision, conductivity measurement, UPS, dry cooler, fire alarm, pumps, 4 auxiliary alarms, broken sensor. | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.19 DUAL MAINS SUPPLY | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| F. Two (2) main switches, one main switch per power supply | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| G. Four (4) pole version according to DIN EN 50600-2-2 | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| H. Supervision of three phases of power supply 1 and power supply 2 | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| I. Supervision of phases on under-voltage and failure | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| J. Priority of power supply 1 | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| K. In case of failure of power supply 1: Commutation to power supply 2 after a selectable time (preselected: 10 seconds). Unit starts by automatic restart. | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| L. In case of voltage return on power supply 1: Unit stop and commutation to power supply 1 after a selectable time (preselected: 10 seconds). Unit starts by automatic restart. | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| M. Installed internally in A/C cabinet | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| N. Maximum current: 63A | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.20 OUTDOOR TEMPERATURE SENSOR | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Type : PT100 sensor | 0.2% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Temperature range: -20 to +40°C | 0.2% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| C. Weather protection: IP67 | 0.2% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.21 CONDENSER | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Features | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Outside type | 1.5% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Air-cooled | 1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. Airflow: Vertical | 0.5% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 4. Main switch for connection to power supply, water jet-proof according to IP 65 | 0.2% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5. Condenser protected with 1x1cm mesh wire at the bottom to prevent nylon bags and other things from blocking the coils/fan. | 1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Condenser Fan Speed Control | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. The fan speed control is realized proportionally by a low loss phase control (TRIAC). | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. The Fan speed control can also be used as winter-kit for the ambient temperature range from -10°C up to - 20°C | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. Protection class: IP 54 | 1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.22 WATER DETECTION SYSTEM | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Water detection system consisting of: | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Water detection module (installed in the electric cabinet) | 0.3% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Sensor electrode | 0.3% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. Operating voltage 24VAC | 0.3% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. The sensor electrode must be installed on the floor near the unit. If water is detected an alarm is transmitted to the controller and the humidification are switched off. | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.23 SHUTDOWN BY EXTERNAL FIRE ALARM | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Shutdown of the A/C unit by external fire alarm | 0.3% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Alarm indication at the controller | 0.3% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| C. Input of the customer's alarm signal via voltage-free contact | 0.3% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| D. Alarm reset at the controller before restart necessary | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.24 REFRIGERANT COPPER PIPEWORK | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Hard drawn copper tubing is used for halocarbon refrigeration systems. | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Refrigerant pipes shall be of seamless copper tube type “L”, jointed by silver brazing, using 45% silver brazing alloy. | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| C. Typical sizes include 5/8 inch, 7/8 inch, 1-1/8 inch, etc. | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| D. Formed fittings, such as elbows and tees, are used with the hard drawn copper tubing. | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| E. All joints are brazed with oxy-acetylene torches by a qualified technician. | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.25 PIPEWORK THERMAL INSULATION | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Pipes shall be insulated with rubber type insulation 12 mm thick similar to Armflex. Insulation shall be closed cell tubing with finished skin, chemical and oil resistant with minimum water absorption. | 0.4% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Insulation shall stand extremes temperatures ranging from 40°C to 120°C. | 0.4% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.26 LABELS | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Each A/C UNIT shall be clearly and permanently labeled identifying Indoor unit number, Outdoor condenser number, and Supply circuit breaker. | 0.1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.27 ACCESSORIES | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. All necessary accessories required for the proper installation and operation of the system including hangers, vibration isolators, and all necessary accessories. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.28 TECHNICAL DATA OF THE UNIT | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Provide technical data as per tables below. | 2% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Unit | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Unit model: [kW] | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Cooling capacity (total): [kW] | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Cooling capacity (sensible): [kW] | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Net total cooling capacity: [kW] | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Net sensible cooling capacity: [kW] | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Condensing temperature: [°C] | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| EER: [kW/kW] | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| AER: [W/(m³/h)] | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Sound power level: [dB(A)] | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| LpA (2m free field): [dB(A)] | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Airflow: [m³/h] | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Air velocity: [m/s] | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Return air temperature: [°C] | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Return air humidity: [%] | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Supply air temperature: [°C] | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Altitude above sea level: [m] | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Height: [mm] | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Width: [mm] | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Depth: [mm] | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Weight: [kg] | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Refrigerant: [] | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Frequency: [Hz] | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| FAN (Data Per Fan) | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Fan type: | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Number: | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Max. revolutions:[U/min] | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Nominal power:[kW] | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Revolutions:[rpm] | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Power consumption:[kW] | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| ESP external static pressure:[Pa] | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Total pressure drop:[Pa] | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Control voltage:[V] | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Motor-efficiency:[%] | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Compressor (Data per compressor) | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Electrical power consumption:[kW] | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Heat rejection:[kW] | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| COP:[kW/kW] | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Number: | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Evaporating temperature:[°C] | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Condenser | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Unit type: | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Ambient temperature:[°C] | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Sound pressure group: | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Required condenser capacity:[kW] | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Available condenser capacity:[kW] | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Difference:[%] | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Weight:[kg] | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Current consumption (per fan):[A] | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Power consumption (per fan):[kW] | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Height:[mm] | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Width:[mm] | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Depth:[mm] | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Airflow:[m³/h] | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| LpA (5m freefield):[dB(A)] | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Number of fans: | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Number of condensers: | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3 END OF SECTION | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
Total |  | 100% | [7 empty] | Total | 0 | 0 | 0 | 0 | 0 | 0
[11 empty] | SUPPLIER 1 SCORE | SUPPLIER 2 SCORE | SUPPLIER 3 SCORE | SUPPLIER 4 SCORE | SUPPLIER 5 SCORE | SUPPLIER 6 SCORE
* For Requirements defined as ''Killer'', a ‘’Fully Compliant’’ score should be the sole acceptable outcome. Failing to obtain a ‘’Fully Compliant’’ score on the requirements defined as Killers, will mandate immediate disqualification for bidders.
Note on D8: Entity (Department/ Unit) that identified the requirement and that will be responsible for its evaluation.
Note on E8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on F8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on G8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on H8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on I8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on J8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements

## Combined Scoring
| RFT Scoring Sheet |  | Reference Number | SF-CF-87
|  |  | Owner | PRO/PMO
|  |  | Revision Code | 3.0 | 3.0
|  |  | Implementation Date | 2024-05-01 | 2024-05-01
Project Name | DEKWANEH WAREHOUSE - Air-Conditioning Precision
| Technical Score | 40%
| Commercial Score | 60%
| Combined Score | 100%