## Grade of Compliance Range
| RFT Scoring Sheet | Reference Number | SF-CF-87
|  | Owner | PRO/PMO
|  | Revision Code | 3.0
|  | Implementation Date | 2024-05-01
Grade of Compliance range from 0 to 15 with a step of 1 unit:
15 : Compliant with additional value, not initially included in the requirements
10 : Fully compliant
4 - 5 - 6: Partially compliant
0 : Not compliant
K : Disqualification
** Project owner should describe how each grade will be selected (0/4-5-6/10/15), and if there is any formula or margins to be mentioned.

## Technical Scoring
| RFT Scoring Sheet | [11 empty] | Reference Number |  | SF-CF-87
[13 empty] | Owner |  | PRO/PMO
[13 empty] | Revision Code |  | 3.0 | 3.0
[13 empty] | Implementation Date |  | 2024-05-01 | 2024-05-01
Project Name | DEKWANEH WAREHOUSE - Air Conditioning - Split |  | * For Requirements defined as ''Killer'', a ‘’Fully Compliant’’ score should be the sole acceptable outcome. Failing to obtain a ‘’Fully Compliant’’ score on the requirements defined as Killers, will mandate immediate disqualification for bidders.
Article | Requirements | Weight | Responsible Entity | Supplier 1 | Supplier 2 | Supplier 3 | Supplier 4 | Supplier 5 | Supplier 6 | Remarks | Supplier 1 Final | Supplier 2 Final | Supplier 3 Final | Supplier 4 Final | Supplier 5 Final | Supplier 6 Final
| 1 GENERAL | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1.1 SUMMARY | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Section includes split-system air conditioning units. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1.2 REFERENCES | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Air-Conditioning, Heating, and Refrigeration | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. ASHRAE 15 – Refrigeration system safety | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. ASHRAE/IESNA 90.1-10 – Energy Standard for Buildings except Low-Rise Residential Buildings | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. ARI 210/240 - Performance Rating of Unitary Air-Conditioning & Air-Source Heat Pump Equipment. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 4. ARI 340/360 - Performance Rating of Commercial and Industrial Unitary Air Conditioning & Air-Source Heat Pump Equipment. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5. LEED Compliance: Supply refrigeration system utilizing HCFC free refrigerants. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Electrostatics | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. DIN EN 61340-5-1 - Protection of electronic devices from electrostatic phenomena - General requirements | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1.3 SUBMITTALS | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Operation instructions manual | 2% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1.4 WARRANTY | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Equipment | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. The supplied products shall be covered by full supplier warranty for a minimum period of one (1) year from delivery to site at a full repair and replacement service. | 0.4% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Warranty shall include all defected spare parts and workmanship. | 0.4% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Services | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Installation and dismantling | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| a. The supplier is responsible for the dismantling, hoisting, transportation and re-installation for parts that cannot be repaired or replaced on site | 0.4% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Part replacement/repair | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| a. For any part replacement or repair service the warranty for the repaired or new part shall be a minimum of 6 (six) months from the date of receipt of the repaired or new part. In case a part was repaired twice already under this warranty and the equipment becomes faulty again within up to six months the Operator on its discretion may request replacement of the complete equipment | 0.4% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. Major defect | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| a. In case of major defect in the supplied products, the Operator reserves the right to reject the equipment. The supplier shall replace the defected system/parts under no cost from the Operator, including dismantling, hoisting, transportation and re-installation | 0.4% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2 PRODUCTS | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.1 MANUFACTURERS | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Manufactured in a company certified according to DIN ISO 9001/ EN 29001 | 13% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.2 COOLING CAPACITY | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Rated cooling capacity at 35°C ambient temperature: 12,000 BTU | 30% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.3 GENERAL CHARACTERISTICS | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Type: split-system | 3% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Mounting type (refer to implementation drawings): | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Wall mount | 2% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| C. Mains supply: | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. 220Vac ±10% 1ph @ 50Hz | 1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| D. Working ambient temperature: -10°C to +50°c | 3% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| E. Cooling and heat pump | 2% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| F. Energy efficiency rating (EER): > 11 Btu/h.W ¦ > 3.2 W/W | 4% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.4 INDOOR UNIT | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Direct drive motor and fan set. Operate at very low noise and are removable for easy services. Fan is of multi-blade centrifugal type. | 2.5% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Minimum of three (3) fan speeds | 2.5% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| C. Adjustable multidirectional swing louvers. | 2.5% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| D. High efficiency air-filter for dust trapping and easy in maintenance, cleanable and reusable. | 2.5% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 OUTDOOR UNIT | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Casing is made of high gauge electrolytic zinc coated sheet steel with powder paint for rust extra protection. | 3% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Compressor type: reciprocating | 3% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| C. Motor and fan with horizontal discharge designed to prevent motor burn out and easy service, operation with low RPM for super quiet operation. | 4% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.6 CONTROLS AND PROTECTION | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. On/OFF switch | 1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Fan speed control: high, medium, low | 1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| C. High-low-pressure protection | 1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| D. Compressor starts after timed setting (3min) | 1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| E. Auto-restart after mains return | 3% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| F. Auto-resume feature: during a power cutoff, all instructions are memorized and restored when power is on again. | 3% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.7 REFRIGERANT | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Standard: R410A | 2% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.8 REFRIGERANT COPPER PIPEWORK | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Annealed copper tubing is used for halocarbon refrigeration systems. | 1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Refrigerant pipes shall be of seamless copper tube type “L”, jointed by silver brazing, using 45% silver brazing alloy. | 1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.9 PIPEWORK THERMAL INSULATION | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Pipes shall be insulated with rubber type insulation 12 mm thick. Insulation shall be closed cell tubing with finished skin, chemical and oil resistant with minimum water absorption. | 1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Insulation shall stand extremes temperatures ranging from 40°C to 120°C. | 1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.10 WIRING | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Cables, power and control, should be terminated with crimp terminals and numbered. | 1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.11 LABELS | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Each A/C UNIT shall be clearly and permanently labeled identifying: | 1% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.12 ACCESSORIES | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. All necessary accessories required for the proper installation and operation of the system including hangers, vibration isolators, and all necessary accessories. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3 END OF SECTION | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
Total |  | 100% | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
[11 empty] | SUPPLIER 1 SCORE | SUPPLIER 2 SCORE | SUPPLIER 3 SCORE | SUPPLIER 4 SCORE | SUPPLIER 5 SCORE | SUPPLIER 6 SCORE
* For Requirements defined as ''Killer'', a ‘’Fully Compliant’’ score should be the sole acceptable outcome. Failing to obtain a ‘’Fully Compliant’’ score on the requirements defined as Killers, will mandate immediate disqualification for bidders.
Note on D8: Entity (Department/ Unit) that identified the requirement and that will be responsible for its evaluation.
Note on E8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on F8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on G8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on H8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on I8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on J8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements

## Combined Scoring
| RFT Scoring Sheet |  | Reference Number | SF-CF-87
|  |  | Owner | PRO/PMO
|  |  | Revision Code | 3.0 | 3.0
|  |  | Implementation Date | 2024-05-01 | 2024-05-01
Project Name | DEKWANEH WAREHOUSE - Air Conditioning - Split
| Technical Score | 40%
| Commercial Score | 60%
| Combined Score | 100%