## TOTAL
DEKWANEH WAREHOUSE Electrical Works
BILL OF QUANTITIES - GRAND TOTAL
ITEM | DESCRIPTION | TOTAL (USD)
A | Electrical | 0
B | Solar | 0
C | UPS | 0
D | Lighting | 0
| GRAND TOTAL | 0

## Electrical
BILL OF QUANTITIES - ELECTRICAL WORKS
ITEM | DESCRIPTION | UNIT | QTY | UNIT PRICE | TOTAL USD
SECTION 26 24 13 Low Voltage Switchboards - 17.12
MAIN DISTRIBUTION BOARDS
Surface mounted or free standing main distribution boards of hinged cover cabinet type complete with busbars, circuit breakers, switch disconnectors, spares, spaces, digital indicating and measuring devices, "PVC" trunking and wires, ground conductors, cable lugs and accessories. The contractor is responsible to verify the design, make the necessary calculations and shall be responsible for the performance of the system and its compliance with the specified standards. ATS & Main distribution boards shall be equipped with digital power meters Power meter similar to EasyLogic PM2230 Ref. METSEPM2230
Each main distribution panel board has to be provided with engraved metal nameplate mounted with corrosion resistant screws.
The electrical cables, inside the main distribution boards, have to be fixed on supports with metallic clamps.
All functional units have to be labeled and identified by using engraved metal nameplate mounted with corrosion resistant screws.
Cables glands shall be provided at the termination of all cables at the enclosures.
The electrical link between the functional units have to be done by rigid bus bars for 100 Amps and more.
The flexible insulated bus bars are allowed only between Main Bursars and circuit breakers where their respective frame is equal or lower than 100 Amps.
The incoming/outgoing cables are connected to functional units by insulated bus bars and suitable insulated connectors.
The direct connection between circuit breakers and outgoing cables is not allowed.
All 3-Ph circuit breakers are 4P4D; All switches are 4P; unless otherwise indicated on the drawings
Electric socket circuits shall be equipped with 30mA differential protection
All panels shall have a minimum of 20% spare space
A01 | MDB @ Electrical Room | U | 1 |  | 0
A02 | SDB OFFICES @ Offices | U | 1 |  | 0
A03 | SDB STORE ROOMS @ GF 2 story building | U | 1 |  | 0
A04 | SDB WH @ Large WH | U | 1 |  | 0
A05 | SDB UPS @ Electrical Room | U | 1 |  | 0
A06 | SDB Fire Pumps @ Fire Pumps | U | 1 |  | 0
A07 | ATS GE1-GE/PT-GE-PV Rated 150A; @ Electrical Room | U | 1 |  | 0
A08 | SURGE ARRESTOR; @ Electrical Room Shelter; 3P+N with box Complete Protection | U | 1 |  | 0
A09 | SDB UPS OFFICES @ Electrical Room | U | 1 |  | 0
SECTION 26 05 19 Low-Voltage Electrical Power Conductors and Cables - 17.12
Supply, install and connect, Alu/PVC/PVC 600/1000 volts, including pull boxes, cable fixing cable cleats, cable glands, sealing compound, cable sleeves, marking and all necessary accessories as specified and shown on drawings. Similar to Liban Cable
B01 | Cable Alu/PVC/PVC 600/1000 volts, NYY | m | 550 |  | 0
4x150 mm² (PT Bldg to ATS)
Supply, install and connect, Cu/PVC/PVC 600/1000 volts, including pull boxes, cable fixing cable cleats, cable glands, sealing compound, cable sleeves, marking and all necessary accessories as specified and shown on drawings Similar to Liban Cable
C01 | Cable Cu/PVC/PVC 600/1000 volts, NYY
C02 | 4x70 mm² (EDL to ATS) | m | 100 |  | 0
C03 | 4x70 mm² (ATS to MDB) | m | 15 |  | 0
C04 | 4x70 mm² (MDB to SDB Fire Pumps) | m | 200 |  | 0
C05 | 4x35 mm² (Gen to ATS) | m | 30 |  | 0
C06 | 4x35 mm² (Inverter to MDB) | m | 75 |  | 0
C07 | 4x25 mm² (MDB to SDB Warehouse) | m | 120 |  | 0
C08 | 4x10 mm² (MDB to SDB Store Rooms) | m | 15 |  | 0
C09 | 4x10 mm² (MDB to SDB Offices) | m | 25 |  | 0
C10 | 4x10 mm² (MDB to UPS) | m | 10 |  | 0
C11 | 4x10 mm² (SDB WAREHOUSE to Forklift Charging PAnel) | m | 30 |  | 0
C12 | 2x10 mm² (ATS to Gen) | m | 100
C13 | 2x4 mm² (ATS to Gen) | m | 100
Earth Cables
Supply, install and terminate earth cables, NYA, including accessories as specified and to the satisfaction of the Engineer. Copper conductor, Single Core, Unarmoured, PVC insulated, Non Sheathed, 450 / 750 V Isolation, with Rigid Conductors - Green/Yellow Similar to Liban Cable
D01 | 1x70 mm² - Copper conductor, Single Core, Unarmoured, PVC insulated, Non Sheathed, 450 / 750 V Isolation, with Rigid Conductors - Green/Yellow | m | 30 |  | 0
D02 | 1x35 mm² - Copper conductor, Single Core, Unarmoured, PVC insulated, Non Sheathed, 450 / 750 V Isolation, with Rigid Conductors - Green/Yellow | m | 215 |  | 0
D03 | 1x25 mm² - Copper conductor, Single Core, Unarmoured, PVC insulated, Non Sheathed, 450 / 750 V Isolation, with Rigid Conductors - Green/Yellow | m | 105 |  | 0
D04 | 1x16 mm² - Copper conductor, Single Core, Unarmoured, PVC insulated, Non Sheathed, 450 / 750 V Isolation, with Rigid Conductors - Green/Yellow | m | 120 |  | 0
D05 | 1x10 mm² - Copper conductor, Single Core, Unarmoured, PVC insulated, Non Sheathed, 450 / 750 V Isolation, with Rigid Conductors - Green/Yellow | m | 80 |  | 0
Miscellaneous Cables
E01 | 10 pair telephone cable, similar to Liban cable LibtelS, 0.5mm² | m | 150 |  | 0
E02 | Control cable 10x1.5 mm² Similar to Liban Cable | m | 150 |  | 0
Miscellaneous
F01 | Alarm distribution frame 50 pairs similar to KRONE; disconnection module to be provided without earth with punching tool | U | 2 |  | 0
EARTH/GROUND
G01 | 3 rods earth system | U | 3 |  | 0
G02 | 1 rod earth system | U | 9 |  | 0
G03 | Test clamp (disconnecting link) | U | 8 |  | 0
G04 | Lightning rod FRANKLIN type 240cm | U | 3 |  | 0
G05 | Elevation rod 2m | U | 3 |  | 0
G06 | Copper tape 30x2mm | m | 184 |  | 0
0
H01 | Surge Protection Box for Mains Feeder 380Vac | U | 1 |  | 0
Panel constructed of weather proof wall mounted metallic box, IP65, with key lockable door consisting of :
- Fuse holders, touch-safe dead front, designed to hold 500Vac 22x38mm fuses, DIN rail mountable and easily removed with no additional fuse pullers or tools according to IEC 60269, Four (4) Poles, Rated current 100A, 690V AC, 6kV Uimp Equipped with light indicator and microswitch Similar to DF, Part No. 485331
- Fuse link, Size 22×58 gPV cylindrical fuse link rated 500Vc, 100A, Interrupting Current 120KA, according to IEC 60269, equipped with striker, Similar to DF, Part No. 422200
- L-N Pluggable, coordinated and modular single-pole lightning current arrester with high follow current limitation, Type 1 SPD according to EN 61643-11, Fault indication Max. continuous operating voltage: 255 V a.c. Voltage protection level: <= 2.5 kV Lightning impulse current (10/350): 50 kA Similar to DEHN, Type: DB M 1 255, Part No.: 961120, Qty= 3
- N-PE Modular, pluggable and coordinated single-pole N-PE lightning current arrester, width: 2 modules, Type 1 SPD according to EN 61643-11 Pressurised encapsulated creepage discharge spark gap, Fault indication, Lightning impulse current (10/350): 100 kA Voltage protection level: <= 1.5 kV TOV resistance: 1200 V/200 ms Similar to DEHN, Type: DGP M 255, Part No.: 961101, Qty=1
SECTION 26 05 36 Cable Trays for Electrical Systems
Supply and install hot dip galvanized perforated steel cable trays with straight flange, complete with corners, return edge type, suspension system, fixing and all accessories including covers
I01 | Cable tray 314mm wide x 48mm high | m | 100 |  | 0
I02 | Ditto 198mm wide x 48mm high | m | 100 |  | 0
I03 | Ditto 100mm wide x 48mm high | m | 100 |  | 0
I04 | Ditto 50mm wide x 48mm high | m | 100 |  | 0
Total |  |  |  |  | 0

## Solar
BILL OF QUANTITIES - SOLAR
ITEM | DESCRIPTION | UNIT | QTY | UNIT PRICE | TOTAL USD
PV Module
Supply, install, connect, and operate with all material needed including supply, install & connect the following: cable trays, clamps, accessories, supports & labels suitable to be installed under the PV arrays.
A01 | Solar Photovolataic module, Mono-chrystalline, half-cut, mon-crystalline, 600Wp, efficiency 22.21% @ STC, power tolerance 0~+3%, 0.4% annual degredation over 30 years, anti-reflection coating, frame made of anodised aluminum alloy, IP68. similar to Jinko Tiger Neo N-Type | U | 86 |  | 0
PV Mounting Structure
Supply and install Module mounting structure from hot galvanized steel profile foundation or Aluminium profile structures suitable to the dimension of selected PV modules and PV numbers, the mounting provides a fixed inclination of the modules same as the inclined roof with vertical supports, plates, screws, the structure profile includes bracing and double hot galvanized angles for dividers.
A02 | The mounting structures and the foundations must be designed structurally to be suitable to withstand all static loads (weight of modules and working technician) and dynanic loads (wind load as per Lebanese Norm NL 137_2020 4th ed) that might occur according to site conditions. The mounting structure components are bonded together to guaranty potential equalization. | LS | 1 |  | 0
Grid-Tie Solar Inverter
Supply, install, connect, and operate DC/AC, Grid-Tie, 3-phase Solar Inverter with data communication unit with Ethernet connection. The inverter must be suited to any PV module configuration. The inverter unit shall be suitable for outdoor installations with IP66 with efficiency 98.7%, with ethernet and RS485 ports for remote monitoring, arc fault protection, DC surge protection, AC surge protection, anti-islanding protection, AC overcurrent protection, DC reverse polarity protection, PV-array string fault monitoring, residual current monitoring, and maximum total harmonic distortion <3%.
| Grid Connection Standards: IEC 61727, VDE 0126-1-1 Safety standards: IEC 62109-1/-2, IEC 62116, IEC 60068, IEC 61683 |  |  |  | 0
A03 | Solar Inverter 36KW, 3-phase, sine wave, Grid-Tie, similar to Huawei SUN2000-36KTL-M3 | U | 1 |  | 0
Fuel Save Controller
Supply, install, connect, and operate with all material needed including supply, install & connect the following: cables, three (3) current transformer, enclosure, accessories, & labels
A04 | Fuel Save Controller to handle the power production from PV and genset to give the highest PV penetration and to ensure safe power production to support the load. Similar to DEIF AGC-150 | U | 1 |  | 0
Protections
A05 | Surge Protection for PV Cables | LS | 1 |  | 0
Panel constructed of weather proof wall mounted metallic box, IP65, with key lockable door consisting of : - Fuse holders, touch-safe dead front, designed to hold 1000Vdc 10x38mm fuses, DIN rail mountable and easily removed with no additional fuse pullers or tools according to IEC 60269-2, -4, and -6. Similar to DF (485153)
| - Fuse link, rated 1000Vdc, 20A, Interrupting Current 30KA, according to UL 248-1, UL 248-19, IEC 60269-6, similar to DF (491635) |  |  |  | 0
| - Surge Protection: Modular and pluggable multipole arrester for use in photovoltaic systems up to 1000 V d.c. with three-step d.c. switching device, Fault indication with remote signalling contact, Type 2 SPD according to EN 61643-31. Total discharge current: 40 kA, Voltage protection level: <= 4 kV Similar to DEHN, Type: DG M YPV SCI 1000 FM, Part No. 952515 |  |  |  | 0
0
A06 | Cables FLEX/XLPE FLEX/XLPE FLEX 1.5/1.5 (1.8) kV DC, Cu, EN50618, IEC62930 similar to Liban Cable
| 1x6mm² (from PV panel to Inverter) | m | 672 |  | 0
Total |  |  |  |  | 0

## UPS
BILL OF QUANTITIES - UPS
ITEM | DESCRIPTION | UNIT | QTY | UNIT PRICE | TOTAL USD
UPS
A01 | 20KVA, 3ph input, 3ph output, PF =>0.9, 380V, 50hz, double line conversion, transformerless, built-in maintenance bypass, high efficiency. | U | 1 |  | 0
Batteries
A02 | Battery Bank for 20KW load consisting of 12Vdc, 170AH C10 to 1.80Vdc @ 20°C VRLA batteries, Absorbed Glass Mat (AGM), front terminal, 10 year float life at 25°C, container and cover in flame retardant UL94-V0 ABS material. | U | 1 |  | 0
A03 | WEB Ethernet SNMP card for remote supervision of UPS | U | 1 |  | 0
A04 | Battery fuse box, 100A, for each string (at the batteries side) | U | 1 |  | 0
A05 | Set of steel racks (Chassis) for batteries | U | 1 |  | 0
A06 | Battery disconnect panels | U | 1 |  | 0
0
A07 | Delivery, transportation, installation, & commissioning | U | 1 |  | 0
Total |  |  |  |  | 0

## Lighting
BILL OF QUANTITIES - LIGHTING
ITEM | DESCRIPTION | UNIT | QTY | UNIT PRICE | TOTAL USD
LIGHTING POINTS AND ELECTRIC OUTLETS
Including concealed and exposed conduits, wiring up to corresponding panelboard, cable outlet, fixing support, and necessary accessories and connections as specified and shown on drawings.
A01 | Lighting point, ceiling mounted | U | 69 |  | 0
A02 | Lighting point, wall mounted | U | 43 |  | 0
A03 | Lighting point, high bay | U | 66 |  | 0
A04 | Lighting point for outdoor flood lights | U | 18 |  | 0
A05 | Outlet for motorized gate, 3x2.5mm2 | U | 3 |  | 0
A06 | Outlet for water heater | U | 1 |  | 0
A07 | Outlet for Air conditioning units 12000 BTU/Hr | U | 9 |  | 0
A08 | Outlet for Air conditioning units 7.5KW precision type | U | 3 |  | 0
A09 | Outlet for FACP | U | 5 |  | 0
A10 | Outlet for CCTV | U | 1 |  | 0
A11 | Outlet for access control system | U | 1 |  | 0
LIGHTING FIXTURES
Including necessary accessories for installation and connection, as specified and shown on drawings.
B01 | LED surface mounted fixture, 4100 lumens, color temperature 4000 K, beam angle of light source 90deg, 34W, white housing, similar to Philips | U | 35 |  | 0
B02 | LED surface mounted fixture, 1800 lumens, color temperature 4000 K, 15W, white housing, similar to Philips | U | 34 |  | 0
B03 | 8W Wall mounted Emergency Light with battery kit, similar to Legrand | U | 24 |  | 0
B04 | 8W Wall mounted Exit Sign with battery kit, similar to Legrand | U | 19 |  | 0
B05 | High Bay, suspended luminaires, LED, 240W, 27000 lumens, White 4000K, Clear Glass, IP66, | U | 66 |  | 0
B06 | Outdoor luminaires, LED, 240W, 27000 lumens, White 4000K, IP66. | U | 18 |  | 0
WIRING DEVICES, DISCONNECTS
Including concealed and exposed conduits, boxes, wiring up to corresponding panelboard, cable outlet, fixing support, plate and necessary accessories and connections as specified and shown on drawings.
C01 | Switches (Similar to Legrand)
C02 | 10A One way, one gang switch | U | 20 |  | 0
C03 | 10A Two way, one gang switch | U | 4 |  | 0
C04 | 10A Push button, one gang | U | 24 |  | 0
C05 | Socket outlets (Similar to Legrand)
C06 | 16A/220V, 2P+T Socket outlet | U | 40 |  | 0
C07 | 20A/220V, 2P+T Power Socket outlet | U | 15 |  | 0
C08 | 16A/220V, 2P+T Socket outlet, UPS | U | 20 |  | 0
TELEPHONE AND DATA SYSTEMS
Including concealed and exposed conduits, boxes, wiring up to corresponding cabinet, wiring accessories with supports, mechanisms and cover plates, and necessary accessories and connections, as specified and shown on drawings.
D01 | Patch panel - 19inch rack - 60 Ports | U | 2 |  | 0
D02 | RJ45 Sockets (data and telephone) | U | 60 |  | 0
Total |  |  |  |  | 0