## Grade of Compliance Range
| RFT Scoring Sheet | Reference Number | SF-CF-87
|  | Owner | PRO/PMO
|  | Revision Code | 3.0
|  | Implementation Date | 2024-05-01
Grade of Compliance range from 0 to 15 with a step of 1 unit:
15 : Compliant with additional value, not initially included in the requirements
10 : Fully compliant
4 - 5 - 6: Partially compliant
0 : Not compliant
K : Disqualification
** Project owner should describe how each grade will be selected (0/4-5-6/10/15), and if there is any formula or margins to be mentioned.

## Technical Scoring
| RFT Scoring Sheet | [11 empty] | Reference Number |  | SF-CF-87
[13 empty] | Owner |  | PRO/PMO
[13 empty] | Revision Code |  | 3.0 | 3.0
[13 empty] | Implementation Date |  | 2024-05-01 | 2024-05-01
Project Name | DEKWANEH WAREHOUSE - Electrical Works |  | * For Requirements defined as ''Killer'', a ‘’Fully Compliant’’ score should be the sole acceptable outcome. Failing to obtain a ‘’Fully Compliant’’ score on the requirements defined as Killers, will mandate immediate disqualification for bidders.
Article | Requirements | Weight | Responsible Entity | Supplier 1 | Supplier 2 | Supplier 3 | Supplier 4 | Supplier 5 | Supplier 6 | Remarks | Supplier 1 Final | Supplier 2 Final | Supplier 3 Final | Supplier 4 Final | Supplier 5 Final | Supplier 6 Final
| SECTION 26 24 13 Low Voltage Switchboards - 17.12 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
MAIN DISTRIBUTION BOARDS
| Surface mounted or free standing main distribution boards of hinged cover cabinet type complete with busbars, circuit breakers, switch disconnectors, spares, spaces, digital indicating and measuring devices, "PVC" trunking and wires, ground conductors, cable lugs and accessories. The contractor is responsible to verify the design, make the necessary calculations and shall be responsible for the performance of the system and its compliance with the specified standards. ATS & Main distribution boards shall be equipped with digital power meters Power meter similar to EasyLogic PM2230 Ref. METSEPM2230 | 15%
| Each main distribution panel board has to be provided with engraved metal nameplate mounted with corrosion resistant screws. | 2%
| The electrical cables, inside the main distribution boards, have to be fixed on supports with metallic clamps. | 2%
| All functional units have to be labeled and identified by using engraved metal nameplate mounted with corrosion resistant screws. | 2%
| Cables glands shall be provided at the termination of all cables at the enclosures. | 2%
| The electrical link between the functional units have to be done by rigid bus bars for 100 Amps and more. | 2%
| The flexible insulated bus bars are allowed only between Main Bursars and circuit breakers where their respective frame is equal or lower than 100 Amps. | 5%
| The incoming/outgoing cables are connected to functional units by insulated bus bars and suitable insulated connectors. | 2%
| The direct connection between circuit breakers and outgoing cables is not allowed. | 2%
| All 3-Ph circuit breakers are 4P4D; All switches are 4P; unless otherwise indicated on the drawings | 5%
| Electric socket circuits shall be equipped with 30mA differential protection | 2%
| All panels shall have a minimum of 20% spare space | 4%
SECTION 26 05 19 Low-Voltage Electrical Power Conductors and Cables - 17.12
| Supply, install and connect, Alu/PVC/PVC 600/1000 volts, including pull boxes, cable fixing cable cleats, cable glands, sealing compound, cable sleeves, marking and all necessary accessories as specified and shown on drawings. Similar to Liban Cable | 5%
| Supply, install and connect, Cu/PVC/PVC 600/1000 volts, including pull boxes, cable fixing cable cleats, cable glands, sealing compound, cable sleeves, marking and all necessary accessories as specified and shown on drawings Similar to Liban Cable | 5%
Earth Cables
| Supply, install and terminate earth cables, NYA, including accessories as specified and to the satisfaction of the Engineer. Copper conductor, Single Core, Unarmoured, PVC insulated, Non Sheathed, 450 / 750 V Isolation, with Rigid Conductors - Green/Yellow Similar to Liban Cable | 10%
Miscellaneous Cables
E01 | 10 pair telephone cable, similar to Liban cable LibtelS, 0.5mm² | 2%
E02 | Control cable 10x1.5 mm² Similar to Liban Cable | 2%
Miscellaneous
F01 | Alarm distribution frame 50 pairs similar to KRONE; disconnection module to be provided without earth with punching tool | 5%
EARTH/GROUND
G01 | 3 rods earth system | 1%
G02 | 1 rod earth system | 1%
G03 | Test clamp (disconnecting link) | 1%
G04 | Lightning rod FRANKLIN type 240cm | 1%
G05 | Elevation rod 2m | 1%
G06 | Copper tape 30x2mm | 1%
H01 | Surge Protection Box for Mains Feeder 380Vac
| Panel constructed of weather proof wall mounted metallic box, IP65, with key lockable door consisting of : | 1%
| - Fuse holders, touch-safe dead front, designed to hold 500Vac 22x38mm fuses, DIN rail mountable and easily removed with no additional fuse pullers or tools according to IEC 60269, Four (4) Poles, Rated current 100A, 690V AC, 6kV Uimp Equipped with light indicator and microswitch Similar to DF, Part No. 485331 | 2%
| - Fuse link, Size 22×58 gPV cylindrical fuse link rated 500Vc, 100A, Interrupting Current 120KA, according to IEC 60269, equipped with striker, Similar to DF, Part No. 422200 | 2%
| - L-N Pluggable, coordinated and modular single-pole lightning current arrester with high follow current limitation, Type 1 SPD according to EN 61643-11, Fault indication Max. continuous operating voltage: 255 V a.c. Voltage protection level: <= 2.5 kV Lightning impulse current (10/350): 50 kA Similar to DEHN, Type: DB M 1 255, Part No.: 961120, Qty= 3 | 5%
| - N-PE Modular, pluggable and coordinated single-pole N-PE lightning current arrester, width: 2 modules, Type 1 SPD according to EN 61643-11 Pressurised encapsulated creepage discharge spark gap, Fault indication, Lightning impulse current (10/350): 100 kA Voltage protection level: <= 1.5 kV TOV resistance: 1200 V/200 ms Similar to DEHN, Type: DGP M 255, Part No.: 961101, Qty=1 | 5%
SECTION 26 05 36 Cable Trays for Electrical Systems
| Supply and install hot dip galvanized perforated steel cable trays with straight flange, complete with corners, return edge type, suspension system, fixing and all accessories including covers | 5%
Total |  | 100% | [7 empty] | Total | 0 | 0 | 0 | 0 | 0 | 0
[11 empty] | SUPPLIER 1 SCORE | SUPPLIER 2 SCORE | SUPPLIER 3 SCORE | SUPPLIER 4 SCORE | SUPPLIER 5 SCORE | SUPPLIER 6 SCORE
* For Requirements defined as ''Killer'', a ‘’Fully Compliant’’ score should be the sole acceptable outcome. Failing to obtain a ‘’Fully Compliant’’ score on the requirements defined as Killers, will mandate immediate disqualification for bidders.
Note on D8: Entity (Department/ Unit) that identified the requirement and that will be responsible for its evaluation.
Note on E8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on F8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on G8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on H8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on I8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on J8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements

## Combined Scoring
| RFT Scoring Sheet |  | Reference Number | SF-CF-87
|  |  | Owner | PRO/PMO
|  |  | Revision Code | 3.0 | 3.0
|  |  | Implementation Date | 2024-05-01 | 2024-05-01
Project Name | DEKWANEH WAREHOUSE - Electrical Works
| Technical Score | 40%
| Commercial Score | 60%
| Combined Score | 100%