## Grade of Compliance Range
| RFT Scoring Sheet | Reference Number | SF-CF-87
|  | Owner | PRO/PMO
|  | Revision Code | 3.0
|  | Implementation Date | 2024-05-01
Grade of Compliance range from 0 to 15 with a step of 1 unit:
15 : Compliant with additional value, not initially included in the requirements
10 : Fully compliant
4 - 5 - 6: Partially compliant
0 : Not compliant
K : Disqualification
** Project owner should describe how each grade will be selected (0/4-5-6/10/15), and if there is any formula or margins to be mentioned.

## Technical Scoring
| RFT Scoring Sheet | [11 empty] | Reference Number |  | SF-CF-87
[13 empty] | Owner |  | PRO/PMO
[13 empty] | Revision Code |  | 3.0 | 3.0
[13 empty] | Implementation Date |  | 2024-05-01 | 2024-05-01
Project Name | DEKWANEH WAREHOUSE - Solar |  | * For Requirements defined as ''Killer'', a ‘’Fully Compliant’’ score should be the sole acceptable outcome. Failing to obtain a ‘’Fully Compliant’’ score on the requirements defined as Killers, will mandate immediate disqualification for bidders.
Article | Requirements | Weight | Responsible Entity | Supplier 1 | Supplier 2 | Supplier 3 | Supplier 4 | Supplier 5 | Supplier 6 | Remarks | Supplier 1 Final | Supplier 2 Final | Supplier 3 Final | Supplier 4 Final | Supplier 5 Final | Supplier 6 Final
| PV Module | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Supply, install, connect, and operate with all material needed including supply, install & connect the following: cable trays, clamps, accessories, supports & labels suitable to be installed under the PV arrays. | 10%
A01 | Solar Photovolataic module, Mono-chrystalline, half-cut, mon-crystalline, 600Wp, efficiency 22.21% @ STC, power tolerance 0~+3%, 0.4% annual degredation over 30 years, anti-reflection coating, frame made of anodised aluminum alloy, IP68. similar to Jinko Tiger Neo N-Type | 20%
PV Mounting Structure
| Supply and install Module mounting structure from hot galvanized steel profile foundation or Aluminium profile structures suitable to the dimension of selected PV modules and PV numbers, the mounting provides a fixed inclination of the modules same as the inclined roof with vertical supports, plates, screws, the structure profile includes bracing and double hot galvanized angles for dividers. | 2%
A02 | The mounting structures and the foundations must be designed structurally to be suitable to withstand all static loads (weight of modules and working technician) and dynanic loads (wind load as per Lebanese Norm NL 137_2020 4th ed) that might occur according to site conditions. The mounting structure components are bonded together to guaranty potential equalization. | 2%
Grid-Tie Solar Inverter
| Supply, install, connect, and operate DC/AC, Grid-Tie, 3-phase Solar Inverter with data communication unit with Ethernet connection. The inverter must be suited to any PV module configuration. The inverter unit shall be suitable for outdoor installations with IP66 with efficiency 98.7%, with ethernet and RS485 ports for remote monitoring, arc fault protection, DC surge protection, AC surge protection, anti-islanding protection, AC overcurrent protection, DC reverse polarity protection, PV-array string fault monitoring, residual current monitoring, and maximum total harmonic distortion <3%. | 25%
| Grid Connection Standards: IEC 61727, VDE 0126-1-1 Safety standards: IEC 62109-1/-2, IEC 62116, IEC 60068, IEC 61683 | 15%
A03 | Solar Inverter 36KW, 3-phase, sine wave, Grid-Tie, similar to Huawei SUN2000-36KTL-M3
Fuel Save Controller
| Supply, install, connect, and operate with all material needed including supply, install & connect the following: cables, three (3) current transformer, enclosure, accessories, & labels | 5%
A04 | Fuel Save Controller to handle the power production from PV and genset to give the highest PV penetration and to ensure safe power production to support the load. Similar to DEIF AGC-150 | 5%
Protections
A05 | Surge Protection for PV Cables | 1%
| Panel constructed of weather proof wall mounted metallic box, IP65, with key lockable door consisting of : - Fuse holders, touch-safe dead front, designed to hold 1000Vdc 10x38mm fuses, DIN rail mountable and easily removed with no additional fuse pullers or tools according to IEC 60269-2, -4, and -6. Similar to DF (485153) | 4%
| - Fuse link, rated 1000Vdc, 20A, Interrupting Current 30KA, according to UL 248-1, UL 248-19, IEC 60269-6, similar to DF (491635) | 4%
| - Surge Protection: Modular and pluggable multipole arrester for use in photovoltaic systems up to 1000 V d.c. with three-step d.c. switching device, Fault indication with remote signalling contact, Type 2 SPD according to EN 61643-31. Total discharge current: 40 kA, Voltage protection level: <= 4 kV Similar to DEHN, Type: DG M YPV SCI 1000 FM, Part No. 952515 | 4%
A06 | Cables FLEX/XLPE FLEX/XLPE FLEX 1.5/1.5 (1.8) kV DC, Cu, EN50618, IEC62930 similar to Liban Cable | 3%
Total |  | 100% | [7 empty] | Total | 0 | 0 | 0 | 0 | 0 | 0
[11 empty] | SUPPLIER 1 SCORE | SUPPLIER 2 SCORE | SUPPLIER 3 SCORE | SUPPLIER 4 SCORE | SUPPLIER 5 SCORE | SUPPLIER 6 SCORE
* For Requirements defined as ''Killer'', a ‘’Fully Compliant’’ score should be the sole acceptable outcome. Failing to obtain a ‘’Fully Compliant’’ score on the requirements defined as Killers, will mandate immediate disqualification for bidders.
Note on D8: Entity (Department/ Unit) that identified the requirement and that will be responsible for its evaluation.
Note on E8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on F8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on G8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on H8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on I8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on J8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements

## Combined Scoring
| RFT Scoring Sheet |  | Reference Number | SF-CF-87
|  |  | Owner | PRO/PMO
|  |  | Revision Code | 3.0 | 3.0
|  |  | Implementation Date | 2024-05-01 | 2024-05-01
Project Name | DEKWANEH WAREHOUSE - Solar
| Technical Score | 40%
| Commercial Score | 60%
| Combined Score | 100%