## Grade of Compliance Range
| RFT Scoring Sheet | Reference Number | SF-CF-87
|  | Owner | PRO/PMO
|  | Revision Code | 3.0
|  | Implementation Date | 2024-05-01
Grade of Compliance range from 0 to 15 with a step of 1 unit:
15 : Compliant with additional value, not initially included in the requirements
10 : Fully compliant
4 - 5 - 6: Partially compliant
0 : Not compliant
K : Disqualification
** Project owner should describe how each grade will be selected (0/4-5-6/10/15), and if there is any formula or margins to be mentioned.

## Technical Scoring
| RFT Scoring Sheet | [11 empty] | Reference Number |  | SF-CF-87
[13 empty] | Owner |  | PRO/PMO
[13 empty] | Revision Code |  | 3.0 | 3.0
[13 empty] | Implementation Date |  | 2024-05-01 | 2024-05-01
Project Name | DEKWANEH WAREHOUSE - Fire System - Clean Agent Fire-Extinguishing Systems - FM200 |  | * For Requirements defined as ''Killer'', a ‘’Fully Compliant’’ score should be the sole acceptable outcome. Failing to obtain a ‘’Fully Compliant’’ score on the requirements defined as Killers, will mandate immediate disqualification for bidders.
Article | Requirements | Weight | Responsible Entity | Supplier 1 | Supplier 2 | Supplier 3 | Supplier 4 | Supplier 5 | Supplier 6 | Remarks | Supplier 1 Final | Supplier 2 Final | Supplier 3 Final | Supplier 4 Final | Supplier 5 Final | Supplier 6 Final
| 1 GENERAL | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
1.1 SUMMARY
A. Provide a "Total Flood" Clean Agent Fire Suppression System with automatic detection and control.
B. Design, installation and testing of a calculated automatic and manual fixed total flooding clean agent fire extinguishing system and releasing system in accordance with NFPA 2001, NFPA 72, NFPA 70, and NFPA 75 and manufacturer’s written instructions for the locations shown on the contract drawings.
1.2 REFERENCES
A. Compliancy with international standards:
1. National Fire Protection Association (NFPA):
a. NFPA 2001 - 2022 – Clean Agent Fire Extinguishing Systems
b. NFPA 70 – National Electrical Code
c. NFPA 72 – Standard for Protective Signaling Systems
d. NFPA 75 - 2020 – Standard for the Protection of Information Technology Equipment
B. Laboratory Approvals
1. Loss Prevention Standard (LPS / LPCB)
a. LPS 1204- 3.1 Requirements for firms engaged in the design installation, commissioning and servicing of gas extinguishing systems.
b. LPS 1230- 1.2 Requirements for fire testing of fixed gaseous fire extinguishing systems.
1.3 SUBMITTALS
| A. Detailed installation drawings of the complete detection and suppression system. | 0.5%
| B. FM-200 Quantity calculation notes | 0.5%
| C. FM-200 Hydraulic discharge calculation run on a licensed software | 0.5%
| D. Isometric drawings | 0.5%
1.4 QUALITY ASSURANCE
| A. Manufacturer: The manufacturer of the system components shall have minimum of 10 years’ experience in the manufacture and design of FM-200 fire suppression systems and related fire detection and control equipment. | 5%
| B. Designer and Installer: The installer shall be authorized and trained by manufacturer to design, install, and maintain FM-200 fire suppression systems with a minimum of 10 years’ experience in the field. | 3%
| C. All system components must be approved by Loss Prevention Certification Board (LPCB). | 10%
1.5 DESIGN REQUIREMENTS
| A. Design the system and construct to include a fixed supply of FM-200 cylinders connected to properly sized, fixed piping with fittings and nozzles to direct this agent into an enclosure surrounding the hazard. | 1%
| B. Provide an approved low-pressure FM-200 total flooding type system conforming to NFPA 2001. | 1%
1.6 WARRANTY
| A. The supplied products shall be covered by full supplier warranty for a minimum period of one (1) year from the commissioning date at a full repair and replacement service. Warranty shall include all defected spare parts and workmanship. | 2%
2 PRODUCTS
2.1 MANUFACTURERS
| A. The FACP and peripheral devices shall be manufactured 100% by a single manufacturer (or division thereof). | 10%
| B. The FM-200 suppression system shall be manufactured by an ISO 9001 certified company and meet the requirements of BS EN9001: ANSI/ASQC Q9001:2015. | 10%
2.2 FIRE SUPPRESSION AGENT
| A. The agent shall be FM-200, heptafluoropropane, HFC-227ea. | 1%
B. The physical and chemical properties of FM-200 shall conform with the following requirements:
| 1. NFPA 2001 Standard | 2%
| 2. UL Listed - Ex4623 | 2%
| 3. FM Approved – 3014476 | 2%
| C. The agent shall be stored in containers, super-pressurized with nitrogen to a maximum total pressure level at 70 degrees F of 360 psig. Higher-pressure agents will not be acceptable. | 1%
2.3 Agent Storage Containers
| A. Standard model and size for ease or replacement and addition. Design, fabricate, certify, and stamp cylinders in accordance with ASME Section VIII. | 1%
| B. Agent storage containers shall be floor mounted and shall include bracket assemblies designed to withstand 1000 pounds (453Kg) thrust for 10 seconds. Floor space is limited, therefore, alternatives requiring more floor space will not be considered. | 2%
| C. The storage containers shall be actuated by means of an electronic initiator. Each container shall be actuated individually. Master/slave solenoid configurations will not be considered. | 1%
| D. Cylinder valves: Heavy duty forged brass, incorporating safety release pressure operated manual control, solenoid discharge valve, and pressure gage. Provide solenoid pilot valves for each cylinder or bank of cylinders. | 1%
| E. Manifold: Provide for systems with more than one cylinder with rack to secure each cylinder and check valves between each cylinder discharge and manifold. | 1%
| F. The container and valve shall be capable of releasing the agent as fast as possible and shall in no case exceed 10 seconds. | 1%
| G. Safety Release: Equip cylinder with frangible disc safety device that operates when internal pressure exceeds 730 pounds per square inch. | 1%
2.4 ACTUATOR
| A. Release of the agent shall be accomplished by an electrical signal from the system control panel in conjunction with a specifically designed agent release module. | 1%
| B. Systems that employ more than one cylinder shall have all electric initiators connected in parallel. | 1%
| C. The electric actuator should be easily removed and installed without a means of toolkit. | 2%
2.5 MANUAL STATIONS WITH DIGITAL COUNTDOWN TIMER
| A. Identification: “AGENT RELEASE” caption, and red finish. | 1%
| B. Unit shall have a metal housing with a dual action release configuration requiring two distinct operations to initiate a system actuation in order to prevent accidental system discharge. | 1%
| C. The countdown timer provides a digital readout, indicating the number of seconds remaining until the clean agent discharges. There shall be a label stating “Seconds Remaining to Discharge” at the digital readout. | 2%
2.6 ABORT STATION
| A. "Dead Man" type, located next to each manual switch. | 1%
| B. Supervised with indication of a trouble condition at the control panel, if depressed and no alarm condition exist. | 1%
| C. Identification: “ABORT” caption, momentary contact, with yellow button. | 1%
2.7 SWITCHES
| A. Listed and approved type, 220-Vac or low voltage compatible with controls. | 1%
| B. Low-Agent Pressure Switch: Pneumatic operation | 1%
2.8 LOW PRESSURE SWITCH
| A. The agent storage container shall be equipped with a low-pressure switch to indicate a loss of container pressure. A decrease in pressure from 360 psi to 275/272 psi will cause the normally closed contact to open, thereby indicating a trouble condition. | 2%
| B. Low pressure switch shall be monitored by the system control panel (FACP) and shall provide a specific indication of cylinder low pressure. | 1%
2.9 LIQUID LEVEL INDICATOR
| A. Tanks holding in excess of 60 pounds (27Kg) of agent shall contain a liquid level indicator to monitor vessel contents, in addition to the low-pressure switch. | 2%
2.10 DISCHARGE NOZZLES
| A. Nozzles shall distribute the agent throughout the protected area. Single nozzle shall not discharge more than 250 pounds (113kG) of agent. | 1%
| B. The nozzles shall utilize a 180 or 360-degree pattern and shall be designed to direct the discharge of agent parallel to the ceiling, thus minimizing the possibility of disturbance to objects within the room. | 1%
| C. Deflector plates shall be used with the nozzles when sensitive ceiling tiles must be protected. | 1%
| D. A maximum nozzle flow rate of 17 lbs./sec (7.7Kg/sec) shall be designed for all areas with false ceilings or delicate operations. Higher flow rates may dislodge objects, which could damage or affect equipment and/or process. | 1%
| E. Construction: One-piece chrome plated brass or aluminum nozzle with textured finish with female pipe thread integral on body. Direct discharge parallel to ceiling. | 1%
| F. Identification: Permanently mark nozzles to show equivalent single orifices diameter. | 1%
2.11 PIPE AND FITTINGS
A. Pipe
| 1. Meets requirements of ASTM A53/A53M T, Type E (electric-resistance welded, Grade A or Grade B) or Type S (seamless, Grade A or Grade B). | 1%
| 2. Pipe shall be threaded end connections, Schedule 80 or Weight Class XS (Extra Strong), except that sizes smaller than one inch may be Schedule 40 or Weight Class STD (Standard). | 1%
| 3. Pipe shall be epoxy coated, installed exposed, including all kind of supports and hangers. | 1%
| 4. Provide pipe and fittings having a minimum bursting pressure of 41.37 Mega Pascal (6,000 psi). | 1%
| B. Threaded Fittings: Use hot-dipped galvanized, ASME B16.11, except sizes 50 mm (2 inches) and smaller may conform to ASME B16.3, Class 300 | 1%
| C. Unions: ASME B16.39, Class 300 | 1%
2.12 PIPE HANGERS AND SUPPORTS
| A. Provide zinc-coated, adjustable pipe hangers and supports conforming to MSS SP-58 and MSS SP-69. | 2%
2.13 PRESSURE RELIEF DEVICE
| A. Provide each system with an approved device designed to operate between 16.50 and 20.70 MPa (gage) 2400 and 3000 psi. | 2%
2.14 PRESSURE-OPERATED FIRE ALARM
| A. Sends signal to FACP when FM200 gas is released/discharged. | 1%
| B. Pressure Switch is connected to cylinder head with a flexible hose. | 1%
2.15 SIGNS AND IDENTIFICATION
| A. Provide signs and identification to each valve required to be identified. | 1%
| B. Provide engraved nameplates for all manual discharge stations and abort switch locations to indicate their function. All alarm devices shall have similar identification plates. | 0.5%
| C. Each entrance door shall include a caution placard indicating that the area is being protected by a clean agent fire suppression system. | 0.5%
2.16 LABELS
| A. FM200 Cylinders should be labeled and numbered with large readable markings. | 1%
2.17 ACCESSORIES
| A. All accessories necessary for the installation and proper operation of the system should be delivered with the system free of charge. | 1%
END OF SECTION
Total |  | 100% | [7 empty] | Total | 0 | 0 | 0 | 0 | 0 | 0
* For Requirements defined as ''Killer'', a ‘’Fully Compliant’’ score should be the sole acceptable outcome. Failing to obtain a ‘’Fully Compliant’’ score on the requirements defined as Killers, will mandate immediate disqualification for bidders.
Note on D8: Entity (Department/ Unit) that identified the requirement and that will be responsible for its evaluation.
Note on E8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on F8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on G8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on H8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on I8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on J8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements

## Combined Scoring
| RFT Scoring Sheet |  | Reference Number | SF-CF-87
|  |  | Owner | PRO/PMO
|  |  | Revision Code | 3.0 | 3.0
|  |  | Implementation Date | 2024-05-01 | 2024-05-01
Project Name | DEKWANEH WAREHOUSE - Fire System - Clean Agent Fire-Extinguishing Systems - FM200
| Technical Score | 40%
| Commercial Score | 60%
| Combined Score | 100%