## Fire
DEKWANEH WAREHOUSE BILL OF QUANTITIES - FIRE PROTECTION
ITEM | DESCRIPTION | UNIT | QTY | UNIT PRICE | TOTAL USD
OFFICES & STORE ROOMS
1 | FM-200 System serving the Electrical Room (Total of 23Kg of FM-200) Void (FFL to ceiling) Area: 13.5m², height = 3m | Ea. | 1 |  | 0
2 | FM-200 System serving the Indoor Storage Room @ GF (Total of 247Kg of FM-200) Void (FFL to ceiling) Area: 146m², height = 3m | Ea. | 1 |  | 0
3 | FM-200 System serving the Indoor Storage Room @ 1st Floor (Total of 78Kg of FM-200) Void (FFL to ceiling) Area: 46m², height = 3m | Ea. | 1 |  | 0
4 | Mechanical installation of FM200 system including piping, nozzles, and all required accessories for complete system installation | Ea. | 1 |  | 0
5 | Fire detection system including: - FACP - Smoke detector - Abort Push Button - Horn - Strobe - Indoor - Strobe - Outdoor - Luminous Evacuate Sign - Pressure Switch - Fire rated cables - Warning signs | Ea. | 4 |  | 0
6 | CO2 Portable fire extinguisher (6kg) | Ea. | 20 |  | 0
7 | ABCE Dry Chemical Portable fire extinguisher (5kg) | Ea. | 10 |  | 0
WAREHOUSE
Detection System
8 | Fire Alarm Control Panel Conventional | U | 1 |  | 0
9 | Reflective Beam Detector | U | 10 |  | 0
10 | Break Glass, Indoor Manual Call Point Without LED - Red | U | 5 |  | 0
11 | Fire Bell | U | 4 |  | 0
Sprinkler System
12 | Standard Response, Pendant Sprinkler, 1/2", 68C, Bronze, K5.6, Reliable, UL/FM | LS | 275 |  | 0
13 | Black seamless Pipes of 5.80 M length | LS | 1 |  | 0
1" Ø25 mm 670m. Piece 116
1¼" Ø32 mm 128m. Piece 22
1½" Ø40 mm 92m. Piece 16
2" Ø50 mm 12m. Piece 3
2½" Ø65 mm 18m. Piece 4
3" Ø80 mm 48m. Piece 9
4" Ø100 mm 54m. Piece 10
6" Ø150 mm 42m. Piece 8
14 | Fittings and accessories | LS | 1 |  | 0
15 | Installation of sprinkler system | LS | 1 |  | 0
Fire Hose Cabinets
16 | Fire Hose Reel Cabinet, Surface Mounted, Horizontal, 1.2mm Full Mild Steel, Single Compartment, Solid Door, Red Powder Coated, Size 70 X 72 X 28 including Fire Hose Reel 1" x 30 Mtr. Cabinet Mounted, Manual with Plastic Nozzle, Kitemark LPCB Approved | U | 6 |  | 0
Fire Pump Set
17 | Diesel Pump achieving 350 GPM @ 7 Bars Type : Base mounted, Horizontal, End Suction. Motor : 30 KW, 50 Hz, water cooled 2900 RPM, Class F, IP 55. Construction : Cast iron casing and impeller, stainless steel shaft, mechanical seal. | U | 1 |  | 0
18 | Electrical Pump achieving 350 GPM @ 7 Bars Type : Base mounted, Horizontal, End Suction. Motor : 30 KW, 3 phase, 400 V, 50 Hz, 2900 RPM, Class F, IP 55. Construction : Cast iron casing and impeller, stainless steel shaft, mechanical seal. | U | 1 |  | 0
19 | Jockey Pump achieving 10 GPM @ 7 Bars Type : Multi-stage, Vertical, Inline. Motor : 0.55 KW, 3 phase, 400 V, 50 Hz, 2900 RPM, Class F, IP 55. Construction : Stainless Steel casing and impellers, stainless steel shaft, mechanical seal. | U | 1 |  | 0
20 | Common operating Control Panel with pump controllers and indicators. | U | 1 |  | 0
21 | Common base plate and accessories | LS | 1 |  | 0
22 | Fire Extinguisher Trolley 12KG Powder | U | 1 |  | 0
23 | Fire Extinguisher Trolley 50KG Powder | U | 2 |  | 0
24 | Testing and commissioning | LS | 1 |  | 0
Total |  |  |  |  | 0