## Grade of Compliance Range
| RFT Scoring Sheet | Reference Number | SF-CF-87
|  | Owner | PRO/PMO
|  | Revision Code | 3.0
|  | Implementation Date | 2024-05-01
Grade of Compliance range from 0 to 15 with a step of 1 unit:
15 : Compliant with additional value, not initially included in the requirements
10 : Fully compliant
4 - 5 - 6: Partially compliant
0 : Not compliant
K : Disqualification
** Project owner should describe how each grade will be selected (0/4-5-6/10/15), and if there is any formula or margins to be mentioned.

## Technical Scoring
| RFT Scoring Sheet | [11 empty] | Reference Number |  | SF-CF-87
[13 empty] | Owner |  | PRO/PMO
[13 empty] | Revision Code |  | 3.0 | 3.0
[13 empty] | Implementation Date |  | 2024-05-01 | 2024-05-01
Project Name | DEKWANEH WAREHOUSE - Fire System - Zoned (DC Loop) Fire-Alarm Systems |  | * For Requirements defined as ''Killer'', a ‘’Fully Compliant’’ score should be the sole acceptable outcome. Failing to obtain a ‘’Fully Compliant’’ score on the requirements defined as Killers, will mandate immediate disqualification for bidders.
Article | Requirements | Weight | Responsible Entity | Supplier 1 | Supplier 2 | Supplier 3 | Supplier 4 | Supplier 5 | Supplier 6 | Remarks | Supplier 1 Final | Supplier 2 Final | Supplier 3 Final | Supplier 4 Final | Supplier 5 Final | Supplier 6 Final
| 1 GENERAL | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
1.1 SUMMARY
A. This section of the specifications includes the furnishing, installation, and connection of the fire alarm equipment to form a complete coordinated system ready for operation. It shall include, but not be limited to, alarm initiating devices, alarm notification appliances, control units, fire safety control devices, annunciators, power supplies, and wiring as shown on the drawings and specified.
1.2 REFERENCES
A. Compliancy with international standards:
1. National Fire Protection Association (NFPA):
a. NFPA 12 – Standard on Carbon Dioxide Extinguishing Systems.
b. NFPA 2001 – Standard on Clean Agent Fire Extinguishing Systems.
c. NFPA 70 – National Electrical Code.
d. NFPA 72 – Standard for Protective Signaling Systems.
2. British Standards
a. BS 5839 – Part 1 (Fire detection and alarm systems for buildings. Code of practice for system design, installation and servicing.
b. BS 6266 – Code of practice for fire protection for electronic data processing installations
c. BS 7273-1 – Code of practice for the operation of fire protection measures
B. Laboratory approvals
1. Loss Prevention Certification Board (LPCB)
2. Underwriter Laboratories (UL)
1.3 QUALITY ASSURANCE
| A. Manufacturer: The manufacturer of the system components shall have minimum of 10 years’ experience in the manufacture and design of fire detection systems and control equipment. | 5%
| B. Installer: The installer shall be authorized and trained by manufacturer to design, install, and maintain fire detection systems. | 2%
| C. All system components must be approved by Loss Prevention Certification Board (LPCB) or Underwriter Laboratory (UL). | 5%
1.4 WARRANTY
A. Equipment
| 1. The supplied products shall be covered by full supplier warranty for a minimum period of one (1) year from commissioning date at a full repair and replacement service. Warranty shall include all defected spare parts and workmanship. | 2%
2 PRODUCTS
2.1 MANUFACTURERS
| 1. The FACP and peripheral devices shall be manufactured 100% by a single manufacturer (or division thereof). | 5%
| 2. The fire alarm system shall be manufactured by an ISO 9001 certified company and meet the requirements of BS EN9001: ANSI/ASQC Q9001:2015. | 5%
2.2 FIRE ALARM CONTROL PANEL (FACP)
A. Functional Description
| 1. The Single Area Conventional Fire Alarm Control Panel (FACP) shall be the central processing unit of the system, receiving and analyzing signals from fire detectors or manual releasing devices, providing audible and visual information to the user, initiating automatic alarm response sequences and providing the means by which the user interacts with the system. It shall also have the capability to electronically activate and release extinguishant by means of control of a solenoid valve. | 1%
| 2. FACP shall comply and should be certified to BS/LPCB or UL/FM. | 4%
| 3. The FACP shall be certified as meeting the requirements of EN 12094-1, (Environmental Class A) by a suitable, notified body. A certificate and test report shall be made available for inspection as evidence of certification. | 2%
| 4. The FACP shall have the capability to support two (2) zones of conventional detection all of which configured to contribute to the release of the extinguishant. | 2%
| 5. Each conventional detection zone shall be capable of supporting up to 20 conventional fire detectors. The detection zones shall be capable of supporting intrinsically safe detection devices using appropriate intrinsically safe (IS) barriers. | 1%
| 6. The FACP shall have the capability to operate in either manual mode or automatic and manual (combined) mode. The mode of the system shall be selectable by means of a key operated switch. In manual mode the extinguishant will not be released by automatic detection. | 2%
| 7. Time delay before extinguishant release should be 30 seconds. | 1%
| 8. In addition to the activation of the extinguishant output, the FACP shall be capable of halting the release of the extinguishant by the operation of a "hold-off" input. | 1%
| 9. The FACP shall have a facility for connecting door interlock switches to change the mode of the system from "automatic and manual" to "manual only". | 1%
| 10. The FACP shall have the facility to monitor a pressure switch connected to the extinguishant cylinder, which indicates release of extinguishant from the cylinder. | 1%
| 11. The FACP shall provide 2 sounder outputs, which operate when any alarm is detected (first stage alarm). It shall be possible to program a delay from 30 seconds or 1 minute to 10 minutes (in 1 minute steps) before the first stage alarm outputs activate. | 1%
| 12. The FACP shall contain one sounder output, which operates when the FACP is in the activated condition (second stage alarm). | 1%
| 13. The FACP shall provide a volt free changeover contact, which operates when first stage alarm is detected (1st fire alarm relay). This relay shall de-activate only when the FACP is reset. | 2%
| 14. The FACP shall provide a volt free changeover contact, which operates when second fire alarm is detected (2nd fire alarm relay). This relay shall de-activate when FACP is reset. | 2%
| 15. The FACP shall provide a volt free changeover contact, which operates when any fault or power loss is detected (fault relay). This relay shall de-activate only when the FACP is reset. | 2%
| 16. Sequence of Operation: System operation shall be such that when a smoke detector detects fire in a zone, it shall send a signal to the FACP which sends it in turn to the alarm distribution frame (ADF) for tele-reporting and starts a first stage alarm status (Preliminary Alarm). This first stage includes an intermittent sound alarm from an electronic siren and a visual alarm from a light strobe. Then, if the alarm condition is confirmed by a second smoke detector, the fire alarm panel shall trigger a second alarm status (2nd stage fire alarm) where the siren shall send a continuous sound and a luminous warning sign inside the room shall be lit. Also, an alarm signal shall be sent to the alarm distribution frame (ADF) and an outdoor warning strobe shall be lit for the attention of the personnel not to enter the protected zone. The audio/visual alarm conditions shall remain for 30 seconds before agent discharge. During this period, personnel should evacuate the premises prior to discharge. | 1%
B. Front panel controls
1. The FACP shall have the following front panel controls:
| a. Silence/sound alarm (first stage) | 0.5%
| b. Alarm/fault warning silence (buzzer) | 0.5%
| c. Reset | 0.5%
| d. Lamp test | 0.5%
| e. Mode • Select • Enter | 0.5%
| f. Enable controls (Key operated switch) | 0.5%
| g. Manual only or Automatic and manual (Key operated switch) | 0.5%
| h. Manual release (Lift flap, push button) / Output Disable | 0.5%
C. Front panel indications
1. The FACP shall have the following front panel indications:
| a. Power on | 0.5%
| b. Test mode | 0.5%
| c. Power fault | 0.5%
| d. General fault | 0.5%
| e. System fault | 0.5%
| f. Alarm/Fault warning silenced | 0.5%
| g. Sounder fault/disabled | 0.5%
| h. Fire zone 1 & Fire zone 2 | 0.5%
| i. Fault zone 1 & Fault zone 2 | 0.5%
| j. Extinguishant disabled | 0.5%
| k. Manual release disabled | 0.5%
| l. 1st stage contact disabled | 0.5%
| m. 2nd stage contact disabled | 0.5%
| n. Extract fan disabled | 0.5%
| o. Extinguishant released | 0.5%
| p. Release imminent | 0.5%
| q. 1st stage activated | 0.5%
| r. Hold activated | 0.5%
| s. Flooding zone fault | 0.5%
| t. Low pressure | 0.5%
| u. Manual only mode | 0.5%
| v. Automatic and manual mode | 0.5%
2.3 BATTERY
| A. Battery backup power shall be through use of rechargeable, sealed-type storage batteries and battery charger. | 1%
| B. Battery capacity should be capable to operate the fire alarm system for 24 hours in supervisory (standby) mode. | 1%
| C. Following this period of standby battery operation, the batteries shall have ample capacity to operate all components of the system, including all alarm signaling devices in the total alarm mode for a minimum period of 1 hour. | 1%
2.4 BATTERY CHARGER
| A. Battery charger shall be completely automatic, 24 Vdc with high/low charging rate, capable of restoring the batteries from full discharge (18 Vdc) to full charge within 48 hours. | 1%
2.5 ABORT PUSH BUTTON
| A. Abort push button (APB) shall be white in color with a red, momentary pushbutton, lockable, and turn to release. | 5%
2.7 MANUAL FIRE ALARM STATIONS
| A. Manual fire alarm stations shall conform to the applicable requirements of BS. | 1%
| B. Stations shall be double action type. | 1%
| C. Stations shall be finished in red, with raised letter operating instructions of contrasting color. | 1%
| D. The use of a key shall be required to reset the station. | 1%
2.8 PHOTOELECTRIC SMOKE DETECTOR
| A. Smoke detectors shall be designed for detection of abnormal smoke densities. | 0.5%
| B. EN54 approved by LPCB | 2%
| C. Detectors shall contain a visible indicator LED that shows when the unit is in alarm condition. | 1%
| D. Optical detectors shall be used | 0.5%
| E. Detectors shall operate on a light scattering concept using an LED light source. | 0.5%
| F. Diode base allowing the monitoring of a removed detector with BS 5839. | 0.5%
2.17 HORN
| H. Horns shall produce a sound rating of at least 92 dBA at 3m. | 1%
| I. Horn should offer two (2) distinct prioritized audible signals from two isolated inputs. | 1%
2.18 STROBE
| A. Strobe shall have clear high intensity optic lens, xenon flash tubes, and output white light. | 2%
| B. Strobe flash rate shall be between 1 to 3 flashes per second and a minimum of 75 candela. | 2%
2.19 LUMINOUS EVACUATE SIGN
| A. Internal luminous warning sign, 10cd, with red letterings: | 1%
| 2. or “FM200 Release – Evacuate Immediately” | 1%
| B. Lighting with high luminosity LED - IP55 | 1%
| C. Internal luminous warning sign is activated on the second stage. | 1%
2.20 WARNING PLATES
A. Door Caution Plate: Door caution plate text should be:
| 2. FM200 protected area: “FM-200 – CAUTION! – This area is protected by a gaseous fire extinguishing system – When alarm sounds or upon gas discharge evacuate hazard area immediately – After discharge do NOT re-enter until thoroughly ventilated” | 2%
B. Manual Release Caution Plate: Warning sign text should be:
| 2. “FM-200 – RELEASE – Manual Control Point – FM-200 – CAUTION – Ensure all personnel are evacuated before releasing FM-200” | 2%
2.21 WIRING
| A. Fire resistant and flame-retardant control cables, BS6387, shall be utilized to connect the different devices of the fire detection system | 1%
| B. Power cable 3x1.5mm² shall be used to connect the FACP to the electrical distribution panel (220Vac) | 1%
| C. Wiring for fire alarm circuits shall be 1.5mm² cross-section, solid copper, three conductors, color coded, with red colored jacket | 1%
2.22 ACCESSORIES
| 1. All accessories necessary for the installation and proper operation of the system should be delivered with the system free of charge. | 1%
END OF SECTION
Total |  | 100% | [7 empty] | Total | 0 | 0 | 0 | 0 | 0 | 0
[11 empty] | SUPPLIER 1 SCORE | SUPPLIER 2 SCORE | SUPPLIER 3 SCORE | SUPPLIER 4 SCORE | SUPPLIER 5 SCORE | SUPPLIER 6 SCORE
* For Requirements defined as ''Killer'', a ‘’Fully Compliant’’ score should be the sole acceptable outcome. Failing to obtain a ‘’Fully Compliant’’ score on the requirements defined as Killers, will mandate immediate disqualification for bidders.
Note on D8: Entity (Department/ Unit) that identified the requirement and that will be responsible for its evaluation.
Note on E8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on F8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on G8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on H8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on I8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on J8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements

## Combined Scoring
| RFT Scoring Sheet |  | Reference Number | SF-CF-87
|  |  | Owner | PRO/PMO
|  |  | Revision Code | 3.0 | 3.0
|  |  | Implementation Date | 2024-05-01 | 2024-05-01
Project Name | DEKWANEH WAREHOUSE - Fire System - Zoned (DC Loop) Fire-Alarm Systems
| Technical Score | 40%
| Commercial Score | 60%
| Combined Score | 100%