## Generator
DEKWANEH WAREHOUE BILL OF QUANTITIES - GENSET INSTALLATION
ITEM | DESCRIPTION | UNIT | QTY | UNIT PRICE | TOTAL USD
Power Generators
1 | Diesel generator, 100KVA prime | U | 1 |  | 0
2 | Sound proof canopy to 65 dBA @ 1m | U | 1 |  | 0
3 | Battery charger 10A | U | 1 |  | 0
4 | Termination on generation main breaker with all needed lugs and accessories | U | 1 |  | 0
5 | Anti-Vibration Pads - Similar to Sylomer® SR220 Length 250mm, Width 250mm, Thickness 75mm Set of 6 pieces | U | 1 |  | 0
6 | Steel plates galvanized 250mmx250mmx50mm to be installed between anti-vibration pad and canopy base; Set of 6 pieces | U | 1 |  | 0
7 | Installation of generator on concrete slab at ground level. | LS | 1 |  | 0
Fuel System
8 | Fuel tank 2000L; 200x100x100cm with retention tray - Constructed of 3mm non galvanized metal sheets - Sprayed with furnace paint, color RAL 7015 - Retention tray extended 10cm from tank perimeter and edge height 10cm provided with a ½ inch drain ball valve. Tray should covered from rain. - Hose level indicator with ball valve - Refer to fuel pipes connections drawing | U | 2 |  | 0
9 | Fuel supply per 1000 liters | U | 1 |  | 0
10 | Diesel Fuel Filter and Water Separator DAHL 100, 40GPH | U | 1 |  | 0
11 | Set of 12 padlocks YALE with 1 master key | U | 1 |  | 0
Supply and installation of seemless black steel fuel pipes, painted dark grey color, complete with all required accessories:
12 | 3/4 inch | m | 20 |  | 0
13 | 3/4 inch ball valves | U | 10 |  | 0
14 | 2" black steel pipe for fuel refilling box | m | 2 |  | 0
15 | 2" elbow | U | 5 |  | 0
16 | 2" accessories and fittings | U | 5 |  | 0
17 | 2" quarter turn valve | U | 5 |  | 0
18 | Metallic refilling box fully equipped (q.t. valve, one way valve, accessories) | U | 1 |  | 0
19 | Concrete blocks for fixation of fuel pipes and cable trays; dimensions 10x10x20cm | U | 10 |  | 0
Total |  |  |  |  | 0