## Grade of Compliance Range
| RFT Scoring Sheet | Reference Number | SF-CF-87
|  | Owner | PRO/PMO
|  | Revision Code | 3.0
|  | Implementation Date | 2024-05-01
Grade of Compliance range from 0 to 15 with a step of 1 unit:
15 : Compliant with additional value, not initially included in the requirements
10 : Fully compliant
4 - 5 - 6: Partially compliant
0 : Not compliant
K : Disqualification
** Project owner should describe how each grade will be selected (0/4-5-6/10/15), and if there is any formula or margins to be mentioned.

## Technical Scoring
| RFT Scoring Sheet | [11 empty] | Reference Number |  | SF-CF-87
[13 empty] | Owner |  | PRO/PMO
[13 empty] | Revision Code |  | 3.0 | 3.0
[13 empty] | Implementation Date |  | 2024-05-01 | 2024-05-01
Project Name | DEKWANEH WAREHOUSE - Generators |  | * For Requirements defined as ''Killer'', a ‘’Fully Compliant’’ score should be the sole acceptable outcome. Failing to obtain a ‘’Fully Compliant’’ score on the requirements defined as Killers, will mandate immediate disqualification for bidders.
Article | Requirements | Weight | Responsible Entity | Supplier 1 | Supplier 2 | Supplier 3 | Supplier 4 | Supplier 5 | Supplier 6 | Remarks | Supplier 1 Final | Supplier 2 Final | Supplier 3 Final | Supplier 4 Final | Supplier 5 Final | Supplier 6 Final
| 1 GENERAL | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
1.1 STANDARDS
A. ISO 3046-1:2002 - Reciprocating internal combustion engines -- Performance -- Part 1: Declarations of power, fuel and lubricating oil consumptions, and test methods -- Additional requirements for engines for general use
B. Manufacturing Standards: ISO 9001 & ISO 14001
1.2 SUBMITTALS
A. The Bidder shall submit all relevant technical data sheets in hard and soft copies. Offer with missing technical data sheets will be disqualified.
C. Certificates
| 1. Factory test results | 0.1%
| 2. Certificate of origin for engine and alternator | 0.1%
| 3. ISO certificate of generator assembler | 5%
| 4. ISO certificate of local supplier | 0.1%
1.3 WARRANTY
A. Equipment
| 1. The supplied products shall be covered by full supplier warranty for a minimum period of one (1) year from commissioning/delivery to site (as of the PAC date of issuance) or 1,000 hours of operation at a full repair and replacement service. | 0.1%
| 2. Warranty shall include all defected spare parts and workmanship. | 0.1%
B. Services
1. Installation and dismantling
| a. The supplier is responsible for the dismantling, hoisting, transportation and re-installation for parts that cannot be repaired or replaced on site | 0.1%
2. Part replacement/repair
| a. For any part replacement or repair service the warranty for the repaired or new part shall be a minimum of 12 (twelve) months from the date of receipt of the repaired or new part. In case a part was repaired twice already under this warranty and the equipment becomes faulty again within up to six months the Operator on its discretion may request replacement of the complete equipment | 1%
3. Major defect
| a. In case of major defect in the supplied products (genset, engine, alternator, control panel, AVR, etc.), the Operator reserves the right to reject the equipment. The supplier shall replace the defected system/parts under no cost from the Operator, including dismantling, hoisting, transportation and re-installation | 0.1%
1.4 TESTING
| A. Factory Testing: Before shipment of equipment, factory test generator set including engine, alternator, control panels, transfer equipment and accessories for performance and proper functioning of control and interfacing circuits. | 0.1%
B. Witness Testing at Supplier’s Workshop
| 1. Witness testing, also known as a Factory Acceptance Test (FAT), shall takes place prior to full site installation and commissioning. | 0.1%
2. TESTS are to include:
| a. Functional tests for voltage sensing, automatic start and transfer of load as applicable | 0.1%
| b. Operation of engine shut- down and alarm a signaling and indication, under simulated fault conditions | 0.1%
| 3. Test procedure: with a portable resistive load bank at 100% rated load of generator, operate set for 8 hours continuously, taking readings at 30-minute intervals, and followed by 10% overload for 1 hour, without interruption. | 0.1%
2 PRODUCTS
2.1 GENERATOR SET
| A. Diesel Generator Set shall be manufactured by an ISO certified assembler as per ISO 9001:2015. | 2%
| B. Generator set mounted on heavy duty steel-based frame incorporating anti-vibration pads | 0.1%
| C. Guards shall be integrally mounted on unit to protect personnel from hot and moving parts (fan, fan drive, battery charger, etc.). | 0.1%
2.2 DIESEL ENGINE
| A. Prime Power: 100KVA | 30%
| C. Number of cylinders: 3 vertical in-line, Cycle 4 stroke, Combustion system: Indirect injection | 0.1%
| D. Mounted air filter, natural aspiration | 0.1%
| E. Fuel system: rotary type pump | 0.1%
| F. Lubrication system: wet sump with filler and dipstick with spin-on oil filter | 0.1%
G. Cooling system: Water cooling system
| 3. Thermostatically-controlled system with gear-driven circulation pump and belt-driven pusher fan | 0.1%
H. Electrical equipment
| 1. A 12 volt starter motor and 12 volt 65 amp alternator with DC output | 0.1%
| 2. A 12 volt shutdown solenoid energized to run | 0.1%
| I. Antifreeze coolant of 50% ratio should be added to the radiator water | 0.1%
2.3 ALTERNATOR
| A. Net Rated Power: 100KVA - similar to Leroy Somer, TAL044 D, 100KVA, 3Ph, 380Vac | 20%
| B. Factory of origin should be indicated. | 0.1%
C. Rating Type
| 1. Prime Power: Output available with varying load for an unlimited time. Average power output is 70% of the prime power rating. | 0.1%
| 2. Typical peak demand is 100% of prime rated ekW with 10% overload capability for emergency use for a maximum of 1 hour in 12. | 0.1%
D. Electrical Characteristics
| 1. Rated voltage, Frequency: 380Vac L-L / 220Vac L-N / 50Hz | 0.1%
| 2. Rated power factor: 0.8 | 0.1%
| 3. Insulation: class H, 40°C for stator, class H, 40°C for Rotor and exciter. | 1%
E. Mechanical Characteristics
| 1. Steel frame with aluminum flanges and shields | 0.1%
| 2. Enclosure: drip proof and screen protected; IP 23 to IEC 529 | 0.1%
| 3. Single bearing | 0.1%
| 4. Permanently greased bearings: 20,000h | 0.1%
2.4 AUTOMATIC VOLTAGE REGULATION (AVR)
| 1. Excitation Type: Shunt - 3 phase sensing | 5%
| 2. Voltage regulation: automatic ±1% | 0.1%
| 3. Similar to Leroy Somer R150 | 0.1%
2.5 CONTROL PANEL
A. Construction
| 1. Provide a unit mounted control panel that is factory built, wired, tested and shock-mounted by the unit manufacturer. | 0.1%
| 2. Control panel shall be a rigid, metal enclosure, mounted on the generator end of the set, containing all devices as specified herein, and as required for described functions with door rotating on hinges. | 0.1%
B. Components
| 1. Remote start board, equipped with USB Port and RS232 Port. | 0.1%
| 2. Protection fuse holders of size 15x10mm for AC and DC control equipment | 0.1%
| 3. 11pin relays, 3 dry contacts, 10A AC3, similar to Finder or Schrack | 0.1%
| 4. Cable glands shall be used for cables entering the panel | 0.1%
| 5. All wires shall end with crimp terminals | 0.1%
| 6. Control wires shall have a minimum cross-section of 1.5mm² | 0.1%
| 7. Hours run meter | 0.1%
| 8. Emergency stop push button: Mushroom Head Emergency Stop Push button, Turn to Release, Color Red, Contacts 10A, shutdown in manual and auto modes | 0.1%
| C. Operation: Auto and Hand Drive start | 0.1%
D. Settings
| 1. Voltage set to 400Vac L-L / L-N 230Vac, 52Hz at no load | 0.1%
| 2. Three (3) tentative starts (cranking time 4 sec, rest 10 sec for a duration of 1 minute) | 0.1%
| E. Main circuit breaker: 4 poles similar to Schneider | 2%
F. Identification Labels
| 1. Control wires shall be numbered on both ends for ease of tracing according to MIC1 schematics | 0.1%
| 2. Terminal blocks shall be numbered | 0.1%
| 3. All components should be labeled with double PVC adhesive tapes, on component and on back plate | 0.1%
| G. Digital LCD) Display | 2%
| 1. Generator AC Voltage – 3 phase (L-L & L-N) | 0.1%
| 2. Generator AC Current – 3 phase (L1, L2, L3) | 0.1%
| 3. Generator Power kW | 0.1%
| 4. Generator Frequency | 0.1%
| 5. Engine RPM | 0.1%
| 6. Battery Voltage | 0.1%
| 7. Engine Hours | 0.1%
| 8. Engine Successful Start Counter | 0.1%
| 9. Engine Oil Pressure | 0.1%
| 10. Engine Coolant Temperature | 0.1%
| 11. Ten (10) Event Fault Log | 0.1%
H. Automatic shut-down with lights and alarms
| 1. Fail to start, Over-crank (shutdown after 3 cranking attempts) | 0.1%
| 2. Emergency stop | 0.1%
| 3. High Battery | 0.1%
| 4. Low Battery | 0.1%
| 5. Engine High Engine Temp | 0.1%
| 6. Engine Low Coolant Level | 0.1%
| 7. Engine Low Oil Pressure | 0.1%
| 8. Low Dynamo Volt | 0.1%
| 9. Genset Over-Voltage | 0.1%
| 10. Genset Under-Voltage | 0.1%
| 11. Genset Phase Failure | 0.1%
| 12. Genset Sequence Failure | 0.1%
| 13. Genset Over-Frequency | 0.1%
| 14. Genset Under-Frequency | 0.1%
| 15. Overload | 0.1%
| 16. Short circuit | 0.1%
| 17. Engine fuel/oil/water leak (sensor located in retention tray) | 0.1%
| 18. Emergency stop push button activated; Auto and Hand-Drive Modes | 0.1%
| I. Digital Inputs: Emergency Stop and Remote Start | 0.1%
| J. Digital Output: Common alarm dry contacts NCO | 0.1%
2.6 NEUTRAL CONNECTION
| A. Neutral of generator, at the CB input side, shall be earthed by an insulated conductor green/yellow of the same cross-section of the generator power conductors and to the generator earth copper bar. | 1%
| B. Earth copper bar dimensions: 200x50x5mm fixed to generator metallic main frame by threaded rods. The copper bar should be drilled with 4 holes Æ6mm. | 1%
2.7 OIL DRAIN HOSE
| A. In absence of sump pump, the oil sump container should be provided with heavy duty ¼ ball valve terminated with stopper. | 1%
| B. A 1m drain hose with ½” adapter should be supplied with the engine in order to connect it to the ¼ ball valve to drain the oil from engine. | 1%
2.8 STARTER BATTERY
| A. Lead-acid, sealed-in-plastic type, complete with battery corrosion resistant mounting rack and inter-cell connectors. | 0.1%
| B. Minimum required battery capacity is 100AH, 12Vdc | 5%
2.9 ENGINE MUFFLER
| A. Constructed from heavy gauge sheet steel with all welded construction and coated with high heat-resistant black paint. | 0.1%
| B. Critical type, low back pressure exhaust muffler, Max 1.4 "Hg @ full load, sized as recommended by engine manufacturer | 0.1%
| C. Rated sound level reduction of 30-35 dBA or more in order to ensure 63±2dBA at 1m. | 2%
| D. Connections from Engine to Exhaust System: Flexible section of corrugated stainless-steel pipe. | 0.1%
2.10 WATER HEATER JACKET
| A. Should be engine mounted, external type, jacket water heater type, thermostatically controlled, 220V AC supply, single phase power. | 0.1%
| B. Heavy duty quarter valves should be provided on both ends in order to isolate the jacket water heater in case of defect. | 0.1%
| C. Power: 1000W – 240Vac | 4.5%
| D. Similar to Hotstart, Reference: TPS102GT 10-0000 | 0.1%
2.11 SOUNDPROOF CANOPY
| A. A weatherproof canopy to house the diesel generator that complies with a minimum IP 34 rating | 0.1%
B. Canopy Model NC55
| 1. Model NC55: Shall ensure a sound level of 63dBA ± 2dBA at 1m from source from all directions, at 100% load, according to noise criteria NC-55 as per table below: | 5%
1%
| C. Exhaust pipe and muffler inside the canopy shall be rock wool insulated and protected with a cover of 1x1cm wire mesh. | 0.1%
| D. Supports for Muffler: Spring hangers and all-thread rods and vibration hangers with approved expansion bolts | 0.1%
| E. Muffler exhaust pipe should be extended 20cm outside the canopy | 0.1%
| F. Radiator to canopy canvas should be minimum 5cm width and made of a cloth tissue and not of rubber joints. | 0.1%
G. Construction
| 1. Free standing enclosure constructed from carbon steel sheets lined with sound absorbent material designed to accommodate engine-alternator and control panel. | 0.1%
| 2. Fitted with 4 doors, two doors on each side | 0.1%
| 3. Service doors at each side, rotating on hinges, for inlet and outlet attenuators for easy service. | 0.1%
| 4. Hinges should be of heavy duty welded type | 0.1%
| 5. Unit body is made of Carbon Steel Cold Rolled Sheet Metal with structure beam where necessary. | 0.1%
| 6. Inlet and Outlet attenuators at the Engine and alternator ends provide ample air flow to ensure proper cooling with maximum 8 m/s air speed @ the total air flow quantity generated by the engine and alternator cooling fan. | 0.1%
| 7. Opening passages for oil drain, fuel pipes, breather, and cables are located according to the required position of installation. | 0.1%
| 8. Wall thickness: 10 cm | 0.1%
| 9. Thickness of outer skin: minimum 2mm to 3mm | 0.1%
| 10. Battery can only be reached via lockable access doors | 0.1%
| H. Internal flexible exhaust pipe | 0.1%
| I. Paint: All the material is treated with corrosion resistant and enhanced by a phosphate chemical conversion coating which provides an excellent corrosion resistant surface. The metal components are then painted by applying an epoxy polyester paint which is subjected to high temperatures and form a continuous, high gloss and extremely durable coating. Color code: RAL 7015 | 0.1%
| J. Locks: Provide welded heavy duty sliding latch, for each canopy door, lockable with padlock. Padlock hole diameter should be 10mm. | 0.1%
END OF SECTION
Total |  | 100% | [7 empty] | Total | 0 | 0 | 0 | 0 | 0 | 0
* For Requirements defined as ''Killer'', a ‘’Fully Compliant’’ score should be the sole acceptable outcome. Failing to obtain a ‘’Fully Compliant’’ score on the requirements defined as Killers, will mandate immediate disqualification for bidders.
Note on D8: Entity (Department/ Unit) that identified the requirement and that will be responsible for its evaluation.
Note on E8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on F8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on G8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on H8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on I8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on J8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements

## Combined Scoring
| RFT Scoring Sheet |  | Reference Number | SF-CF-87
|  |  | Owner | PRO/PMO
|  |  | Revision Code | 3.0 | 3.0
|  |  | Implementation Date | 2024-05-01 | 2024-05-01
Project Name | DEKWANEH WAREHOUSE - Generators
| Technical Score | 40%
| Commercial Score | 60%
| Combined Score | 100%