## TOTAL
DEKWANEH WAREHOUSE Civil & Electrical Works
BILL OF QUANTITIES - GRAND TOTAL
ITEM | DESCRIPTION | TOTAL (USD)
| Electrical | 0
| Solar | 0
| UPS | 0
| Lighting | 0
| Generator | 0
| Fire Fighting and Alarm | 0
| Air Conditioning | 0
| CCTV & Access Control | 0
| Outdoor Civil Works | 0
| External Offices + Logistics 2 Story Building | 0
| GRAND TOTAL | 0

## Electrical
BILL OF QUANTITIES - ELECTRICAL WORKS
ITEM | DESCRIPTION | UNIT | QTY | UNIT PRICE | TOTAL USD
SECTION 26 24 13 Low Voltage Switchboards - 17.12
MAIN DISTRIBUTION BOARDS
Surface mounted or free standing main distribution boards of hinged cover cabinet type complete with busbars, circuit breakers, switch disconnectors, spares, spaces, digital indicating and measuring devices, "PVC" trunking and wires, ground conductors, cable lugs and accessories. The contractor is responsible to verify the design, make the necessary calculations and shall be responsible for the performance of the system and its compliance with the specified standards. ATS & Main distribution boards shall be equipped with digital power meters Power meter similar to EasyLogic PM2230 Ref. METSEPM2230
Each main distribution panel board has to be provided with engraved metal nameplate mounted with corrosion resistant screws.
The electrical cables, inside the main distribution boards, have to be fixed on supports with metallic clamps.
All functional units have to be labeled and identified by using engraved metal nameplate mounted with corrosion resistant screws.
Cables glands shall be provided at the termination of all cables at the enclosures.
The electrical link between the functional units have to be done by rigid bus bars for 100 Amps and more.
The flexible insulated bus bars are allowed only between Main Bursars and circuit breakers where their respective frame is equal or lower than 100 Amps.
The incoming/outgoing cables are connected to functional units by insulated bus bars and suitable insulated connectors.
The direct connection between circuit breakers and outgoing cables is not allowed.
All 3-Ph circuit breakers are 4P4D; All switches are 4P; unless otherwise indicated on the drawings
Electric socket circuits shall be equipped with 30mA differential protection
All panels shall have a minimum of 20% spare space
| MDB @ Electrical Room | U | 1 |  | 0
| SDB OFFICES @ Offices | U | 1 |  | 0
| SDB STORE ROOMS @ GF 2 story building | U | 1 |  | 0
| SDB WH @ Large WH | U | 1 |  | 0
| SDB UPS @ Electrical Room | U | 1 |  | 0
| SDB Fire Pumps @ Fire Pumps | U | 1 |  | 0
| ATS GE1-GE/PT-GE-PV Rated 150A; @ Electrical Room | U | 1 |  | 0
| SURGE ARRESTOR; @ Electrical Room Shelter; 3P+N with box Complete Protection | U | 1 |  | 0
| SDB UPS OFFICES @ Electrical Room | U | 1 |  | 0
SECTION 26 05 19 Low-Voltage Electrical Power Conductors and Cables - 17.12
Supply, install and connect, Alu/PVC/PVC 600/1000 volts, including pull boxes, cable fixing cable cleats, cable glands, sealing compound, cable sleeves, marking and all necessary accessories as specified and shown on drawings
| Cable Alu/PVC/PVC 600/1000 volts, NYY | m | 550 |  | 0
4x150 mm² (PT Bldg to ATS)
Supply, install and connect, Cu/PVC/PVC 600/1000 volts, including pull boxes, cable fixing cable cleats, cable glands, sealing compound, cable sleeves, marking and all necessary accessories as specified and shown on drawings
Cable Cu/PVC/PVC 600/1000 volts, NYY
| 4x70 mm² (EDL to ATS) | m | 100 |  | 0
| 4x70 mm² (ATS to MDB) | m | 15 |  | 0
| 4x70 mm² (MDB to SDB Fire Pumps) | m | 200 |  | 0
| 4x35 mm² (Gen to ATS) | m | 30 |  | 0
| 4x35 mm² (Inverter to MDB) | m | 75 |  | 0
| 4x25 mm² (MDB to SDB Warehouse) | m | 120 |  | 0
| 4x10 mm² (MDB to SDB Store Rooms) | m | 15 |  | 0
| 4x10 mm² (MDB to SDB Offices) | m | 25 |  | 0
| 4x10 mm² (MDB to UPS) | m | 10 |  | 0
| 4x10 mm² (SDB WAREHOUSE to Forklift Charging PAnel) | m | 30 |  | 0
| 2x10 mm² (ATS to Gen) | m | 100
| 2x4 mm² (ATS to Gen) | m | 100
Earth Cables
Supply, install and terminate earth cables, NYA, including accessories as specified and to the satisfaction of the Engineer. Copper conductor, Single Core, Unarmoured, PVC insulated, Non Sheathed, 450 / 750 V Isolation, with Rigid Conductors - Green/Yellow
Supply, install and terminate earth cables, NYA, including accessories as specified and to the satisfaction of the Engineer. Copper conductor, Single Core, Unarmoured, PVC insulated, Non Sheathed, 450 / 750 V Isolation, with Rigid Conductors - Green/Yellow
| 1x70 mm² - Copper conductor, Single Core, Unarmoured, PVC insulated, Non Sheathed, 450 / 750 V Isolation, with Rigid Conductors - Green/Yellow | m | 30 |  | 0
| 1x35 mm² - Copper conductor, Single Core, Unarmoured, PVC insulated, Non Sheathed, 450 / 750 V Isolation, with Rigid Conductors - Green/Yellow | m | 215 |  | 0
| 1x25 mm² - Copper conductor, Single Core, Unarmoured, PVC insulated, Non Sheathed, 450 / 750 V Isolation, with Rigid Conductors - Green/Yellow | m | 105 |  | 0
| 1x16 mm² - Copper conductor, Single Core, Unarmoured, PVC insulated, Non Sheathed, 450 / 750 V Isolation, with Rigid Conductors - Green/Yellow | m | 120 |  | 0
| 1x10 mm² - Copper conductor, Single Core, Unarmoured, PVC insulated, Non Sheathed, 450 / 750 V Isolation, with Rigid Conductors - Green/Yellow | m | 80 |  | 0
Miscellaneous Cables
| 10 pair telephone cable, Liban cable LibtelS, 0.5mm² | m | 150 |  | 0
| Control cable 10x1.5 mm² | m | 150 |  | 0
Miscellaneous
| Alarm distribution frame 50 pairs KRONE original; disconnection module to be provided without earth with punching tool | U | 2 |  | 0
EARTH/GROUND
| 3 rods earth system | U | 3 |  | 0
| 1 rod earth system | U | 9 |  | 0
| Test clamp (disconnecting link) | U | 8 |  | 0
| Lightning rod FRANKLIN type 240cm | U | 3 |  | 0
| Elevation rod 2m | U | 3 |  | 0
| Copper tape 30x2mm | m | 184 |  | 0
0
| 3P+N Lightning surge arrestor class B & C with fuses and metallic enclosure | U | 1 |  | 0
SECTION 26 05 36 Cable Trays for Electrical Systems
Supply and install hot dip galvanized perforated steel cable trays with straight flange, complete with corners, return edge type, suspension system, fixing and all accessories including covers
| Cable tray 314mm wide x 48mm high | m | 100 |  | 0
| Ditto 198mm wide x 48mm high | m | 100 |  | 0
| Ditto 100mm wide x 48mm high | m | 100 |  | 0
| Ditto 50mm wide x 48mm high | m | 100 |  | 0
Total |  |  |  |  | 0

## Solar
BILL OF QUANTITIES - SOLAR
ITEM | DESCRIPTION | UNIT | QTY | UNIT PRICE | TOTAL USD
PV Module
Supply, install, connect, and operate with all material needed including supply, install & connect the following: cable trays, clamps, accessories, supports & labels suitable to be installed under the PV arrays.
| Solar Photovolataic module, Mono-chrystalline, half-cut, 540Wp, similar to Jinko Tiger Pro | U | 96 |  | 0
Grid-Tie Solar Inverter
Supply, install, connect, and operate DC/AC, Grid-Tie, 3-phase Solar Inverter with data communication unit with Ethernet connection. The inverter must be suited to any PV module configuration. The inverter unit shall be suitable for outdoor installations with IP65.
| Solar Inverter 36KW, 3-phase, sine wave, Grid-Tie | U | 1 |  | 0
Fuel Save Controller - (Refer to Specifications Secton 6)
Supply, install, connect, and operate with all material needed including supply, install & connect the following: cables, three (3) current transformer, accessories, & labels
| Fuel Save Controller, similar to DEIF AGC-150 | U | 1 |  | 0
Protections
| Surge Protection for PV Cables | LS | 1 |  | 0
Cables Cu/PVC/PVC 1.5/1.5 kV
| 1x6mm² (from PV panel to Inverter) | m | 672 |  | 0
Total |  |  |  |  | 0

## UPS
BILL OF QUANTITIES - SOLAR
ITEM | DESCRIPTION | UNIT | QTY | UNIT PRICE | TOTAL USD
UPS
| 20KVA, 3ph input, 3ph output, 0.9pf, 380V, 50hz, double line conversion, transformerless | U | 1 |  | 0
Batteries
| Battery Bank for two (2) hours backup time for 20KW load consisting of 12Vdc, 165AH C10 to 1.80Vdc @ 20°C VRLA batteries | U | 1 |  | 0
| WEB Ethernet SNMP card for remote supervision of UPS | U | 1 |  | 0
| Battery fuse box, 100A, for each string (at the batteries side) | U | 1 |  | 0
| Set of steel racks (Chassis) for batteries | U | 1 |  | 0
| Battery disconnect panels | U | 1 |  | 0
0
| Delivery, transportation, installation, & commissioning | U | 1 |  | 0
Total |  |  |  |  | 0

## Lighting
BILL OF QUANTITIES - LIGHTING
ITEM | DESCRIPTION | UNIT | QTY | UNIT PRICE | TOTAL USD
LIGHTING POINTS AND ELECTRIC OUTLETS
Including concealed and exposed conduits, wiring up to corresponding panelboard, cable outlet, fixing support, and necessary accessories and connections as specified and shown on drawings.
| Lighting point, ceiling mounted | U | 69 |  | 0
| Lighting point, wall mounted | U | 43 |  | 0
| Lighting point, high bay | U | 66 |  | 0
| Lighting point for outdoor flood lights | U | 18 |  | 0
| Outlet for motorized gate, 3x2.5mm2 | U | 3 |  | 0
| Outlet for water heater | U | 1 |  | 0
| Outlet for Air conditioning units 12000 BTU/Hr | U | 9 |  | 0
| Outlet for Air conditioning units 7.5KW precision type | U | 3 |  | 0
| Outlet for FACP | U | 5 |  | 0
| Outlet for CCTV | U | 1 |  | 0
| Outlet for access control system | U | 1 |  | 0
| Steel deep galvanized poles 9m high to support flood lights and CCTV cameras | U | 9 |  | 0
LIGHTING FIXTURES
Including necessary accessories for installation and connection, as specified and shown on drawings.
| 4x5W Decorative LED fixture with reflective louvers | U | 35 |  | 0
| 2x8W Decorative LED fixture with reflective louvers | U | 34 |  | 0
| 8W Wall mounted Emergency Light with battery kit (Legrand) | U | 24 |  | 0
| 8W Wall mounted Exit Sign with battery kit (Legrand) | U | 19 |  | 0
| High Bay, syspended luminaires, LED, 240W | U | 66 |  | 0
| Outdoor flood lights, LED, 250W | U | 18 |  | 0
WIRING DEVICES, DISCONNECTS
Including concealed and exposed conduits, boxes, wiring up to corresponding panelboard, cable outlet, fixing support, plate and necessary accessories and connections as specified and shown on drawings.
Switches
| 10A One way, one gang switch | U | 20 |  | 0
| 10A Two way, one gang switch | U | 4 |  | 0
| 10A Push button, one gang | U | 24 |  | 0
Socket outlets
| 16A/220V, 2P+T Socket outlet | U | 40 |  | 0
| 20A/220V, 2P+T Power Socket outlet | U | 15 |  | 0
| 16A/220V, 2P+T Socket outlet, UPS | U | 20 |  | 0
TELEPHONE AND DATA SYSTEMS
Including concealed and exposed conduits, boxes, wiring up to corresponding cabinet, wiring accessories with supports, mechanisms and cover plates, and necessary accessories and connections, as specified and shown on drawings.
| Patch panel - 19inch rack - 60 Ports | U | 2 |  | 0
| RJ45 Sockets (data and telephone) | U | 60 |  | 0
Total |  |  |  |  | 0

## Generator
BILL OF QUANTITIES - GENSET INSTALLATION
ITEM | DESCRIPTION | UNIT | QTY | UNIT PRICE | TOTAL USD
Power Generators
| Diesel generator, 100KVA prime | U | 1 |  | 0
| Sound proof canopy to 65 dBA @ 1m | U | 1 |  | 0
| Battery charger 10A | U | 1 |  | 0
| Termination on generation main breaker with all needed lugs and accessories | U | 1 |  | 0
| Anti-Vibration Pads - Similar to Sylomer® SR220 Length 250mm, Width 250mm, Thickness 75mm Set of 6 pieces | U | 1 |  | 0
| Steel plates galvanized 250mmx250mmx50mm to be installed between anti-vibration pad and canopy base; Set of 6 pieces | U | 1 |  | 0
| Installation of 60KVA generator on top of the rooftop of the two-stories building | LS | 1 |  | 0
Fuel System
| Fuel tank 2000L; 200x100x100cm with retention tray - Constructed of 3mm non galvanized metal sheets - Sprayed with furnace paint, color RAL 7015 - Retention tray extended 10cm from tank perimeter and edge height 10cm provided with a ½ inch drain ball valve. Tray should covered from rain. - Hose level indicator with ball valve - Refer to fuel pipes connections drawing | U | 2 |  | 0
| Fuel supply per 1000 liters | U | 1 |  | 0
| Diesel Fuel Filter and Water Separator DAHL 100, 40GPH | U | 1 |  | 0
| Set of 12 padlocks YALE with 1 master key | U | 1 |  | 0
Supply and installation of seemless black steel fuel pipes, painted dark grey color, complete with all required accessories:
| 3/4 inch | m | 20 |  | 0
| 3/4 inch ball valves | U | 10 |  | 0
| 2" black steel pipe for fuel refilling box | m | 2 |  | 0
| 2" elbow | U | 5 |  | 0
| 2" accessories and fittings | U | 5 |  | 0
| 2" quarter turn valve | U | 5 |  | 0
| Metallic refilling box fully equipped (q.t. valve, one way valve, accessories) | U | 1 |  | 0
| Concrete blocks for fixation of fuel pipes and cable trays; dimensions 10x10x20cm | U | 10 |  | 0
| Concrete slabs for 1*generators and 2 Fuel tanks; (thickness 10cm, 20MPa compressive strength) | m² | 7.5 |  | 0
Total |  |  |  |  | 0

## Fire
BILL OF QUANTITIES - FIRE PROTECTION
ITEM | DESCRIPTION | UNIT | QTY | UNIT PRICE | TOTAL USD
OFFICES & STORE ROOMS
| FM-200 System serving the Electrical Room (Total of 23Kg of FM-200) Void (FFL to ceiling) Area: 13.5m², height = 3m | Ea. | 1 |  | 0
| FM-200 System serving the Indoor Storage Room @ GF (Total of 247Kg of FM-200) Void (FFL to ceiling) Area: 146m², height = 3m | Ea. | 1 |  | 0
| FM-200 System serving the Indoor Storage Room @ 1st Floor (Total of 78Kg of FM-200) Void (FFL to ceiling) Area: 46m², height = 3m | Ea. | 1 |  | 0
| Mechanical installation of FM200 system including piping, nozzles, and all required accessories for complete system installation | Ea. | 1 |  | 0
| Fire detection system including: FACP Smoke detector Abort Push Button Horn Strobe - Indoor Strobe - Outdoor Luminous Evacuate Sign Pressure Switch Fire rated cables Warning signs | Ea. | 4 |  | 0
| CO2 Portable fire extinguisher (6kg) | Ea. | 20 |  | 0
| ABCE Dry Chemical Portable fire extinguisher (5kg) | Ea. | 10 |  | 0
WAREHOUSE
Detection System
| Fire Alarm Control Panel Addressable | U | 1 |  | 0
| Reflective Beam Detector | U | 10 |  | 0
| Break Glass, Indoor Manual Call Point Without LED - Red | U | 5 |  | 0
| Fire Bell | U | 4 |  | 0
Sprinkler System
| Standard Response, Pendant Sprinkler, 1/2", 68C, Bronze, K5.6, Reliable, UL/FM | LS | 275 |  | 0
| Black seamless Pipes of 5.80 M length | LS | 1 |  | 0
1" Ø25 mm 670m. Piece 116
1¼" Ø32 mm 128m. Piece 22
1½" Ø40 mm 92m. Piece 16
2" Ø50 mm 12m. Piece 3
2½" Ø65 mm 18m. Piece 4
3" Ø80 mm 48m. Piece 9
4" Ø100 mm 54m. Piece 10
6" Ø150 mm 42m. Piece 8
| Fittings and accessories | LS | 1 |  | 0
| Installation of sprinkler system | LS | 1 |  | 0
Fire Hose Cabinets
| Fire Hose Reel Cabinet, Surface Mounted, Horizontal, 1.2mm Full Mild Steel, Single Compartment, Solid Door, Red Powder Coated, Size 70 X 72 X 28 including Fire Hose Reel 1" x 30 Mtr. Cabinet Mounted, Manual with Plastic Nozzle, Kitemark LPCB Approved | U | 6 |  | 0
Fire Pump Set
| Diesel Pump achieving 350 GPM @ 7 Bars Type : Base mounted, Horizontal, End Suction. Motor : 30 KW, 50 Hz, water cooled 2900 RPM, Class F, IP 55. Construction : Cast iron casing and impeller, stainless steel shaft, mechanical seal. | U | 1 |  | 0
| Electrical Pump achieving 350 GPM @ 7 Bars Type : Base mounted, Horizontal, End Suction. Motor : 30 KW, 3 phase, 400 V, 50 Hz, 2900 RPM, Class F, IP 55. Construction : Cast iron casing and impeller, stainless steel shaft, mechanical seal. | U | 1 |  | 0
| Jockey Pump achieving 10 GPM @ 7 Bars Type : Multi-stage, Vertical, Inline. Motor : 0.55 KW, 3 phase, 400 V, 50 Hz, 2900 RPM, Class F, IP 55. Construction : Stainless Steel casing and impellers, stainless steel shaft, mechanical seal. | U | 1 |  | 0
| Common operating Control Panel with pump controllers and indicators. | U | 1 |  | 0
| Common base plate and accessories | LS | 1 |  | 0
| Testing and commissioning | LS | 1 |  | 0
| Fire Extinguisher Trolley 12KG Powder | U | 1 |  | 0
| Fire Extinguisher Trolley 50KG Powder | U | 2 |  | 0
Water Tank
| Water Tank 10m3 | U | 2 |  | 0
| Water tank accessories, valves, water level, etc | LS | 1 |  | 0
Total |  |  |  |  | 0

## Air-Con
BILL OF QUANTITIES - AIR-CON
ITEM | DESCRIPTION | UNIT | QTY | UNIT PRICE | TOTAL USD
| Air Conditioner, split, wall type, 12000 BTU A/C Unit, inverter type, 220Vac, 1Ph, with auto-restart including copper pipes (up to 10m) and drain pipes | U | 8 |  | 0
| Air Conditioner, Precision, air-Cooled, 7.5KW total sensible cooling, with humidifier and heater, stand alone, upflow including copper pipes and drain pipes | U | 3 |  | 0
Ducting:
Supply and Installation of GI Ducting according to SMACNA Rectangular indoor, according to specifications
| 500x500mm ducts | Lm | 45 |  | 0
Grills and Diffusers:
| 500x500mm rectangular Diffusers | U | 20 |  | 0
Total |  |  |  |  | 0

## CCTV & Access Control
BILL OF QUANTITIES - CCTV & ACCESS CONTROL
ITEM | DESCRIPTION | UNIT | QTY | UNIT PRICE | TOTAL USD
Refer to "security systems specifications"
Shall include supply, installation, testing, and commissioning. Shall include all required cables and accessories for completion system operation
INSIDE WAREHOUSE
| Indoor Camera | U | 25 |  | 0
| Access Control | U | 6 |  | 0
| Time Attendance | U | 1 |  | 0
INSIDE OFFICES & INDOOR STORAGE ROOMS
| Indoor Camera | U | 8 |  | 0
| Outdoor Camera | U | 1 |  | 0
| Access Control | U | 5 |  | 0
| Time Attendance | U | 1 |  | 0
OUTSIDE AREA
| Outdoor Cameras | U | 12 |  | 0
Total |  |  |  |  | 0

## Outdoor Civil Works
BILL OF QUANTITIES - OUTDOOR CIVIL WORKS
ITEM | WORK DESCRIPTION | UNIT | QTY | UNIT PRICE | TOTAL USD
INTERNAL AND EXTERNAL WORKS
PRELIMINARY WORK
1 | Topographic Survey Plot No. 1668 (~15,000m²) including marking of plot boundaries, warehouse boundaries, existing infrastructure and facilities, and levels. | LS | 1 |  | 0
EXCAVATION
2 | Excavate, compact and level, where needed | m² | 500 |  | 0
FENCE
3 | Masonry wall | m² | 212 |  | 0
4 | Columns 0.2*0.2*2.3m | Ea | 28 |  | 0
5 | Columns foundation 0.4*0.4*0.2m | Ea | 27 |  | 0
6 | Linear wall foundation 20x20cm | Lm | 88 |  | 0
7 | Excavation (10cm wider than foundations) | m³ | 20 |  | 0
8 | Barbed Wire + fence detail on top of walls | m | 97 |  | 0
0
Warehouse (Hangar) 70m*40m
9 | Design and execution. Including, but not limited to, everything mentioned in the technical document and drawings. | Ea | 1 |  | 0
Prefabricated Security Rooms
10 | 2.5x2.5x2.5m with door and 2 windows, including floor and structure, lighting, air-conditioner 9,000BTU, with 30cm high legs. | Ea | 2 |  | 0
11 | 2.5x3.5x2.5m with door and 2 ventilation windows and lighting for fire pumps fixed to the concrete slab | Ea | 1 |  | 0
Miscellaneous Civil Works
12 | Concrete slab for fire pumps room and water tank: 3x10x0.2 cm | Ea | 1 |  | 0
13 | Reinforced concrete trench top cover for the existing trench in the outdoor area (width varying between 45cm and 165cm), refer to drawing; thickness of 20cm | m2 | 40 |  | 0
14 | Reinforced concrete foundation for lighting poles (refer to drawings for detail) including excavation and all needed works | Ea | 9 |  | 0
15 | Tripod 4m 3"/4mm with offset pipe for transmission MW | Ea | 1 |  | 0
16 | Cable Tray 98x48mm perforated with return edge and cover | Lm | 20 |  | 0
17 | Electrical Duct Bank Supply all required materials, and construct duct bank with four (4) PVC ducts 4"Ø each, complete including all necessary excavation, ducts, concrete bed & surround using moderate sulphate resistant cement to ASTM C150, Type II, 30 MPa on cylinder (38 MPa on cube), formwork, reinforcement, accessories, PVC covered wire rope for ducting, warning tape, application of two coats of bituminous paint to concrete surfaces in contact with soil, backfilling, compaction, removal of surplus material to approved dumping areas, and all other related works, all as specified, to the satisfaction of the Engineer, and in full coordination with relevant local authorities. Check provided trench drawing detail. | Lm | 100 |  | 0
18 | Supply all required materials, and construct 100x100x100cm [WxDxH] manhole complete including, but not limited to all necessary excavation, concrete works using moderate sulphate resistant cement to ASTM C150, Type II, 14 MPa on Cylinder (18 MPa on Cube) for blinding and 30 MPa on Cylinder (38 MPa on Cube) for reinforced concrete works, all necessary formwork, reinforcement, accessories, application of two coats of bituminous paint to concrete surfaces in contact with soil, backfilling, compaction, removal of surplus materials to approved dumping areas, covers and frames, and all other related works, all as specified, to the satisfaction of the Engineer, and in full coordination with relevant local authorities. | Ea | 4 |  | 0
Total |  |  |  |  | 0

## External Offices + Logistics
BILL OF QUANTITIES - DOORS
ITEM | DESCRIPTION | UNIT | QTY | UNIT PRICE | TOTAL USD
EXTERNAL OFFICES AND LOGISTICS BUILDING
General description
| -The building will consist of 2 stories. Bottom ground floor story is reserved for logistics warehouse. Top story is reserved for offices, kitchen, 2 bathrooms and a small storage area. -Projected top view dimensions of the building will be 20m x 7.5m. -Building walls, internal and external, consist of 10cm thick sandwish panels. -Building will be installed on a concrete solid slab on grade acting as foundation. -The first story ceiling slab (or the 2nd story floor slab) consists of a metallic structure. It also should allow for floor tiling and all mechanical installations for the kitchen and the bathrooms, without any risk for spillage or flooding or draining into the 1st story. -The roof consists of a metallic structure that should support a layer of 10cm sandwish panel. -No columns are allowed inside of the building along the 7.5m width. Columns can only be within the edge walls. -Clear structural internal height shall be 3m in each story. More details are shown in the attached drawings. | U | 1 |  | 0
==> In addition to the above general architecture and structure figures, the room includes the below:
Foundation
| Concrete slab on grade of 21m x 9m x 0.25m size acting as a foundation for the building (designer to confirm that 25cm thickness is needed or if 20cm is enough) | m3 | 47.25 |  | 0
Bathrooms
| 2 bathrooms fully equipped of (1.45x2.85m²) each, containing each: 2 sinks and 1 toilet. | Ea. | 2 |  | 0
Kitchen
| A kitchen fully equipped including 1 big stainless steel sink surface (2.85m) with drawers and cupboards underneath | Ea. | 1 |  | 0
Windows
| Standard 2 sliding panels aluminum windows 120cm x 120cm | U | 6 |  | 0
| Standard hinged small window 60cm x 60cm | U | 2 |  | 0
Floor tiling and mechanical
| Ceramic tiles 60x60cm with mechanical installation beneath. Designer to present a full solution. Also consider the price of all mechanical installations and pipes in this item. | m2 | 71 |  | 0
Doors + Porches + Platform + Stairs
| Double leaf door, 60min fire rated, structural reveal (80+80)*2150cm. Main leaf fitted from the inside with emergency twist handle and from the outside with handle and cylinder. Secondary leaf equipped with carrier arm and a closing regulator with built-in impact damper. Opens to the outside. Main leaf opens to the left. Similar to Ninz REI 0217. ( + 1 Porch cover 2m x 1.5m on top of the main storage room door at the ground floor). | U | 1 |  | 0
| Single leaf door, 60min fire rated, structural reveal 1200*2150cm; The door is fitted from the inside with emergency twist handle and from the outside with handle and cylinder. Similar to Ninz. ( + 1 porch cover 1.5m x 1m for the main entrance of the second story.) | U | 4 |  | 0
| Single leaf wooden door 900x2150cm | U | 2 |  | 0
| Single leaf wooden door 700x2150cm | U | 4 |  | 0
| 2nd story main entrance platform 2m x 1.5m + 1m handrails all around | m2 | 3 |  | 0
| Mid-platform for metallic stairs 1.2m x 1.2m + 1m handrails all around | m2 | 1.44 |  | 0
| Metallic external stair leading to 2nd story; width=120cm, 5 steps/m, for roof top access - painted - Tubular 80x40 - Steps made of duck board with frame right angled 2.5x2.5cm - Handles on one both sides 40x40mm | lm | 5.8 |  | 0
Sceptic Tank
| Sceptic tank 7.5m x 2.5m x 2.9m external dimensions. All walls and slabs, internal and external, are 20cm thick reinforced concrete 30MPa, reinforced by 2 layers of rebars T10@150mm in both directions. Tank is divided into 3 chambers seperated by 20cm thick walls perforated by 2 connection openings (40x40cm). Include plumbing connections from building till sceptic tank. Consider 3 access traps (40x40cm) and their metallic covers. Refer to drawings. | U | 1 |  | 0
Water tanks and pump
| PVC water tank, triple layer, 2000L to supply water to the WCs and Kitchen. (similar to NTG RTH3) | U | 2 |  | 0
| Water pump with pressure head, 0.5HP | U | 1 |  | 0
Total |  |  |  |  | 0