## TOTAL
JDEIDET MOT - CORE SITE Diesel Generators
BILL OF QUANTITIES - GRAND TOTAL
ITEM | DESCRIPTION | TOTAL (USD)
A | Diesel Generators 350KVA | 0
B | Retrofit of Existing Diesel Generator 350KVA | 0
| GRAND TOTAL | 0

## Diesel Genset
BILL OF QUANTITIES - DIESEL GENERATOR
ITEM | DESCRIPTION | QTY | UNIT | UNIT PRICE | TOTAL US$
26 32 13.13.DG12 - Diesel-Engine-Driven Generator Sets - 350KVA-LA
1 | Supply and installation of 350KVA diesel powered, factory assembled, generator including the following:
* Synchro control panel Seep Sea Electronics DSE 8610 or equivalent
* Protection & remote start board
| * Permanent magnet generator (PMG) * 630A rated circuit breaker, 4P, 4D, with electronic trip unit (Schneider NSX630N, with Micrologic 5.3E or equivalent) * Electronic governor * AVR/AREP * Starter Battery * Earth bar * Genset neutral connection to earth bar * Battery charger 10A, 24VDC * Engine coolant heater (1000W) * Fuel high pressure hydraulic hoses * Manual sump pump * Residential exhaust muffler, 63±2dBA at 1m * Delivery to site, FoT, within GBA | Ea. |  | 1 | 0
2 | Supply and installation of sound proof canopy for 350KVA genset based on NC-55. | Ea. |  | 1 | 0
3 | Termination, testing, synchro programming, and commissioning of the generator set. | Ea. |  | 1 | 0
Total |  |  |  |  | 0

## Retrofit
BILL OF QUANTITIES - RETROFIT
ITEM | DESCRIPTION | QTY | UNIT | UNIT PRICE | TOTAL US$
Retrofit of the Existing Generator 350KVA
1 | Replacement of the stand alone control panel of the existing generator with synchro panel Deep Sea Electronics or equivalent including all necessary accessories for the proper installation and operation. | Ea. |  | 1 | 0
2 | Supply and installation of all control cables between the two generators and ATS for the proper operation of the synchro including all required accessories. | Ea. |  | 1 | 0
3 | Termination, testing, synchro programming, and commissioning of the generator set. | Ea. |  | 1 | 0
Total |  |  |  |  | 0