## TOTAL
JDEIDEH MOT - CORE SITE Civil Works
BILL OF QUANTITIES - GRAND TOTAL
ITEM | DESCRIPTION | TOTAL (USD)
1 | CW Data Center & Generator | 0
2 | CW Battery Room | 0
3 | TOWER Civil Works | 0
| GRAND TOTAL | 0

## CW Data Center & GE
BILL OF QUANTITIES - CIVIL WORKS DATA CENTER
ITEM | DESCRIPTION | UNIT | QTY | UNIT PRICE | TOTAL USD
Wall constructed of HCB, thickness : 15 cm
1 | Closing of openings in data center room 3rd floor | m² | 15 |  | 0
PAINTING
For internal walls and ceiling: -Smoothing the plaster surface by special stone -Painting a primary layer: TINOCRYL EM Tinted Primer 21300 -Treatment of the small ruts by local plaster -Painting 2 layers of TINOCRYL EM AntiCarbonation 11600 White (or equivalent product to be submited for approval) For floor (epoxy): -Painting a primary layer: TINOPOXY Tinted Primer 3840 + Hardener 8 + 50% diluted TINOSOLVE 1007 -Painting 2 layers of TINOPOXY Floor coating 13040 + Hardener 8 + 25% diluted TINOSOLVE 1007
2 | data center room walls and ceiling | m² | 590 |  | 0
MISCELLANEOUS
3 | Shelter supply for housing the electrical panels (ATS & MDB) * W3.5 x L4.5 x H3 m * Floor load: 750kg/m² * Door hook * Stairs 2 steps * Ladder * Cable opening for generator cables * Cable opening for EDL cables * Cable opening for outgoing cables Refer to attached specifications | U | 1 |  | 0
4 | Steel platform with grate surface W120 x L400 cm inside electrical room shelter. Shall be 45cm above FFL | U | 1
5 | Remove and dispose of all rubish inside data center area | Lot | 1 |  | 0
6 | Crane (hoisting) 160 Tons / 63m (hoisting the shelter, generators, fuel tank, and electrical distribution cabinets) | Ea. | 2 |  | 0
7 | Remove tiles in data center room | m² | 280 |  | 0
8 | Grinding the surface for perfect levelling and wash areas to remove any remaining particles - Data Center room | m² | 280 |  | 0
9 | Apply a layer of epoxy primer once the concrete is dry then apply 2 layers of epoxy paint on Data center floor (as per paint specs mentioned above) | m² | 280 |  | 0
10 | Concrete wall H40 x 15W x L650 cm to protect fuel tanks | U | 1 |  | 0
11 | Foldable and extractable iron ladder 2.5m high | U | 2 |  | 0
12 | Concrete beam 20x30 cm | Lm | 16 |  | 0
13 | Relocation of the existing 2 Nos. Outdoor AC units | U | 1 |  | 0
14 | Relocation of the existing uninstalled and unused 250KVA generator with canopy. | U | 1 |  | 0
15 | Hoisting of 350KVA generator at Jeita warehouse & Jdeideh MoT | U | 2
16 | Transportation of 350KVA generator from Jeita warehouse to Jdeideh MOT | U | 1
Total |  |  |  |  | 0

## UPS & DC Systems Room
BILL OF QUANTITIES - CIVIL WORKS UPS & DC SYSTEMS ROOM
ITEM | DESCRIPTION | UNIT | QTY | UNIT PRICE | TOTAL USD
ROOM STRUCTURE
1 | Mat Foundation excavation | m3 | 44.4 |  | 0
2 | Compaction of soil under mat foundation to 95% compaction on the standard Proctor | m2 | 45.5 |  | 0
REINFORCED CONCRETE
Concrete compressive strength 30MPa, cement type II
Steel yield strength 420MPa (Grade 60)
3 | Mat Foundation reinforced concrete | m3 | 18.2 |  | 0
4 | Room columns reinforced concrete
4.1 | Columns from mat foundation 20x50cm | m | 13.6 |  | 0
4.2 | Columns from ground floor slab 20x50cm | m | 26.4 |  | 0
5 | Room slabs reinforced concrete
5.1a | Ground floor slab 25cm | m2 | 45.5 |  | 0
5.1b | Ground floor slab on slab 10cm | m2 | 15.2 |  | 0
5.2 | Roof slab 20cm | m2 | 67.9 |  | 0
6 | Backfill original soil on top of mat foundation to level at the same road level | m3 | 33.3 |  | 0
ROOM ARCHETECTURE AND FINISHING
8 | Masonry walls (labor and material)
8.1 | Masonry walls ground floor thickness 20cm | m2 | 130.35 |  | 0
8.2 | Masonry parapet on roof thickness 10cm | m2 | 33.92 |  | 0
9 | Cement rendering (labor and material)
External cement rendering thickness 20 to 25mm
Internal cement rendering thickness 10 to 15mm
Materials ratio: 5:1:1 ratio of sand, cement, and lime
Initial scratch coat is required of a ratio of 4:1:1
9.1 | Cement rendering internal ground floor story | m2 | 182.51 |  | 0
9.2 | Cement rendering external ground floor story | m2 | 82.99 |  | 0
9.3 | Cement rendering parapet roof both sides and top | m2 | 47.5 |  | 0
10 | Paint (labor and material)
For internal walls and ceiling: -Painting a primary layer: TINOCRYL EM Tinted Primer 21300 -Treatment of the small ruts by local plaster -Painting 2 layers of TINOCRYL EM AntiCarbonation 11600 White (or equivalent product to be submited for approval) For external walls, slabs and parapets: -Painting a primary layer: TINOLAC Tinted primer 21000 -Painting 2 layers of TINOFLEX Ecoating 6100 (or equivalent product to be submited for approval) For floor (epoxy): -Painting a primary layer: TINOPOXY Tinted Primer 3840 + Hardener 8 + 50% diluted TINOSOLVE 1007 -Painting 2 layers of TINOPOXY Floor coating 13040 + Hardener 8 + 25% diluted TINOSOLVE 1007
10.1 | Paint all internal walls and ceiling | m2 | 182.51 |  | 0
10.2 | Paint 3 exposed external walls | m2 | 82.99 |  | 0
10.3 | Paint parapet roof both sides and top | m2 | 47.5 |  | 0
10 | Apply a layer of epoxy primer once the concrete is dry then apply 2 layers of epoxy paint on ground floor (as per paint specs mentioned above) | m2 | 52.8 |  | 0
MISCELLANEOUS
11 | Supply-apply solvent base bituminous primer and one layer APP bituminous membrane, “Mapethene Mineral TA” or “Viscogum” 4.5kg/m2, 180g/m2 polyester reinforced, Slate finish, on new roof and parapets. | m2 | 110 |  | 0
12 | Existing metallic stairs modification and painting to allow for 2 stairs (one from existing terrace to new room roof and one from that roof till existing building roof) | m | 10 |  | 0
13 | Relocation of existing 2 drain ducts along 18m | LS | 1 |  | 0
14 | Cleanup the area before excavation, cut 5 small trees, removal of some debris and concrete parts | LS | 1 |  | 0
15 | Modification of existing fan duct to allow for the construction of the room | LS | 1 |  | 0
16 | Removal and reinstallation of multiple facades panels to allow for cable trays and chimneys passage | m2 | 50 |  | 0
Total |  |  |  |  | 0

## Tower CW
BILL OF QUANTITIES - TOWER CIVIL WORKS
ITEM | DESCRIPTION | UNIT | QTY | UNIT PRICE | TOTAL USD | Notes
Site Preparation and Protection at Rooftop
1 | Cleaning and removal of rubbish with transportation of all MoT removed and cleaned assets to the ground floor | LS | 1 |  | 0
2 | Protective netting, protective gear to all workers and harness as per method statement and drawings | LS | 1 |  | 0
3 | Removal of all damaged concrete, and rusted steel from walls at height manually or by small hand held mechanical equipments, steel brushing, clean up and preparation of surfaces | m² | 20 |  | 0
4 | Protection of existing equipment and material during project execution | LS | 1 |  | 0
5 | Wall repairs and cavity filling as needed to restore original dimensions and surfaces with non shrink grout where instructed by engineer (Sika®Grout 100G or similar product) | m² | 20 |  | 0
6 | Liquid waterproofing on all exposed concrete walls surfaces ( base bituminous primer PU + 2 coats of liquid membrane ) | m² | 60 |  | 0
7 | Crane (hoisting) 300 Tons / (63m+70m) in Greater Beirut | LS | 3 |  | 0 | 1 crane for removing existing tower and 1 for the beams beams. 1 crane for the new tower
8 | Handrail 1m high at rooftop level | m | 15 |  | 0
9 | Metallic ladder, width=60cm, for rooftop access | m | 3 |  | 0
10 | Reperation and reinforcement of circular metallic stair inside the concrete tower | LS | 1 |  | 0
0
| Tower Installation at Rooftop |  |  |  | 0
0
11 | Tower installation, including all related civil works as per detailed drawings, concrete of 30MPa compressive strength, Steel yield strength 420MPa (Grade 60), including, but not limited to, the following:
11.1 | Rebar anchors + Drilling + Hilti (Around 51 T16 rebars anchored 60cm, and around 95 T14 rebars anchored 40cm and 10 T14 anchored 20cm) | cm | 7060 |  | 0
11.2 | Steel beams supports for formwork (TREC150x100x3.2mm; weight 12.2kg/m) | m | 40 |  | 0
11.3 | Formwork (approximated at only 1m high around the concrete tower circumference, and below the new slab) | m2 | 26 |  | 0
11.4 | Polystyrene between steel beams (around 20cm thick) | m2 | 15 |  | 0
11.5 | Reinforced concrete (new slab + wall + rebars) | m3 | 9 |  | 0
11.6 | Counter-plates for tower legs | Ea. | 3 |  | 0
11.7 | Custom made flanges/adapters for tower legs | Ea. | 3 |  | 0
11.8 | Tower legs bolts embedded in slab (M24 L=50cm) | Ea. | 24 |  | 0
11.9 | Tower assembly and erection | LS | 1 |  | 0
11.1 | Tower painting, labor and material | LS | 1 |  | 0
11.11 | Cable tray coring opening | LS | 1 |  | 0
Total |  |  |  |  | 0