## TOTAL
JDEIDET MOT - CORE SITE Electrical, Doors, Generators Installation, & Telco Works
BILL OF QUANTITIES - GRAND TOTAL
ITEM | DESCRIPTION | TOTAL (USD)
1 | Electrical | 0
2 | Doors | 0
3 | Generator Installation | 0
4 | Telco | 0
| GRAND TOTAL | 0

## Electrical
BILL OF QUANTITIES - ELECTRICAL WORKS
ITEM | DESCRIPTION | UNIT | QTY | UNIT PRICE | TOTAL USD
SECTION 26 24 13 - Low Voltage Switchboards
MAIN DISTRIBUTION BOARDS
Surface mounted or free standing main distribution boards of hinged cover cabinet type complete with busbars, circuit breakers, switch disconnectors, spares, spaces, digital indicating and measuring devices, "PVC" trunking and wires, ground conductors, cable lugs and accessories. The contractor is responsible to verify the design, make the necessary calculations and shall be responsible for the performance of the system and its compliance with the specified standards.
Each electrical distribution board (main, sub-main, and secondary) shall be equipped with a digital power meter with RS-485 communication interface
Each main distribution panel board has to be provided with engraved metal nameplate mounted with corrosion resistant screws.
The electrical cables, inside the main distribution boards, have to be fixed on supports with metallic clamps.
All functional units have to be labeled and identified by using engraved metal nameplate mounted with corrosion resistant screws.
Cables glands shall be provided at the termination of all cables at the enclosures.
The electrical link between the functional units have to be done by rigid bus bars for 600 Amps and more (cables are not allowed).
The flexible insulated bus bars are allowed only between Main Bursars and circuit breakers where their respective frame is equal or lower than free standingmps.
The incoming/outgoing cables are connected to functional units by insulated bus bars and suitable insulated connectors.
The direct connection between circuit breakers and outgoing cables is not allowed.
All 3-Ph circuit breakers are 4P4D; All switches are 4P; unless otherwise indicated on the drawings
Electric socket circuits shall be equipped with 30mA differential protection
All panels shall have a minimum of 20% spare space
All free standing panels, shall be assembled as per Form 2B in accordance with IEC 61439 standard
1 | EDL PANEL, 600A @ Electrical Room; free standing cabinet: * 1 No. switch disconnector, 600A, 4P, 415VAC; Schneider INS630 or equivalent * 2 Nos. MCCB, 600A, 4P4D, 50KA, 415VAC, Electronic trip unit; Schneider NSX630N or equivalent | U | 1 |  | 0
2 | SURGE ARRESTOR; @ Electrical Room; 3P+N Lightning surge arrestor class B with blade type fuses and metallic enclosure | U | 1 |  | 0
3 | ATS/MTS EDL-GE-A, rated for 600A; @ Electrical Room, free standing cabinets: * 2 Nos. Contactors 600A, 4P (4NO), 415VAC; with mechanical and electrical interlock; Schneider TeSys F, LC1F or equivalent * 2 Nos. Manual transfer switch, 600A, 4+8P; Socomec Sircover I-0-II or equivalent * 4 Nos. switch disconnector, 600A, 4P, 415VAC; Schneider INS630 or equivalent * ATS Control (to be provided by MIC1) | U | 1 |  | 0
4 | ATS/MTS EDL-GE-B, rated for 600A; @ Electrical Room, free standing cabinets: * 2 Nos. Contactors 600A, 4P (4NO), 415VAC; with mechanical and electrical interlock; Schneider TeSys F, LC1F or equivalent * 2 Nos. Manual transfer switch, 600A, 4+8P; Socomec Sircover I-0-II or equivalent * 4 Nos. switch disconnector, 600A, 4P, 415VAC; Schneider INS630 or equivalent * ATS Control (to be provided by MIC1) | U | 1 |  | 0
5 | SYNCRO PANEL GE-A, rated for 600A; @ Electrical Room, free standing cabinet: * 3 Nos. Switch disconnector, 600A, 4P; Schneider INS630 or equivalent * 2 Nos. Contactors 600A, 4P (4NO), 415VAC; Schneider TeSys F, LC1F or equivalent | U | 1 |  | 0
6 | SYNCRO PANEL GE-B, rated for 600A; @ Electrical Room, free standing cabinet: * 3 Nos. Switch disconnector, 600A, 4P; Schneider INS630 or equivalent * 2 Nos. Contactors 600A, 4P (4NO), 415VAC; Schneider TeSys F, LC1F or equivalent | U | 1 |  | 0
7 | MDB-A @ Electrical Room Shelter, free standing cabinet: * Main Switch: 4P, 600A, 415VAC; Schneider INS630 or equivalent * 3 Nos. MCCB, 4P4D, 250A, 415VAC, Electronic Trip Unit * 1 No. MCCB, 4P4D, 160A, 415VAC, Electronic Trip Unit * 4 Nos. MCCB, 4P4D, 100A, 415VAC, Electronic Trip Unit | U | 1 |  | 0
8 | MDB-B @ Electrical Room Shelter, free standing cabinet: * Main Swtich: 4P, 600A, 415VAC; Schneider INS630 or equivalent * 3 Nos. MCCB, 4P4D, 250A, 415VAC, Electronic Trip Unit * 1 No. MCCB, 4P4D, 160A, 415VAC, Electronic Trip Unit * 4 Nos. MCCB, 4P4D, 100A, 415VAC, Electronic Trip Unit | U | 1 |  | 0
9 | MDB CRAC - A @ Data Center, free standing cabinet: * Main Switch: 4P, 250A, 415VAC; Schneider INS250 or equivalent * 8 Nos. MCCB, 4P4D, 100A, 415VAC, Electronic Trip Unit; Schneider NSX100F or equivalent | U | 1 |  | 0
10 | MDB CRAC - B @ Data Center, free standing cabinet: * Main Switch: 4P, 250A, 415VAC; Schneider INS250 or equivalent * 8 Nos. MCCB, 4P4D, 100A, 415VAC, Electronic Trip Unit; Schneider NSX100F or equivalent | U | 1 |  | 0
11 | MDB UPS-IN-A @ UPS & DC Systems Room, free standing cabinet: * Main Switch: 4P, 250A, 415VAC; Schneider INS250 or equivalent * 2 Nos. MCCB, 4P4D, 250A,415VAC, Electronic Trip Unit; Schneider NSX250F or equivalent | U | 1 |  | 0
12 | MDB UPS-IN-B @ UPS & DC Systems Room, free standing cabinet: * Main Switch: 4P, 250A, 415VAC; Schneider INS250 or equivalent * 2 Nos. MCCB, 4P4D, 250A, 415VAC, Electronic Trip Unit; Schneider NSX250F or equivalent | U | 1 |  | 0
13 | MDB UPS-OUT-A @ UPS & DC Systems Room, free standing cabinet: * Main Switch: 4P, 250A, 415VAC; Schneider INS250 or equivalent * 2 Nos. MCCB, 4P4D, 250A, 415VAC, Electronic Trip Unit; Schneider NSX160F or equivalent | U | 1 |  | 0
14 | MDB UPS-OUT-B @ UPS & DC Systems Room, free standing cabinet: * Main Switch: 4P, 250A, 415VAC; Schneider INS250 or equivalent * 2 Nos. MCCB, 4P4D, 250A, 415VAC, Electronic Trip Unit; Schneider NSX160F or equivalent | U | 1 |  | 0
15 | MDB-UTILITY-UPS-IN @ UPS & DC Systems Room, free standing cabinet: * Main Switch: 4P, 250A, 415VAC; Schneider INS250 or equivalent * 2 Nos. MCCB, 4P4D, 250A,415VAC, Electronic Trip Unit; Schneider NSX250F or equivalent | U | 1 |  | 0
16 | MDB-UTILITY-UPS-OUT @ UPS & DC Systems Room, free standing cabinet: * Main Switch: 4P, 250A, 415VAC; Schneider INS250 or equivalent * 1 Nos. MCCB, 4P4D, 250A, 415VAC, Electronic Trip Unit; Schneider NSX250F or equivalent * 7 No. MCCB, 4P4D, 63A, 415VAC, Electronic Trip Unit; Schneider NSX100F or equivalent | U | 1 |  | 0
17 | MDB RECTIFIERS - A @ UPS & DC Systems Room, free standing cabinet: * Main Switch: 4P, 250A, 415VAC; Schneider INS250 or equivalent * 2 Nos. MCCB, 4P4D, 160A, 415VAC, Electronic Trip Unit; Schneider NSX100F or equivalent | U | 1 |  | 0
18 | MDB RECTIFIERS - B @ UPS & DC Systems Room, free standing cabinet: * Main Switch: 4P, 250A, 415VAC; Schneider INS250 or equivalent * 2 Nos. MCCB, 4P4D, 160A, 415VAC, Electronic Trip Unit; Schneider NSX100F or equivalent | U | 1 |  | 0
19 | SDB Utility @ Electrical Room: * Main Switch 32A, 4P, with differential protection 300mA * 2 Nos. MCB, 16A, 4P4D * 3 Nos. MCB, 16A, 2P1D, with differential protection 30mA * 2 Nos. MCB, 10A, 2P1D * 3 Nos. MCB, 6A, 2P1D | U | 1 |  | 0
20 | SDB Utility @ Data Center: * Main Switch 40A, 4P, with differential protection 300mA * 2 Nos. MCB, 16A, 4P4D * 7 Nos. MCB, 16A, 2P1D, with differential protection 30mA * 10 Nos. MCB, 10A, 2P1D * 6 Nos. MCB, 6A, 2P1D | U | 1 |  | 0
21 | SDB Utility @ UPS & DC Systems Room: * Main Switch 63A, 4P, with differential protection 300mA * 4 Nos. MCB, 16A, 4P4D * 5 Nos. MCB, 16A, 2P1D, with differential protection 30mA * 4 Nos. MCB, 16A, 2P1D * 5 Nos. MCB, 10A, 2P1D * 5 Nos. MCB, 6A, 2P1D | U | 1 |  | 0
22 | SDB-UPS UTILITY @ UPS & DC Systems Room: * Main Switch 32A, 4P, with differential protection 300mA * 2 Nos. MCB, 16A, 2P1D, with differential protection * 5 Nos. MCB, 10A, 2P1D * 5 Nos. MCB, 6A, 2P1D | U | 1 |  | 0
23 | SDB-UPS UTILITY @ Data Center Room: * Main Switch 32A, 4P, with differential protection 300mA * 2 Nos. MCB, 16A, 2P1D, with differential protection * 7 Nos. MCB, 10A, 2P1D * 7 Nos. MCB, 6A, 2P1D | U | 1 |  | 0
24 | SDB-UPS UTILITY @ Electrical Room: * Main Switch 32A, 4P, with differential protection 300mA * 2 Nos. MCB, 16A, 2P1D, with differential protection * 5 Nos. MCB, 10A, 2P1D * 5 Nos. MCB, 6A, 2P1D | U | 1 |  | 0
25 | SMDB-UPS-A free standing cabinet: * Main Switch 250A, 4P, 415V, Schneider INS250 or equivalent * 4 Nos. MCCB, 4P4D, 100A, 415VAC, Electronic Trip Unit; Schneider NSX100F or equivalent | U | 1 |  | 0
26 | SMDB-UPS-B free standing cabinet: * Main Switch 160A, 4P, 415V, Schneider INS250 or equivalent * 4 Nos. MCCB, 4P4D, 100A, 415VAC, Electronic Trip Unit; Schneider NSX100F or equivalent | U | 1 |  | 0
27 | SDB-UPS-A-1 - Free standing cabinet: * Main Switch 100A, 4P, 415V, Schneider INS100 or equivalent * 60 Nos. 32A, MCB, 2P1D, * 18 Nos. 32A, MCB, 4P4D | U | 1 |  | 0
28 | SDB-UPS-A-2 - Free standing cabinet: * Main Switch 100A, 4P, 415V, Schneider INS100 or equivalent * 60 Nos. 32A, MCB, 2P1D, * 18 Nos. 32A, MCB, 4P4D | U | 1 |  | 0
29 | SDB-UPS-B-1 - Free standing cabinet: * Main Switch 100A, 4P, 415V, Schneider INS100 or equivalent * 60 Nos. 32A, MCB, 2P1D, * 18 Nos. 32A, MCB, 4P4D | U | 1 |  | 0
30 | SDB-UPS-B-2 - Free standing cabinet: * Main Switch 100A, 4P, 415V, Schneider INS100 or equivalent * 60 Nos. 32A, MCB, 2P1D, * 18 Nos. 32A, MCB, 4P4D | U | 1 |  | 0
SECTION 26 05 19 - Low-Voltage Electrical Power Conductors and Cables
Supply, install and connect, Cu/PVC/PVC 600/1000 volts, including pull boxes, cable fixing cable cleats, cable glands, sealing compound, cable sleeves, marking and all necessary accessories as specified and shown on drawings. Insulation resistance testing shall be done by installer following installation of all power cables. Test shall be witnessed by MIC1 engineer
Cable Cu/PVC/PVC 600/1000 volts, NYY
31 | 4x185 mm² (EDL Meter to EDL Panel) - 2 runs of 120m each | m | 240 |  | 0
32 | 4x185 mm² (EDL Panel to ATS/MTS EDL/GE-A) - 2 runs of 10m each | m | 20 |  | 0
33 | 4x185 mm² (EDL Panel to ATS/MTS EDL/GE-B) - 2 runs of 10m each | m | 20 |  | 0
34 | 4x185 mm² (GE-A to SYNCRO GE-A) - 2 runs of 35m each | m | 70 |  | 0
35 | 4x185 mm² (GE-B to SYNCRO GE-B) - 2 runs of 38m each | m | 76 |  | 0
36 | 4x185 mm² (SYNCRO GE-A to SYNCRO GE-B) - 2 runs of 10m each | m | 20 |  | 0
37 | 4x185 mm² (ATS/MTS EDL-GE-A to MDB-A) - 2 runs of 10m each | m | 20 |  | 0
38 | 4x185 mm² (ATS/MTS EDL-GE-B to MDB-B) - 2 runs of 10m each | m | 20 |  | 0
39 | 4x95 mm² (MDB-A @ Electrical Room to MDB-UPS-IN-A @ DC & UPS Systems Room @ GF) - 1 run of 45m | m | 45 |  | 0
40 | 4x95 mm² (MDB-B @ Electrical Room to MDB-UPS-IN-B @ DC & UPS Systems Room @ GF) - 1 run of 45m | m | 45 |  | 0
41 | 4x95 mm² (MDB-A @ Electrical Room to MDB CRAC - A) - 1 run of 90m | m | 100 |  | 0
42 | 4x95 mm² (MDB-B @ Electrical Room to MDB-UTILITY UPS-IN) - 1 run of 100m | m | 45 |  | 0
43 | 4x95 mm² (MDB-UPS-IN-A to 120KVA UPS-A) - 2 runs of 15m each (Primary & Bypass) | m | 30 |  | 0
44 | 4x95 mm² (MDB-UPS-IN-B to 120KVA UPS-B) - 2 runs of 15m each (Primary & Bypass) | m | 30 |  | 0
45 | 4x95 mm² (UPS-A to MDB-UPS-OUT-A) - 1 run of 15m | m | 15 |  | 0
46 | 4x95 mm² (UPS-B to MDB-UPS-OUT-B) - 1 run of 15m | m | 15 |  | 0
47 | 4x95 mm² (MDB-UPS-OUT-A to SMDB-UPS-A) - 1 run of 75m | m | 75 |  | 0
48 | 4x95 mm² (MDB-UPS-OUT-B to SMDB-UPS-B) - 1 run of 75m | m | 75 |  | 0
49 | 4x95 mm² (MDB-UTILITY-UPS-IN to UTILITY UPS) - 2 runs of 15m | m | 30 |  | 0
50 | 4x95 mm² (UTILITY UPS to MDB-UTILITY-UPS-OUT) - 1 run of 15m | m | 15 |  | 0
51 | 4x95 mm² (MDB-UTILITY-UPS-OUT to MDB-CRAC-B) - 1 run of 75m | m | 75 |  | 0
52 | 4x95 mm² (MDB-A@ Electrical Room to MDB-RECTIFIERS-A) - 1 run of 45m | m | 45 |  | 0
53 | 4x95 mm² (MDB-B@ Electrical Room to MDB-RECTIFIERS-B) - 1 run of 45m | m | 45 |  | 0
54 | 4X50 mm² (SMDB-UPS-A to SDB-UPS-A-1) - 1 run of 10m | m | 10 |  | 0
55 | 4X50 mm² (SMDB-UPS-A to SDB-UPS-A-2) - 1 run of 10m | m | 10 |  | 0
56 | 4X50 mm² (SMDB-UPS-B to SDB-UPS-B-1) - 1 run of 10m | m | 10 |  | 0
57 | 4X50 mm² (SMDB-UPS-B to SDB-UPS-B-2) - 1 run of 10m | m | 10 |  | 0
58 | 4X50 mm² (MDB-RECTIFIERS-A to RECTIFIER-A) - 2 runs of 15m each - 1 run for each power cabinet | m | 30 |  | 0
59 | 4X50 mm² (MDB-RECTIFIERS-B to RECTIFIER-B) - 2 runs of 15m each - 1 run for each power cabinet | m | 30 |  | 0
60 | 4X16 mm² (MDB-A to SDB-UTILITY @ Data Center 3rd Floor) - 1 run of 100m | m | 100 |  | 0
61 | 4X16 mm² (MDB AC to A/C 1 to 6) - 12 runs of 25m | m | 300 |  | 0
62 | 4x16 mm² (MDB-A to SDB-UTILITY @UPS & DC System room - 1 run of 45m | m | 45 |  | 0
63 | 4x6 mm² (MDB-A to SDB UTILITY @ Electrical Room) - 1 run of 10m | m | 10 |  | 0
64 | 4X6 mm² (SDB-UTILITY @ UPS & DC Systems Room to A/C Units) - 3 runs of 20m each | m | 60 |  | 0
65 | 4X6 mm² (MDB-UTILITY-UPS-OUT to SDB UPS UTILITY @ Electrical Room) - 1 run of 100m | m | 45 |  | 0
66 | 4X6 mm² (MDB-UTILITY-UPS-OUT to SDB UPS UTILITY @ UPS & DC Systems Room) - 1 run of 50m | m | 20 |  | 0
67 | 4X6 mm² (MDB-UTILITY-UPS-OUT to SDB UPS UTILITY @ Data Center) - 1 run of 75m | m | 75 |  | 0
68 | 3X6 mm² (SDB UTILITY @ Electrical Room to AC Units) - 2 runs of 15m each | m | 30 |  | 0
69 | 3x6 mm² (SDB-UPS-A-1&2 / SDB-UPS-B-1&2to 40 racks) | m | 1600 |  | 0
70 | 1x240 mm² * Rectifiers to Batteries - 32 runs of 12m each * Rectifiers to distribution panels - 32 runs of 80m each | m | 2944 |  | 0
71 | Cable Cu/PVC 600/1000V NYAF
72 | 1x240 mm² NYAF (UPS System to UPS DC Panels) - 8 runs of 20m each | m | 160 |  | 0
73 | 1x240 mm² NYAF (UTILITY UPS System to UPS DC Panel) - 4 runs of 20m each | m | 80 |  | 0
74 | 1x50 mm² NYAF (UPS DC panels to string fuses including jumper cables) - 1 run for each battery string (20 battery strings for 2 UPS units) | m | 350 |  | 0
75 | 1x50 mm² NYAF (UTILITY UPS DC panels to string fuses including jumper cables) - 1 run for each battery string (6 battery strings for 2 UPS units) | m | 105 |  | 0
76 | 2x10 mm² NYAF from DPD to 19 Racks | m | 1710 |  | 0
Earth Cables
Supply, install and terminate earth cables, NYA, including accessories as specified and to the satisfaction of the Engineer. Copper conductor, Single Core, Unarmoured, PVC insulated, Non Sheathed, 450 / 750 V Isolation, with Rigid Conductors - Green/Yellow
Supply, install and terminate earth cables, NYA, including accessories as specified and to the satisfaction of the Engineer. Copper conductor, Single Core, Unarmoured, PVC insulated, Non Sheathed, 450 / 750 V Isolation, with Rigid Conductors - Green/Yellow
77 | 1x185 mm² - Copper conductor, Single Core, Unarmoured, PVC insulated, Non Sheathed, 450 / 750 V Isolation, with Rigid Conductors - Green/Yellow | m | 123 |  | 0
78 | 1x50 mm² - Copper conductor, Single Core, Unarmoured, PVC insulated, Non Sheathed, 450 / 750 V Isolation, with Rigid Conductors - Green/Yellow | m | 550 |  | 0
79 | 1x35 mm² - Copper conductor, Single Core, Unarmoured, PVC insulated, Non Sheathed, 450 / 750 V Isolation, with Rigid Conductors - Green/Yellow | m | 90 |  | 0
80 | 1x25 mm² - Copper conductor, Single Core, Unarmoured, PVC insulated, Non Sheathed, 450 / 750 V Isolation, with Rigid Conductors - Green/Yellow | m | 100 |  | 0
81 | 1x16 mm² - (for ground bars in data center) Copper conductor, Single Core, Unarmoured, PVC insulated, Non Sheathed, 450 / 750 V Isolation, with Rigid Conductors - Green/Yellow | m | 75 |  | 0
82 | 1x10 mm² - Copper conductor, Single Core, Unarmoured, PVC insulated, Non Sheathed, 450 / 750 V Isolation, with Rigid Conductors - Green/Yellow | m | 295 |  | 0
83 | 1x6 mm² - Copper conductor, Single Core, Unarmoured, PVC insulated, Non Sheathed, 450 / 750 V Isolation, with Rigid Conductors - Green/Yellow | m | 210 |  | 0
84 | 1x6 mm² (Racks earthing) - Copper conductor, Single Core, Unarmoured, PVC insulated, Non Sheathed, 450 / 750 V Isolation, with Rigid Conductors - Green/Yellow | m | 175 |  | 0
85 | 30x2mm copper tape on room circumference for UPS and DC Systems Room | m | 40 |  | 0
Miscellaneous Cables
86 | Control Cables: Copper, Multi-Core, Unarmored, PVC insulated, PVC Sheathed, 0.6 / 1 KV Isolation 24 x 1.5 mm² (from Electrical Room @GF to Data Center at 3rd Floor) - 2 runs of 100m each | m | 200 |  | 0
87 | 20 pair telephone cable, 0,5mm² (UPS &DC systems room to data center) - 1 run of 60m | m | 60 |  | 0
88 | Data cable STP Cat6 (shielded) with cable installation and termination with RJ45 connector (alarms & precision A/C) | m | 100 |  | 0
89 | Data cable STP Cat6 (shielded) with cable installation and termination with RJ45 connector (UPS and DC systems) | m | 450 |  | 0
90 | Data cable STP Cat6 (shielded) with cable installation and termination with RJ45 connector (CCTV & Access Control) | m | 260 |  | 0
91 | 6 pair telephone cable, 0,5mm² | m | 100 |  | 0
92 | 2 pair telephone cable, 0.5mm² | m | 200 |  | 0
93 | RS-485, twisted pair cable, shielded | m | 300 |  | 0
Miscellaneous Equipment
94 | Main earth Bar (MEB) for racks static earth network & at each room | U | 12 |  | 0
95 | Environmental monitoring system, with remote monitoring and control through ethernet port, with data logging for a period of 1 month minimum: * 22 temperature sensors * 4 Humidity sensors * 15 water sensors | U | 1 |  | 0
96 | Alarm distribution frame 20 pairs for 1.5mm² wire; spring type connectors (Electrical Room) | U | 1 |  | 0
97 | Alarm distribution frame 20 pairs for 1.5mm²; spring type connectors (Data Center) | U | 1 |  | 0
98 | Alarm distribution frame 50 pairs KRONE original or equivalent (UPS and DC Systems Room) | U | 1 |  | 0
99 | Alarm distribution frame 200 pairs KRONE original or equivalent (Data Center) | U | 1 |  | 0
ELECTRICAL PANEL POWER MONITORING
100 | Supply and install a monitoring system for complete power monitoring for the power distribution panels. Shall include the following: | U | 1 |  | 0
* All electrical panels included in the Synoptic Diagram E01 should be monitored
* Data storage shall be for 1 year
* User interface through HTTP or product software
* Hardware shall be housed in a metallic box with key lock; similar to HIMEL
* All cables and accessories for complete installation
* Installation, testing & comissioning
LIGHTING POINTS.
101 | Lighting points including "PVC" outlet boxes and all medium gauge "PVC" rigid conduits, flexible medium gauge conduits, cables, wires, "PVC" junction and pull boxes, all accessories from feeding distribution boards, ground continuity conductors from ground terminal in SDB's to all lighting points. The installation shall be surface mounted. | U | 120 |  | 0
LIGHTING FIXTURES
Supply, install and connect lighting fixtures complete with lamps, ballast, wiring and all necessary accessories for fixing the fixtures as specified and shown on drawings. All lighting fixtures to be compensated for power factor >0.9.
102 | Surface mounted fixture, 4x18W cool white 4000K lamps, LED, V-aluminum diffuser, 220Vac | U | 96 |  | 0
103 | Non-maintained self containing emergency fixture, surface mounted. IP43. The lamp shall be, LED, 360 lumens and the battery autonomy 1 hour | U | 12 |  | 0
104 | LED lighting fixture for emergency lighting; surface mounted; Similar to Philips MASTER LEDtube GA 1200mm 22W | U | 12 |  | 0
105 | Projector, IP65 rated, 200W, wall mounted | U | 5 |  | 0
WIRING DEVICES.
Supply, install and connect wiring devices including cover plate, supports, boxes, medium conduits, wires and all necessary fixing accessories as specified and shown on drawings to the full satisfaction of the Engineer (All sockets to be French standard). The installation shall be surface mounted.
All rigid and flexible conduits to be with threaded conduit coupling between themselves and pull / junction PVC boxes.
106 | 6A, push button, double pole, 1 module, 250Vac, including the impulse relay inside electrical distribution panel; push button similar to Legrand | U | 10 |  | 0
107 | One-way one gang lighting switch, Similar to Legrand | U | 10 |  | 0
108 | wall mounted single socket outlets10/16A, 250Vac | U | 12 |  | 0
109 | RJ45 duplex outlet in wall mounted PVC box | U | 6 |  | 0
EARTH/GROUND
110 | Goose Foot earth system | U | 1 |  | 0
SECTION 26 05 36 - Cable Trays for Electrical Systems
Supply and install hot dip galvanized perforated steel cable trays with straight flange, complete with corners, return edge type, suspension system, fixing and all accessories
111 | Cable tray 506mm wide x 48mm high (80m above racks[power+data] + 40m A/C + 30m GE + 30m in shaft ) | m | 216 |  | 0
112 | Ditto 400mm wide x 48mm high | m | 70 |  | 0
113 | Ditto 314mm wide x 48mm high | m | 160 |  | 0
114 | Ditto 198mm wide x 48mm high | m | 70 |  | 0
115 | Ditto 500mm wide x 75mm high (UPS and DC Systems Room to Data Center - DC & AC Cables) | m | 120 |  | 0
116 | Ditto 500mm wide x 75mm high (Inside UPS and DC Systems Room) | m | 65 |  | 0
117 | Ditto 450mm wide x 75mm high (Gen to shelter and inside shelter) | m | 30 |  | 0
118 | Ditto 450mm wide x 75mm high (shelter to ups and dc systems room) | m | 30 |  | 0
119 | Ditto 314mm wide x 75mm high (Inside UPS & DC Systems Room) | m | 20 |  | 0
120 | Ditto 314mm wide x 75mm high (shelter to data center) | m | 80 |  | 0
121 | Ditto 198mm wide x 75mm high (EDL cables to Shelter) | m | 100 |  | 0
122 | Ditto 198mm wide x 75mm high (GE Cables to Shelter) | m | 35 |  | 0
123 | Ditto 198mm wide x 75mm high (ups and dc systems room to data center) | m | 75 |  | 0
124 | Ditto 198mm wide x 75mm high (shelter to ups and dc systems room) | m | 30 |  | 0
125 | Ditto 314mm wide x 75mm high (Data Center to Transmission shelter on rooftop) | m | 50 |  | 0
126 | Cable Ladder, 420mm (4 runs of 25m each) | m | 100 |  | 0
Total |  |  |  |  | 0

## Doors
BILL OF QUANTITIES - DOORS
ITEM | DESCRIPTION | UNIT | QTY | UNIT PRICE | TOTAL USD
SECTION 08 11 13.00.FD01 Hollow Metal Doors and Frames
FIRE RATED DOORS
Galvanized steel-sheet reversible door leaf with insulating-material core, total thickness 50 mm.
Corner reversible frame not assembled, with or without bottom frame, made of galvanized steel-sheet profile, with brackets to be set into wall and preparation for fixing with expansion screws.
Lock in main leaf with cylinder bore and plastic keyhole for patent key, included.
Secondary leaf with internal upper and lower closing rod with central manual control and prepared to receive the anti-panic kit.
Safety bolt in hinge-side leaf edge.
Black safety handle with steel core, supplied with plates, cylinder bore and keyholes for patent keys.
2 hinges/leaf, one per leaf with spring for the self-closing and one per leaf ball-bearing with screws for the vertical adjustment.
Strengthening plates inside door leaf for fastening door closer and emergency handle if required.
Thermoexpanding gasket inserted in appropriate cavity in frame. Identification plate on door edge. Painted with epoxy-polyester oven-baked powder paint with antiscratch goffered finish - light pastel turquoise for door leaf (NCS4020-B50G), and a darker shade for the frame (NCS5020-B50G).
1 | Double leaf door, 60min fire rated, structural reveal (80+80)*2150cm. Main leaf fitted from the inside with emergency twist handle and from the outside with handle and cylinder. Secondary leaf equipped with carrier arm and a closing regulator with built-in impact damper. Opens to the outside. Main leaf opens to the left. Similar to Ninz REI 0217. * Data center * Data center delivery room * UPS and DC Systems Room * Electrical Room | U | 4 |  | 0
2 | Single leaf door, 60min fire rated, structural reveal 1200*2150cm; The door is fitted from the inside with emergency twist handle and from the outside with handle and cylinder. Similar to Ninz. * Electrical Room | U | 1 |  | 0
Total |  |  |  |  | 0

## Generator Installation
BILL OF QUANTITIES - GENSET INSTALLATION
ITEM | DESCRIPTION | UNIT | QTY | UNIT PRICE | TOTAL USD
Power Generators
1 | Installation of 350KVA generator | U | 2 |  | 0
2 | Battery charger 10A | U | 2 |  | 0
3 | Termination on generator main breaker with all needed lugs and accessories | U | 2 |  | 0
4 | Anti-Vibration Pads - Similar to Sylomer® SR220 Length 250mm, Width 250mm, Thickness 75mm Set of 6 pieces | U | 2 |  | 0
5 | Steel plates galvanized 250mmx250mmx50mm to be installed between anti-vibration pad and canopy base; Set of 6 pieces | U | 2 |  | 0
Fuel System
6 | Fuel tank 2000L; 200x100x100cm with retention tray - Constructed of 3mm non galvanized metal sheets - Sprayed with furnace paint, color RAL 7015 - Retention tray extended 10cm from tank perimeter and edge height 10cm provided with a ½ inch drain ball valve. Tray should covered from rain. - Hose level indicator with ball valve - Refer to fuel pipes connections drawing | U | 5 |  | 0
7 | Fuel supply per 1000 liters | U | 5 |  | 0
8 | Diesel Fuel Filter and Water Separator DAHL 100, 40GPH | U | 2 |  | 0
9 | Set of 12 padlocks YALE with 1 master key | U | 2 |  | 0
10 | Level Pressure sensor | U | 1 |  | 0
11 | Digital indicator with 2 relays and special selector switch; Shall include RS-485 connection | U | 1 |  | 0
Supply and installation of seemless black steel fuel pipes, painted dark grey color, complete with all required accessories:
12 | 3/4 inch | m | 60 |  | 0
13 | 3/4 inch ball valves | U | 18 |  | 0
14 | 2" black steel pipe for fuel tanks interconnection | m | 5 |  | 0
15 | 2" elbow/T-Connection/Fittings | U | 10 |  | 0
16 | 2" quarter turn valve | U | 5 |  | 0
17 | Concrete blocks for fixation of fuel pipes and cable trays; dimensions 10x10x20cm | U | 20 |  | 0
18 | Chimney Supply and Installation for MIC1 Generators Supply and installation of 8" exhaust pipe, including insulation and jacketing, 5 cm Rockwool insulation, stainless steel jacketing including elbows, supports, drain zone, venturi, flexible pipes, and all necessary accessories * MIC1 Generator A + Generator B | m | 60 |  | 0
19 | Chimney Supply and Installation for MoT Generators Supply and installation of 8" exhaust pipe, including insulation and jacketing, 5 cm Rockwool insulation, stainless steel jacketing including elbows, supports, drain zone, venturi, flexible pipes, and all necessary accessories * 2Nos. MoT Generators | m | 60 |  | 0
20 | Concrete slabs for 2*generators and 4 Fuel tanks; (thickness 10cm, 20MPa compressive strength) | m² | 60 |  | 0
21 | Fence for fuel tanks, 2.5m high | Lm | 7.5 |  | 0
| Steel wall cover above concrete wall of fence, 1m high | Lm | 7.5 |  | 0
22 | Gate for fence, H 2m x W1.6m, double leaf | U | 1 |  | 0
| Metallic canopy above fence, L7 x W2.2 m | U | 1 |  | 0
| Lattice tower 4.5m high 50x50cm, including concrete base | U | 1 |  | 0
| Lattice tower 4.5m high 100x50cm, including concrete base | U | 1 |  | 0
| Lattice bridge, 50cm wide | Lm | 15 |  | 0
Total |  |  |  |  | 0

## Telco
BILL OF QUANTITIES - TELCO WORKS
ITEM | DESCRIPTION | UNIT | QTY | UNIT PRICE | TOTAL USD
| Fiber Optic Works |  |  |  | 0
1 | 6-pair fiber optic cables, armored, single mode with capacity of 100Gbps per pair - 4 runs | Lm | 300 |  | 0
2 | 6-pair fiber optic cables, armored, multi-mode with capacity of 10Gbps per pair - 4 runs | Lm | 300 |  | 0
3 | Patch panel in the transmission shelter having 24 single mode ports and 24 multi-mode ports | U | 2 |  | 0
0
| SECTION 27 11 16 Communications Cabinets, Racks, Frames, and Enclosures |  |  |  | 0
4 | racks 42U, W60*D110 cm, as per specs | U | 50 |  | 0
5 | racks 42U, W80*D110 cm, as per specs | U | 12 |  | 0
0
| Section 27 11 26 Communications Rack Mounted Power Protection and Power Strips |  |  |  | 0
6 | Power distribution Unit (PDU): * vertical installation * 32A, 1Ph, 230VAC * Minimum 20Nos. C13 plugs * Minimum 4 Nos. C19 plugs * Equipped with power meter with interactive LCD display * Support RS-485 and Ethernet |  | 80 |  | 0
7 | Power distribution Unit (PDU): * vertical installation * 32A, 3Ph, 415VAC * Minimum 36Nos. C13 plugs * Minimum 6 Nos. C19 plugs * Equipped with power meter with interactive LCD display * Support RS-485 and Ethernet |  | 6 |  | 0
0
Total |  |  |  |  | 0