## General Requirements
| RFT Compliance Matrix |  |  |  | Reference Number | SF-CF-25
[5 empty] | Owner | PRO
[5 empty] | Revision Code | 3.0
[5 empty] | Implementation Date | 2024-03-01
Project Name:
Reference Number:
RFT Article (Part Number or Title) | Requirements (Description) | Killer | Fully Compliant | Partially Compliant | Non-Compliant | Reference (Specify document & page nb)
Article 4 | Conditions for the Participation of the Eligible Bidders
4.1 | 1- Bidders shall meet the following conditions, declared in accordance with the required documents in the First section of this Article mentioned below as (First: Envelope No. (1) Administrative Documents and Transactions):
a- That there is no proven violation, by the bidders, of professional ethics generally accepted and stipulated in the relevant provisions, if any;
b- Bidders have the legal capacity to enter into the procurement contract;
c- Bidders have fulfilled their obligations to pay taxes and social security contributions;
d- Bidders have not been convicted, neither their directors nor employees involved with the procurement process, by a court decision of any criminal offence - even if the verdict can still be appealed - related to their professional conduct or the making of false statements or misrepresentations as to their qualifications to enter into a procurement contract, or corrupting a public procurement or a contract awarding process, or have not been otherwise disqualified pursuant to administrative suspension or debarment proceedings, or have been in a situation of exclusion from participation in public procurements;
e- Bidders are not the subject of legal proceedings for insolvency or bankruptcy, or were declared bankrupt by a court of law;
f- Bidders have not been convicted by a court decision - even if the verdict can still be appealed - of usury or money laundering;
g- Bidders have not participated in the decision-making process of the contracting authority or have any conflict of interest, or any material interest linking them to any of the decision makers;
h- Any other conditions set forth by the contracting authority in the tender documents that are commensurate with the required works;
i- Certificate from the Ministry of Economy proving compliance with the provisions of the Law on Boycott of Israel for foreign companies (added by Law No. 309, dated April 19, 2023).
j- Declaration of the economic beneficiaries (according to Law No. 309, dated April 19, 2023).
4.2 | 2- The bid must be submitted clearly and unequivocally without any deletion, alteration, or modification.
4.3 | 3- The bidders state in their offer that they have reviewed the Tender document and its complementary documents and have obtained a copy. They accept and undertake to adhere to all the conditions outlined therein without any reservations or exceptions. The bidder submits their offer on this basis and affixes financial stamps worth fifty thousand Lebanese pounds covering all the documents.
4.4 | 4- Any bid containing reservations or exceptions is rejected.
4.5 | 5- The bidder mentions in their offer a clear address and place of residence for prompt communication.
Administrative Documents and Transactions | First: Envelope No. (1) Administrative Documents and Transactions
A- General Conditions:
1- Undertaking Letter (Declaration), according to the attached form, signed and stamped by the bidder, this Undertaking includes the bidder's confirmation of their commitment to the price and the validity of the offer. A financial stamp of 50,000 L.L. is affixed.
2- Commercial Circular specifying the authorized signatory of the bidder and a sample of their signature.
3- Legal Authorization: If the offer is signed by someone other than the person authorized to sign according to the commercial circular, it must be notarized by a notary public.
4- Police Record of the Authorized Signatory or his “legal representative”, not exceeding three months from the bid opening date.
5- Partnership Contract legalized by a notary public if required.
6- Registration Certificate before the Directorate of Value Added Tax, if applicable, or a certificate of non-registration if not subject to it. In the latter case, the bidder commits to their bid price even if they become registered for VAT during the execution period.
7- Registration Certificate issued by the Ministry of Finance – Department of Revenue.
8- Certificate issued by the Ministry of Finance proving the bidder's compliance with tax obligations.
9- Clearance Certificate from the National Social Security Fund “comprehensive or valid for participation in public tenders and bids” valid on the date of the bid opening session, stating that the bidder has paid all his subscriptions (the bidder must be registered before the National Social Security Fund and any statement mentioning the phrase “unregistered institution” will be rejected).
10- Certificate issued by the Municipality, proving full payment of municipal fees by the bidder, issued by the municipality within its jurisdiction based on the commercial registration certificate.
11- Comprehensive Certificate issued by the Commercial Register showing founders, members, contributors, or partners, authorized signatories, the manager, capital, the bidder's activity, and ongoing liabilities.
12- Certificate issued by the relevant authorities proving that the bidder is not in a state of bankruptcy.
13- Certificate issued by the relevant authorities proving that the bidder is not in a state of judicial liquidation.
14- Bid bond as required in the specific Tender document of the procurement project, in accordance with Articles 34 and 36 of the Public Procurement Law.
15- Declaration from the Bidder identifying the economic beneficiary/beneficiaries according to Form M18 issued by the Ministry of Finance (any natural person who owns or effectively controls the ultimate outcome of the activity practiced by the bidder, either directly or indirectly, whether the bidder is a natural person or a legal entity.)
16- Copies of Identification Cards (ID/Passport) for the economic beneficiary/beneficiaries.
17- Copies of Identification Cards (ID/Passport) for each person representing the bidder (those acting on behalf of the bidder in their relationship with the contracting authority: legal representative, representative of the legal entity, or authorized signatory).
18- Integrity Declaration Document signed by the bidder in accordance with the prescribed format
Miscellaneous | The bidder shall declare any relative relations with any Alfa employee up to the 4th degree under Clause 30 of the PPL, for MIC1 to be able to assess the existing of any potential conflict of interests which may lead to deprive the bidder from participating to the tender under the risk of disqualification.
The bidder or any of his employees, partners, agents, contributors, consultants, or their relatives shall declare any relationships that may lead to a conflict of interest in the subject of this contract.
Special Conditions | B- Special Conditions Regarding the Subject of the Contract:
Financial Qualifications | 1- Financial Qualifications (To be determined based on the size and nature of the contract).
Technical/Professional Qualifications | 2- Technical/Professional Qualifications (To be determined based on the nature of the contract):
1- Certificate from the Chamber of Commerce, Industry, and Agriculture confirming that the bidder is engaged in the activities related to the subject of the contract, valid as of the date of the bidding session and valid for participation in public tenders.
2- Clearance certificate from the Order of Engineers…
3- Clearance certificate from the Contractors Syndicate…
4- ISO certificate.
5- Five Certificates of good execution and completion for similar projects in terms of size and type.
6- Technical proposal according to the required specifications in the appendix (1) of the RFT.
7- Declaration of site inspection by the bidder, denying any unfamiliarity, according to the attached model.
Participation of a foreign bidder | C- In case of the participation of a foreign bidder, the bidder must comply with one of the following conditions:
1- is part of a coalition that includes at least one Lebanese company that meets the conditions required by the specific Tender document of the procurement project.
2- The personal presence of the legal representative of the company to participate in the procurement proceedings (not mandatory).
3- Has an authorized agent or representative in Lebanon responsible for signing the contract on its behalf.
In addition to the above conditions, the foreign bidder must submit the following:
1- Certificate registration of the company or certificate of establishment issued by the relevant authorities in their country.
2- Certificate from the Lebanese Ministry of Economy and Trade confirming compliance with the provisions of the Law on Israel Boycott.
3- The required certificates according to paragraph (First) above, according to the laws of the country where the bidder is located, provided that these certificates are authenticated according to the regulations of the competent authorities.
For certificates issued without an expiration date, the validity date of each certificate is determined according to its nature, not exceeding six months from the date of the bid opening session.
Information Security Specifications | Information Security Specifications Issuing Department to determine whether all or part of this Article is applicable to their specific RFT
The Bidder shall commit to refrain from offering any product / equipment which can cause security threat or information leakage that jeopardizes MIC1 network security. (K)
The Bidder shall accept that MIC1 runs a vulnerability scan on the proposed solution prior to issuing the acceptance and in case any vulnerability is found, the Bidder undertakes to take the necessary actions to remedy such vulnerability within _____________________ days from its notification.
The Bidder shall mention the security standards adopted/followed in designing the proposed solution.
The Bidder should specify if it has acquired the ISO27001 certification or any other equivalent security certification and submit with the Offer a copy of such certificate.
The Bidder shall not hard code passwords in the proposed solution.
The provided application should run without the need of root (unix) and / or admin (win) privileges.
Source code of proposed application should be owned by MIC1.
System shall allow generation of user, operator as well as alarms logs.
Solution and storage shall be sized to host history logs for at least 1 year back.
The Bidder should submit a data flow diagram and schema of the solution architecture.
In case of online payment, the Bidder shall use encryption. (K)
The Bidder shall harden systems servers / storage before being published online, and describe hardening aspects applied on each type.
The Bidder shall describe security checking and audits performed on the designed solution prior to putting it on the market.
The Bidder shall change default errors / messages and configuration.
Application should support role-based access, specific privileges per user (i.e specific access to application modules and reports)
Database should support restricted access per user or groups to data (i.e access per field or per table, …)
Encryption shall be used in all communications / interactions between systems, especially if the communication is through web access. Web based access shall always be used through HTTP+SSL.
Each user shall have only one account / profile to access data.
Least-privileges should always be specified on nodes / applications.
Pseudocode flow chart shall be provided by the Bidders.
The Bidder should commit to improve solution / systems information security weaknesses whenever needed or highlighted by MIC1 information security team.
Health, Safety and Environmental Specifications | To ensure that the proposed products and services bidders are compliant with HSE culture, bidders should state basic HSE specifications and compliance information:
Bidder shall provide the product’s specifications that have an environmental impact (power consumption, gas emissions, etc…)
Bidder shall provide the product specifications that contribute into preserving the environment (made of recycled material, ozone friendly, low volatile organic compounds, etc…)
Bidder shall provide the product’s specifications that contribute towards the health and safety of the users (ergonomic design, safety features, etc)
Bidder shall state the safety measures being followed by personnel performing the work on Alfa’s sites (ISO45001 certification, specific best practices, etc…).
Bidder shall provide the product’s life cycle data if available.

## Technical Requirements
| RFT Compliance Matrix |  |  |  | Reference Number | SF-CF-25
[5 empty] | Owner | PRO
[5 empty] | Revision Code | 3.0
[5 empty] | Implementation Date | 2024-03-01
Project Name: | JDEIDET DATA CENTER
Reference Number: | 26 05 19 - Low-Voltage Electrical Power Conductors and Cables - 10.2023
RFT Article (Part Number or Title) | Requirements (Description) | Killer | Fully Compliant | Partially Compliant | Non-Compliant | Reference (Specify document & page nb)
1 GENERAL
1.1 SUMMARY
A. Section includes Low-Voltage Electrical Power Conductors and Cables.
1.2 REFERENCES
A. Standards
1. IEC 60228:2004 – Conductors of insulated cables
2. IEC 60502-1:2004+AMD1:2009 – Power cables with extruded insulation and their accessories for rated voltages from 1 kV (Um = 1,2 kV) up to 30 kV(Um = 36 kV) - Part 1: Cables for rated voltagesof 1 kV (Um = 1,2 kV) and 3 kV (Um = 3,6 kV)
1.3 SUBMITTALS
A. Product Data: Manufacturer's product literature, specifications and installation instructions.
1.4 WARRANTY
A. Equipment
1. The supplied products shall be covered by full supplier warranty for a minimum period of one (1) year from delivery to site at a full repair and replacement service.
2. Warranty shall include all defected spare parts and workmanship.
B. Services
1. Installation and dismantling
a. The supplier is responsible for the dismantling, hoisting, transportation and re-installation for parts that cannot be repaired or replaced on site
2. Part replacement/repair
a. For any part replacement or repair service the warranty for the repaired or new part shall be a minimum of 6 (six) months from the date of receipt of the repaired or new part. In case a part was repaired twice already under this warranty and the equipment becomes faulty again within up to six months the Operator on its discretion may request replacement of the complete equipment
3. Major defect
a. In case of major defect in the supplied products, the Operator reserves the right to reject the equipment. The supplier shall replace the defected system/parts under no cost from the Operator, including dismantling, hoisting, transportation and re-installation
2 PRODUCTS
2.1 MANUFACTURERS
A. Manufactured in a company certified according to DIN ISO 9001/ EN 29001
2.2 GENERAL PROPERTIES
A. Color code:
1. Phase R à Red, Phase S à Yellow, Phase T à Blue,
2. Neutral à Black
3. Protective Earth (PE) à Green/Yellow
4. Minimum cable cross-section for each circuit breaker is listed below: (refer to table in specs)
5. Protective earth conductors should be installed separately along power cables.
2.3 METHOD OF INSTALLATION
A. Distance between cables: >D (cable diameter)
B. Minimum bending radius: 6D (cable diameter)
C. Cables should be laid in metallic cable trays or in flexible metallic conduits of appropriate dimension as per site work description.
D. Cable should be fixed with PVC cable ties, of width 9mm, every 50cm, similar to Legrand.
E. High rise cables should be tied to steel tension wires, of 6mm minimum diameter, every 50cm, and fixed to clamps or poles.
2.4 MULTI-CORE, UNARMORED, PVC INSULATED, PVC INSULATED, AND PVC SHEATH CABLES
A. Scope: This specification covers single, two, three or four core cables, PVC insulated and PVC sheathed, rated at 0.6/1 KV, unarmored type to International Electrotechnical Commission Publication IEC 60502-1 for use in cable ducts and indoors and for underground burial, where they are not likely to suffer mechanical damage.
B. Construction
1. Conductor: Plain, annealed electrolytic copper conductors, solid, circular stranded or sectorial stranded; conforming to the applicable requirements of IEC 228.
2. Insulation: PVC based thermoplastic material, conforming to the applicable requirements of IEC 60502-1.
3. Assembly: Insulated conductors are laid up, filled where necessary with non-hygroscopic material and covered with an additional layer of extruded thermoplastic material or non-hygroscopic binding tape.
a. Sheath: PVC based thermoplastic material, conforming to the applicable requirements of IEC 60502-1.
b. Tests: Conforming to the applicable requirements of IEC 60502-1 either on raw materials or on finished products.
c. Similar to Liban Cable
2.5 SINGLE-CORE, NON SHEATHED, PVC INSULATED CABLES WITH FLEXIBLE CONDUCTORES
A. Scope: This specification covers single core,PVC insulated cables, intended for internal wiring in dry locations,concealed in conduits, type 227 IEC 05 For rigid conductors and type 227 IEC 06 for flexible conductors ( 0.5mm 2 to 1mm 2 cross-sectional area) rated 300/500 V; or intended for general purposes, wiring applications in buildings where high dielectric resistance to chemical products, heat grease and acid is required, type 227 IEC 01 for rigid conductors and type 227 IEC 02 for flexible conductors having cross-sectional area above 1.0 mm 2 ,rated 450/750 V to International Electrotechnical Commission Publication IEC 227.
B. Construction
1. Conductor: Plain, annealed, electrolytic copper conductors, solid or stranded,complying with the applicable requirements of IEC 228.
2. Insulation: PVC based thermoplastic material,conforming to the applicable requirements of IEC 227.
3. Similar to Liban Cable
2.6 CONTROL, MULTI-CORE, PVC INSULATED AND PVC SHEATHED CABLES
A. Scope: This specification covers multicore cables for signalization and control purposes, PVC insulated and sheathed rated 0.6 / 1 KV; to International Electrotechnical Commission IEC 60502-1, for use in cable ducts and indoors and for underground burial.
B. Construction
1. Conductor: Plain, annealed electrolytic copper conductors, solid or circular stranded conforming to the applicable requirements of IEC 60228.
2. Cross section
3. numbering
4. Insulation: PVC based thermoplastic material conforming to the applicable requirements of IEC 60502-1.
5. Assembly: Insulated conductors are laid up, filled where necessary with non-hygroscopic material or covered with a layer of non-hygroscopic tape.
6. Sheath: PVC based thermoplastic material conforming to the applicable requirements of IEC 60502-1.
7. Tests: Conforming to the applicable requirements of IEC 60502-1 either on raw materials or on finished products.
8. Similar to Liban Cable
2.7 SINGLE-CORE, NON SHEATHED, PVC INSULATED CABLES WITH RIGID CONDUCTORS – GREEN/YELLOW
A. Scope: This specification covers single core, PVC insulated cables, intended for internal wiring in dry locations, concealed in conduits, type 227 IEC 05 for rigid conductors and type 227 IEC 06 for flexible conductors (0.5mm2 to 1mm2 cross-sectional area) rated 300/500V; intended for general purposes, wiring applications in buildings where high dielectric resistance to chemical products, heat grease and acid is required, type 227 IEC 01 for rigid conductors and type 227 IEC 02 for flexible conductors having cross-sectional area above 1.0 mm2, rated 450/750 V to International Electrotechnical Commission Publication IEC 227.
B. Construction
1. Conductor: Plain, annealed, electrolytic copper conductors, solid or stranded, complying with the applicable requirements of IEC 228.
2. Insulation: PVC based thermoplastic material, conforming to the applicable requirements of IEC 227.
3. Similar to Liban Cable
2.8 SINGLE-CORE, NON SHEATHED, PVC INSULATED CABLES WITH RIGID CONDUCTORS – BARE CONDUCTRORS
A. Scope: This specification covers single core, bare conductor
B. Construction
1. Conductor: Plain, annealed, electrolytic copper conductors, solid or stranded, complying with the applicable requirements of IEC 228.
2. Insulation: PVC based thermoplastic material, conforming to the applicable requirements of IEC 227.
3. Similar to Liban Cable
2.9 INDOOR USE TELEPHONE CABLES PVC INSULATED AND PVC SHEATHED
A. Scope: Based on IEC 60189-1/2; LIBTEL (Indoor surface and conduit wiring)
B. Construction
1. Conductors: Copper 0.5 mm diameter bare.
2. Insulation: PVC colored in the mass with surface ring marking for identification.
3. Twisting: Pair.
4. Stranding: Concentric including earth continuity insulated tinned wire, protected with overlapped non-hygroscopic tape.
5. Outer-sheath: Grey PVC : A rip cord is laid up under the sheath for easy stripping.
6. Similar to Liban Cable
2.10 OUTDOOR USE TELEPHONE CABLES PVC INSULATED AND PVC SHEATHED
A. Scope: Based on IEC 60189-1/2; LIBTELS (Outdoor Screened)
B. Construction
1. Conductors: Copper 0.5 mm diameter bare.
2. Insulation: PVC colored in the mass with surface ring marking for identification.
3. Twisting: Pair.
4. Stranding: Concentric including earth continuity insulated tinned wire, protected with overlapped non-hygroscopic tape.
5. Moisture barrierand screen: ( S - type ) Aluminum foil applied with overlap.
6. Outer-sheath: Grey PVC : A rip cord is laid up under the sheath for easy stripping.
C. Similar to Liban Cable
2.11 CABLE TIES
A. General Characteristics
1. Colson™ ties are black, UV resistant, have external teeth and are designed to hold cables, strands and tubes in external installations.
2. Colson™ cable ties are compliant with standards EN 62275 type1 (NFC 68-146)
B. Width: 9mm
C. Resistance to temperature:
1. Maximum permanent usage temperature (1,000 Hrs. according to EN 50 146): 85°C
2. Min. permanent usage temperature (tie installed): -40 °C
3. Min. installation temperature: -30 °C
D. UV Protection:
1. Resistance to UV radiation according to standard IEC 62275 type 1
2. The UV resistant black cable ties for exterior use successfully pass UV resistance tests and climatic ageing tests representing actual conditions of use.
3. These cycles combine 1000 hours of exposure to radiation under arc or xenon lamps according to ISO 4892-2 method 1.
4. Similar to Legrand Ref. 319 10, 319 13, 319 16, 319 19, 319 20, 319 21
E. Tightening tool: should be used to tighten and trim surplus strap length close to the tie head. Similar to Legrand Ref. 319 96
F. Plugs: Wall spacer plug base, black, UV resistant, similar to Legrand Ref. 319 58
2.12 STEEL TENSION WIRES
A. Galvanized steel wire rope.
B. Proper accessories and fittings should be used with steel wire ropes.
C. Diameter:
1. 6mm
2. 8mm
3. 12mm
4. 14mm
5. 16mm
2.13 ACCESSORIES
A. All necessary accessories required for the proper installation and operation.
3 EXECUTION
3.1 INSTALLATION AND COMMISSIONING
END OF SECTION

## Grade of Compliancy
| RFT Compliance Matrix | Reference Number | SF-CF-25
|  | Owner | PRO
|  | Revision Code | 3.0
|  | Implementation Date | 2024-03-01
Grade of Compliance range from 0 to 15 with a step of 1 unit:
15 : Compliant with additional value, not initially included in the requirements
10 : Fully compliant
4 - 5 - 6: Partially compliant
0 : Not compliant
K : Disqualification