## General Requirements
| RFT Compliance Matrix |  |  |  | Reference Number | SF-CF-25
[5 empty] | Owner | PRO
[5 empty] | Revision Code | 3.0
[5 empty] | Implementation Date | 2024-03-01
Project Name:
Reference Number:
RFT Article (Part Number or Title) | Requirements (Description) | Killer | Fully Compliant | Partially Compliant | Non-Compliant | Reference (Specify document & page nb)
Article 4 | Conditions for the Participation of the Eligible Bidders
4.1 | 1- Bidders shall meet the following conditions, declared in accordance with the required documents in the First section of this Article mentioned below as (First: Envelope No. (1) Administrative Documents and Transactions):
a- That there is no proven violation, by the bidders, of professional ethics generally accepted and stipulated in the relevant provisions, if any;
b- Bidders have the legal capacity to enter into the procurement contract;
c- Bidders have fulfilled their obligations to pay taxes and social security contributions;
d- Bidders have not been convicted, neither their directors nor employees involved with the procurement process, by a court decision of any criminal offence - even if the verdict can still be appealed - related to their professional conduct or the making of false statements or misrepresentations as to their qualifications to enter into a procurement contract, or corrupting a public procurement or a contract awarding process, or have not been otherwise disqualified pursuant to administrative suspension or debarment proceedings, or have been in a situation of exclusion from participation in public procurements;
e- Bidders are not the subject of legal proceedings for insolvency or bankruptcy, or were declared bankrupt by a court of law;
f- Bidders have not been convicted by a court decision - even if the verdict can still be appealed - of usury or money laundering;
g- Bidders have not participated in the decision-making process of the contracting authority or have any conflict of interest, or any material interest linking them to any of the decision makers;
h- Any other conditions set forth by the contracting authority in the tender documents that are commensurate with the required works;
i- Certificate from the Ministry of Economy proving compliance with the provisions of the Law on Boycott of Israel for foreign companies (added by Law No. 309, dated April 19, 2023).
j- Declaration of the economic beneficiaries (according to Law No. 309, dated April 19, 2023).
4.2 | 2- The bid must be submitted clearly and unequivocally without any deletion, alteration, or modification.
4.3 | 3- The bidders state in their offer that they have reviewed the Tender document and its complementary documents and have obtained a copy. They accept and undertake to adhere to all the conditions outlined therein without any reservations or exceptions. The bidder submits their offer on this basis and affixes financial stamps worth fifty thousand Lebanese pounds covering all the documents.
4.4 | 4- Any bid containing reservations or exceptions is rejected.
4.5 | 5- The bidder mentions in their offer a clear address and place of residence for prompt communication.
Administrative Documents and Transactions | First: Envelope No. (1) Administrative Documents and Transactions
A- General Conditions:
1- Undertaking Letter (Declaration), according to the attached form, signed and stamped by the bidder, this Undertaking includes the bidder's confirmation of their commitment to the price and the validity of the offer. A financial stamp of 50,000 L.L. is affixed.
2- Commercial Circular specifying the authorized signatory of the bidder and a sample of their signature.
3- Legal Authorization: If the offer is signed by someone other than the person authorized to sign according to the commercial circular, it must be notarized by a notary public.
4- Police Record of the Authorized Signatory or his “legal representative”, not exceeding three months from the bid opening date.
5- Partnership Contract legalized by a notary public if required.
6- Registration Certificate before the Directorate of Value Added Tax, if applicable, or a certificate of non-registration if not subject to it. In the latter case, the bidder commits to their bid price even if they become registered for VAT during the execution period.
7- Registration Certificate issued by the Ministry of Finance – Department of Revenue.
8- Certificate issued by the Ministry of Finance proving the bidder's compliance with tax obligations.
9- Clearance Certificate from the National Social Security Fund “comprehensive or valid for participation in public tenders and bids” valid on the date of the bid opening session, stating that the bidder has paid all his subscriptions (the bidder must be registered before the National Social Security Fund and any statement mentioning the phrase “unregistered institution” will be rejected).
10- Certificate issued by the Municipality, proving full payment of municipal fees by the bidder, issued by the municipality within its jurisdiction based on the commercial registration certificate.
11- Comprehensive Certificate issued by the Commercial Register showing founders, members, contributors, or partners, authorized signatories, the manager, capital, the bidder's activity, and ongoing liabilities.
12- Certificate issued by the relevant authorities proving that the bidder is not in a state of bankruptcy.
13- Certificate issued by the relevant authorities proving that the bidder is not in a state of judicial liquidation.
14- Bid bond as required in the specific Tender document of the procurement project, in accordance with Articles 34 and 36 of the Public Procurement Law.
15- Declaration from the Bidder identifying the economic beneficiary/beneficiaries according to Form M18 issued by the Ministry of Finance (any natural person who owns or effectively controls the ultimate outcome of the activity practiced by the bidder, either directly or indirectly, whether the bidder is a natural person or a legal entity.)
16- Copies of Identification Cards (ID/Passport) for the economic beneficiary/beneficiaries.
17- Copies of Identification Cards (ID/Passport) for each person representing the bidder (those acting on behalf of the bidder in their relationship with the contracting authority: legal representative, representative of the legal entity, or authorized signatory).
18- Integrity Declaration Document signed by the bidder in accordance with the prescribed format
Miscellaneous | The bidder shall declare any relative relations with any Alfa employee up to the 4th degree under Clause 30 of the PPL, for MIC1 to be able to assess the existing of any potential conflict of interests which may lead to deprive the bidder from participating to the tender under the risk of disqualification.
The bidder or any of his employees, partners, agents, contributors, consultants, or their relatives shall declare any relationships that may lead to a conflict of interest in the subject of this contract.
Special Conditions | B- Special Conditions Regarding the Subject of the Contract:
Financial Qualifications | 1- Financial Qualifications (To be determined based on the size and nature of the contract).
Technical/Professional Qualifications | 2- Technical/Professional Qualifications (To be determined based on the nature of the contract):
1- Certificate from the Chamber of Commerce, Industry, and Agriculture confirming that the bidder is engaged in the activities related to the subject of the contract, valid as of the date of the bidding session and valid for participation in public tenders.
2- Clearance certificate from the Order of Engineers…
3- Clearance certificate from the Contractors Syndicate…
4- ISO certificate.
5- Five Certificates of good execution and completion for similar projects in terms of size and type.
6- Technical proposal according to the required specifications in the appendix (1) of the RFT.
7- Declaration of site inspection by the bidder, denying any unfamiliarity, according to the attached model.
Participation of a foreign bidder | C- In case of the participation of a foreign bidder, the bidder must comply with one of the following conditions:
1- is part of a coalition that includes at least one Lebanese company that meets the conditions required by the specific Tender document of the procurement project.
2- The personal presence of the legal representative of the company to participate in the procurement proceedings (not mandatory).
3- Has an authorized agent or representative in Lebanon responsible for signing the contract on its behalf.
In addition to the above conditions, the foreign bidder must submit the following:
1- Certificate registration of the company or certificate of establishment issued by the relevant authorities in their country.
2- Certificate from the Lebanese Ministry of Economy and Trade confirming compliance with the provisions of the Law on Israel Boycott.
3- The required certificates according to paragraph (First) above, according to the laws of the country where the bidder is located, provided that these certificates are authenticated according to the regulations of the competent authorities.
For certificates issued without an expiration date, the validity date of each certificate is determined according to its nature, not exceeding six months from the date of the bid opening session.
Information Security Specifications | Information Security Specifications Issuing Department to determine whether all or part of this Article is applicable to their specific RFT
The Bidder shall commit to refrain from offering any product / equipment which can cause security threat or information leakage that jeopardizes MIC1 network security. (K)
The Bidder shall accept that MIC1 runs a vulnerability scan on the proposed solution prior to issuing the acceptance and in case any vulnerability is found, the Bidder undertakes to take the necessary actions to remedy such vulnerability within _____________________ days from its notification.
The Bidder shall mention the security standards adopted/followed in designing the proposed solution.
The Bidder should specify if it has acquired the ISO27001 certification or any other equivalent security certification and submit with the Offer a copy of such certificate.
The Bidder shall not hard code passwords in the proposed solution.
The provided application should run without the need of root (unix) and / or admin (win) privileges.
Source code of proposed application should be owned by MIC1.
System shall allow generation of user, operator as well as alarms logs.
Solution and storage shall be sized to host history logs for at least 1 year back.
The Bidder should submit a data flow diagram and schema of the solution architecture.
In case of online payment, the Bidder shall use encryption. (K)
The Bidder shall harden systems servers / storage before being published online, and describe hardening aspects applied on each type.
The Bidder shall describe security checking and audits performed on the designed solution prior to putting it on the market.
The Bidder shall change default errors / messages and configuration.
Application should support role-based access, specific privileges per user (i.e specific access to application modules and reports)
Database should support restricted access per user or groups to data (i.e access per field or per table, …)
Encryption shall be used in all communications / interactions between systems, especially if the communication is through web access. Web based access shall always be used through HTTP+SSL.
Each user shall have only one account / profile to access data.
Least-privileges should always be specified on nodes / applications.
Pseudocode flow chart shall be provided by the Bidders.
The Bidder should commit to improve solution / systems information security weaknesses whenever needed or highlighted by MIC1 information security team.
Health, Safety and Environmental Specifications | To ensure that the proposed products and services bidders are compliant with HSE culture, bidders should state basic HSE specifications and compliance information:
Bidder shall provide the product’s specifications that have an environmental impact (power consumption, gas emissions, etc…)
Bidder shall provide the product specifications that contribute into preserving the environment (made of recycled material, ozone friendly, low volatile organic compounds, etc…)
Bidder shall provide the product’s specifications that contribute towards the health and safety of the users (ergonomic design, safety features, etc)
Bidder shall state the safety measures being followed by personnel performing the work on Alfa’s sites (ISO45001 certification, specific best practices, etc…).
Bidder shall provide the product’s life cycle data if available.

## Technical Requirements
| RFT Compliance Matrix |  |  |  | Reference Number | SF-CF-25
[5 empty] | Owner | PRO
[5 empty] | Revision Code | 3.0
[5 empty] | Implementation Date | 2024-03-01
Project Name: | JDEIDET DATA CENTER
Reference Number: | 26 05 36 - Cable Trays for Electrical Systems - 10.2023
RFT Article (Part Number or Title) | Requirements (Description) | Killer | Fully Compliant | Partially Compliant | Non-Compliant | Reference (Specify document & page nb)
1 GENERAL
1.1 SUMMARY
A. This Section includes mild steel cable trays and ladders with related accessories.
B. Cable trays and ladders systems are defined to include, but not limited to trays straight sections, covers for cable trays (if required), bends, tees, elbows, drop-outs, supports and accessories.
1.2 REFERENCES
A. Standards
1. IEC EN 61537:2007 – Cable management. Cable tray systems and cable ladder systems
1.3 SUBMITTALS
A. Data: submit manufacturer documents including, but not limited to, data on trays material types, finishes, fittings, technical characteristics, test certificates, etc...
B. Shop Drawings: For each type of tray.
1. Show fabrication and installation details of cable tray, including plans, elevations, and sections of components and attachments to other construction elements.
2. Designate components and accessories, including, but not limited to, clamps, brackets, hanger rods, splice-plate connectors, expansion-joint assemblies, straight lengths, and fittings.
C. Coordination Drawings: Floor plans and sections, drawn to scale. Include scaled cable trays and ladders layout and relationships between components and adjacent structural, electrical, and mechanical elements. Show the following:
1. Vertical and horizontal offsets and transitions.
2. Clearances for access above and to side of cable trays.
3. Vertical elevation of cable trays above the floor or bottom of ceiling structure.
D. Field quality-control reports.
1.4 WARRANTY
A. Equipment
1. The supplied products shall be covered by full supplier warranty for a minimum period of one (1) year from delivery to site at a full repair and replacement service.
2. Warranty shall include all defected spare parts and workmanship.
B. Services
1. Installation and dismantling
a. The supplier is responsible for the dismantling, hoisting, transportation and re-installation for parts that cannot be repaired or replaced on site
2. Part replacement/repair
a. For any part replacement or repair service the warranty for the repaired or new part shall be a minimum of 6 (six) months from the date of receipt of the repaired or new part. In case a part was repaired twice already under this warranty and the equipment becomes faulty again within up to six months the Operator on its discretion may request replacement of the complete equipment
3. Major defect
a. In case of major defect in the supplied products, the Operator reserves the right to reject the equipment. The supplier shall replace the defected system/parts under no cost from the Operator, including dismantling, hoisting, transportation and re-installation
2 PRODUCTS
2.1 MANUFACTURERS
A. Approved Brands:
1. Tramsteel
2. Attarsteel
3. or equivalent
B. Manufactured in a company certified according to DIN ISO 9001:2015
2.2 CABLE TRAYS
A. Construction:
1. Galvanization: manufactured from Galvanized Steel (Sendzimir Process). This Galvanized Steel Sheet is obtained by immersing a soft steel sheet in a zinc bath; a stable iron-zinc alloy is formed with a predominance of pure zinc on surface. The thickness of this zinc coating is 21 microns, i.e. 275 gr/m² on both sides. When a galvanized sheet of standard thickness is sheared or punched, the cut edges of the metal are protected by the formation of zinc electrolyte system.
2. Flanges: Return type
3. Perforation: The trays have obround perforations of 25x7mm.
4. Thickness: 1.5mm for all dimensions
B. Cable protection: cut edges should be treated and covered with PVC protection to prevent damage to cables. The interiors of all types of cable shall be smooth and free of any projection that might injure cable sheaths and jackets (NEC 318-4). All slice plates should be installed on the outside surface of the supports. Round head bolts, screws or other fasteners (head inside) are to be used exclusively.
2.3 CABLE TRAY COVERS
A. Should be made of galvanized metal sheets of thickness 0.5mm, tied with 304 stainless steel wire tray tie with hoop, Size: 12×0.5m at every 50cm length.
2.4 CABLE TRAY ACCESSORIES
A. Fittings: Tees, crosses, risers, elbows, and other fittings as indicated, of same materials and finishes as cable tray.
B. Elbow: minimum 45°, round or straight
C. Supports: standard cable supports and elements for wall and ceiling installations, spaced 100cm.
D. Covers: Louvered type of same materials and finishes as cable tray.
E. Barrier Strips: Same materials and finishes as cable tray.
F. Cable tray supports and connectors, including bonding jumpers, as recommended by cable tray manufacturer.
G. All necessary accessories required for the proper installation of the cable trays and ladders.
2.5 Cable Ladders
A. Cable ladders are used for the cables installed on towers. Ladders shall be selected for their ability to provide protection, consolidation, distribution, and accessibility of cables.
B. The ladder shall be capable of being supported to both vertical and horizontal surfaces.
C. Outdoor cable ladders shall be hot dip galvanized with coating thickness of minimum 85 -100 microns. The dimensions shall be 3000mm in length, 420mm in width and it is made of steel angles (40x40x4) mm and (30x30x3) mm with 25cm spacing between steps.
2.6 CABLE LADDERS ACCESSORIES
A. Fittings: Tees, crosses, risers, elbows, and other fittings as indicated, of same materials and finishes as cable ladder.
B. Supports and connectors, including bonding jumpers, as recommended by tray manufacturer.
2.7 CABLE BASKET
A. APPLICATION
1. Suitable for indoor installation to support, store, and manage low current and electrical cables, either overhead, under raised floor or mounted vertically on a wall.
B. MATERIALS AND FINISHES
1. Description: Cable basket shall be made of high strength steel wires and formed into a mesh pattern with intersecting wires welded together. Wire ends along sides (flanges) shall be rounded during manufacturing for safety of cables and installers. Straight section longitudinal wires shall be straight with no bends.
2. Finishes: Hot-dip galvanized finish.
2.8 CABLE BASKET ACCESSORIES
A. Fittings: Tees, crosses, risers, elbows, and other fittings as indicated, of same materials and finishes as cable basket.
B. Covers: Non-perforated type of same materials and finishes as cable basket.
C. Barrier Strips: Same materials and finishes as cable tray.
D. Cable ladder supports and connectors, including bonding jumpers, as recommended by cable basket manufacturer.
2.9 WARNING SIGNS
A. Lettering: 40-mm high, black letters on yellow background with legend "WARNING! NOT TO BE USED AS WALKWAY, LADDER, OR SUPPORT FOR LADDERS OR PERSONNEL."
2.10 EARTHING BRAIDS
A. Earthing braids are made of annealed stranded copper, 10mm², Yellow/Green PVC insulation, to link cable tray sections.
2.11 SCREWS
A. Roof bolt, M6 x 25mm, Zinc Plated with semi-sphere head.
3 EXECUTION
3.1 CABLE TRAY INSTALLATION
A. Comply with recommendations in IEC EN 61537. Install as a complete system, including all necessary fasteners, hold-down clips, splice-plate support systems, barrier strips, hinged horizontal and vertical splice plates, elbows, reducers, tees, and crosses.
B. Remove burrs and sharp edges from trays.
C. Fasten trays supports to building structure.
1. Place supports so that spans do not exceed 0.5cm.
2. Construct supports from channel members, threaded rods, and other appurtenances furnished by tray manufacturer. Arrange supports in trapeze or wall-bracket form as required by application.
3. Support bus assembly to prevent twisting from eccentric loading.
4. Manufacture center-hung support, designed for 60 percent versus 40 percent eccentric loading condition, with a safety factor of 3.
D. Make connections to equipment with flanged fittings fastened to tray and to equipment. Support cable tray and ladder independent of fittings. Do not carry weight of trays on equipment enclosure.
E. Install expansion connectors where tray crosses building expansion joint and in cable tray and ladder runs that exceed dimensions recommended in IEC EN 61537. Space connectors and set gaps according to applicable standard.
F. Make changes in direction and elevation using standard fittings.
G. Make cable tray and ladder connections using standard fittings.
H. Seal penetrations through fire and smoke barriers according to Section 07 84 13 "Penetration Fire-stopping."
I. Sleeves for Future Cables: Install capped sleeves for future cables through Firestop sealed cable tray penetrations of fire and smoke barriers.
J. Workspace: Install cable trays with enough space to permit access for installing cables.
K. After installation of cable trays is completed, install warning signs in visible locations on or near cable trays.
3.2 CABLE INSTALLATION
A. Install cables only when cable tray and ladder installation has been completed and inspected.
B. Fasten cables installed on perforated trays and ladders with hot dip galvanized cast steel clamps for cables sections equal or higher than and with cable ties for the lowest sections. Tighten clamps only enough to secure the cable, without indenting the cable jacket. Install cable ties with a tool that includes an automatic pressure-limiting device.
C. Fasten cables to tray every 500 mm.
D. Where required or specified, install covers after installation of cable is completed.
3.3 CONNECTIONS
A. Ground cable trays and ladders according to manufacturer's written instructions.
B. Install an insulated equipment grounding conductor with cable tray and ladder, in addition to those required by IEC 364.
3.4 FIELD QUALITY CONTROL
A. After installing cable trays and after electrical circuitry has been energized, survey for compliance with requirements. Perform the following field quality-control survey:
1. Visually inspect cable insulation for damage. Correct sharp corners, protuberances in cable tray and ladder, vibration, and thermal expansion and contraction conditions, which may cause or have caused damage.
2. Verify that the number, size, and voltage of cables in tray do not exceed that permitted by IEC 364.
3. Verify that there is no intrusion of such items as pipe, hangers, or other equipment that could damage cables.
4. Remove deposits of dust, industrial process materials, trash of any description, and any blockage of tray ventilation.
5. Visually inspect each tray joint and each ground connection for mechanical continuity. Check bolted connections between sections for corrosion. Clean and retorque in suspect areas.
6. Check for missing or damaged bolts, bolt heads, or nuts. When found, replace with specified hardware.
7. Perform visual and mechanical checks for adequacy of cable tray and ladder grounding; verify that all takeoff raceways are bonded to tray.
B. Report results in writing.
3.5 PROTECTION
A. Protect installed cable trays and ladders.
1. Repair cut or damage to galvanized finishes with zinc-rich paint recommended by cable tray and ladder manufacturer.
2. Repair damage to PVC or paint finishes with matching touchup coating recommended by cable tray and ladder manufacturer.
3. Install temporary protection for cables in open trays to protect exposed cables from falling objects or debris during construction. Temporary protection for cables and trays can be constructed of wood or metal materials until the risk of damage is over.
END OF SECTION

## Grade of Compliancy
| RFT Compliance Matrix | Reference Number | SF-CF-25
|  | Owner | PRO
|  | Revision Code | 3.0
|  | Implementation Date | 2024-03-01
Grade of Compliance range from 0 to 15 with a step of 1 unit:
15 : Compliant with additional value, not initially included in the requirements
10 : Fully compliant
4 - 5 - 6: Partially compliant
0 : Not compliant
K : Disqualification