## grade of compliance range
| RFT Scoring Sheet | Reference Number | SF-CF-87
|  | Owner | PRO/PMO
|  | Revision Code | 2.0
|  | Implementation Date | 2021-09-01
Grade of Compliance range from 0 to 15 with a step of 1 unit:
15 : Compliant with additional value, not initially included in the requirements
10 : Fully compliant
4 - 5 - 6: Partially compliant
0 : Not compliant
K : Disqualification

## weight
| RFT Scoring Sheet | [11 empty] | Reference Number |  | SF-CF-87
[13 empty] | Owner |  | PRO/PMO
[13 empty] | Revision Code |  | 2.0
[13 empty] | Implementation Date |  | 2021-09-01
Project Name | JDEIDET DATA CENTER
Weight Distribution | 50% Technical 50% Commercial
Article | Requirements | Weight | Responsible Entity | Supplier 1 | Supplier 2 | Supplier 3 | Supplier 4 | Supplier 5 | Supplier 6 | Remarks | Supplier 1 Final | Supplier 2 Final | Supplier 3 Final | Supplier 4 Final | Supplier 5 Final | Supplier 6 Final
| 1 GENERAL | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1.1 SUMMARY | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. This Section includes mild steel cable trays and ladders with related accessories. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Cable trays and ladders systems are defined to include, but not limited to trays straight sections, covers for cable trays (if required), bends, tees, elbows, drop-outs, supports and accessories. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1.2 REFERENCES | 5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Standards | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. IEC EN 61537:2007 – Cable management. Cable tray systems and cable ladder systems | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1.3 SUBMITTALS | 5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Data: submit manufacturer documents including, but not limited to, data on trays material types, finishes, fittings, technical characteristics, test certificates, etc... | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Shop Drawings: For each type of tray. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Show fabrication and installation details of cable tray, including plans, elevations, and sections of components and attachments to other construction elements. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Designate components and accessories, including, but not limited to, clamps, brackets, hanger rods, splice-plate connectors, expansion-joint assemblies, straight lengths, and fittings. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| C. Coordination Drawings: Floor plans and sections, drawn to scale. Include scaled cable trays and ladders layout and relationships between components and adjacent structural, electrical, and mechanical elements. Show the following: | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Vertical and horizontal offsets and transitions. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Clearances for access above and to side of cable trays. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. Vertical elevation of cable trays above the floor or bottom of ceiling structure. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| D. Field quality-control reports. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1.4 WARRANTY | 5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Equipment | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. The supplied products shall be covered by full supplier warranty for a minimum period of one (1) year from delivery to site at a full repair and replacement service. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Warranty shall include all defected spare parts and workmanship. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Services | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Installation and dismantling | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| a. The supplier is responsible for the dismantling, hoisting, transportation and re-installation for parts that cannot be repaired or replaced on site | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Part replacement/repair | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| a. For any part replacement or repair service the warranty for the repaired or new part shall be a minimum of 6 (six) months from the date of receipt of the repaired or new part. In case a part was repaired twice already under this warranty and the equipment becomes faulty again within up to six months the Operator on its discretion may request replacement of the complete equipment | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. Major defect | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| a. In case of major defect in the supplied products, the Operator reserves the right to reject the equipment. The supplier shall replace the defected system/parts under no cost from the Operator, including dismantling, hoisting, transportation and re-installation | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2 PRODUCTS | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.1 MANUFACTURERS | 5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Approved Brands: | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Tramsteel | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Attarsteel | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. or equivalent | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Manufactured in a company certified according to DIN ISO 9001:2015 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.2 CABLE TRAYS | 5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Construction: | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Galvanization: manufactured from Galvanized Steel (Sendzimir Process). This Galvanized Steel Sheet is obtained by immersing a soft steel sheet in a zinc bath; a stable iron-zinc alloy is formed with a predominance of pure zinc on surface. The thickness of this zinc coating is 21 microns, i.e. 275 gr/m² on both sides. When a galvanized sheet of standard thickness is sheared or punched, the cut edges of the metal are protected by the formation of zinc electrolyte system. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Flanges: Return type | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. Perforation: The trays have obround perforations of 25x7mm. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 4. Thickness: 1.5mm for all dimensions | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Cable protection: cut edges should be treated and covered with PVC protection to prevent damage to cables. The interiors of all types of cable shall be smooth and free of any projection that might injure cable sheaths and jackets (NEC 318-4). All slice plates should be installed on the outside surface of the supports. Round head bolts, screws or other fasteners (head inside) are to be used exclusively. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.3 CABLE TRAY COVERS | 5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Should be made of galvanized metal sheets of thickness 0.5mm, tied with 304 stainless steel wire tray tie with hoop, Size: 12×0.5m at every 50cm length. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.4 CABLE TRAY ACCESSORIES | 5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Fittings: Tees, crosses, risers, elbows, and other fittings as indicated, of same materials and finishes as cable tray. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Elbow: minimum 45°, round or straight | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| C. Supports: standard cable supports and elements for wall and ceiling installations, spaced 100cm. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| D. Covers: Louvered type of same materials and finishes as cable tray. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| E. Barrier Strips: Same materials and finishes as cable tray. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| F. Cable tray supports and connectors, including bonding jumpers, as recommended by cable tray manufacturer. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| G. All necessary accessories required for the proper installation of the cable trays and ladders. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 Cable Ladders | 5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Cable ladders are used for the cables installed on towers. Ladders shall be selected for their ability to provide protection, consolidation, distribution, and accessibility of cables. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. The ladder shall be capable of being supported to both vertical and horizontal surfaces. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| C. Outdoor cable ladders shall be hot dip galvanized with coating thickness of minimum 85 -100 microns. The dimensions shall be 3000mm in length, 420mm in width and it is made of steel angles (40x40x4) mm and (30x30x3) mm with 25cm spacing between steps. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.6 CABLE LADDERS ACCESSORIES | 5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Fittings: Tees, crosses, risers, elbows, and other fittings as indicated, of same materials and finishes as cable ladder. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Supports and connectors, including bonding jumpers, as recommended by tray manufacturer. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.7 CABLE BASKET | 5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. APPLICATION | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Suitable for indoor installation to support, store, and manage low current and electrical cables, either overhead, under raised floor or mounted vertically on a wall. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. MATERIALS AND FINISHES | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Description: Cable basket shall be made of high strength steel wires and formed into a mesh pattern with intersecting wires welded together. Wire ends along sides (flanges) shall be rounded during manufacturing for safety of cables and installers. Straight section longitudinal wires shall be straight with no bends. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Finishes: Hot-dip galvanized finish. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.8 CABLE BASKET ACCESSORIES | 5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Fittings: Tees, crosses, risers, elbows, and other fittings as indicated, of same materials and finishes as cable basket. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Covers: Non-perforated type of same materials and finishes as cable basket. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| C. Barrier Strips: Same materials and finishes as cable tray. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| D. Cable ladder supports and connectors, including bonding jumpers, as recommended by cable basket manufacturer. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.9 WARNING SIGNS | 5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Lettering: 40-mm high, black letters on yellow background with legend "WARNING! NOT TO BE USED AS WALKWAY, LADDER, OR SUPPORT FOR LADDERS OR PERSONNEL." | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.10 EARTHING BRAIDS | 5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Earthing braids are made of annealed stranded copper, 10mm², Yellow/Green PVC insulation, to link cable tray sections. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.11 SCREWS | 5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Roof bolt, M6 x 25mm, Zinc Plated with semi-sphere head. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3 EXECUTION | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3.1 CABLE TRAY INSTALLATION | 10 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Comply with recommendations in IEC EN 61537. Install as a complete system, including all necessary fasteners, hold-down clips, splice-plate support systems, barrier strips, hinged horizontal and vertical splice plates, elbows, reducers, tees, and crosses. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Remove burrs and sharp edges from trays. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| C. Fasten trays supports to building structure. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Place supports so that spans do not exceed 0.5cm. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Construct supports from channel members, threaded rods, and other appurtenances furnished by tray manufacturer. Arrange supports in trapeze or wall-bracket form as required by application. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. Support bus assembly to prevent twisting from eccentric loading. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 4. Manufacture center-hung support, designed for 60 percent versus 40 percent eccentric loading condition, with a safety factor of 3. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| D. Make connections to equipment with flanged fittings fastened to tray and to equipment. Support cable tray and ladder independent of fittings. Do not carry weight of trays on equipment enclosure. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| E. Install expansion connectors where tray crosses building expansion joint and in cable tray and ladder runs that exceed dimensions recommended in IEC EN 61537. Space connectors and set gaps according to applicable standard. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| F. Make changes in direction and elevation using standard fittings. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| G. Make cable tray and ladder connections using standard fittings. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| H. Seal penetrations through fire and smoke barriers according to Section 07 84 13 "Penetration Fire-stopping." | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| I. Sleeves for Future Cables: Install capped sleeves for future cables through Firestop sealed cable tray penetrations of fire and smoke barriers. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| J. Workspace: Install cable trays with enough space to permit access for installing cables. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| K. After installation of cable trays is completed, install warning signs in visible locations on or near cable trays. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3.2 CABLE INSTALLATION | 5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Install cables only when cable tray and ladder installation has been completed and inspected. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Fasten cables installed on perforated trays and ladders with hot dip galvanized cast steel clamps for cables sections equal or higher than and with cable ties for the lowest sections. Tighten clamps only enough to secure the cable, without indenting the cable jacket. Install cable ties with a tool that includes an automatic pressure-limiting device. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| C. Fasten cables to tray every 500 mm. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| D. Where required or specified, install covers after installation of cable is completed. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3.3 CONNECTIONS | 5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Ground cable trays and ladders according to manufacturer's written instructions. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Install an insulated equipment grounding conductor with cable tray and ladder, in addition to those required by IEC 364. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3.4 FIELD QUALITY CONTROL | 5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. After installing cable trays and after electrical circuitry has been energized, survey for compliance with requirements. Perform the following field quality-control survey: | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Visually inspect cable insulation for damage. Correct sharp corners, protuberances in cable tray and ladder, vibration, and thermal expansion and contraction conditions, which may cause or have caused damage. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Verify that the number, size, and voltage of cables in tray do not exceed that permitted by IEC 364. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. Verify that there is no intrusion of such items as pipe, hangers, or other equipment that could damage cables. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 4. Remove deposits of dust, industrial process materials, trash of any description, and any blockage of tray ventilation. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5. Visually inspect each tray joint and each ground connection for mechanical continuity. Check bolted connections between sections for corrosion. Clean and retorque in suspect areas. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 6. Check for missing or damaged bolts, bolt heads, or nuts. When found, replace with specified hardware. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 7. Perform visual and mechanical checks for adequacy of cable tray and ladder grounding; verify that all takeoff raceways are bonded to tray. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Report results in writing. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3.5 PROTECTION | 5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Protect installed cable trays and ladders. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Repair cut or damage to galvanized finishes with zinc-rich paint recommended by cable tray and ladder manufacturer. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Repair damage to PVC or paint finishes with matching touchup coating recommended by cable tray and ladder manufacturer. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. Install temporary protection for cables in open trays to protect exposed cables from falling objects or debris during construction. Temporary protection for cables and trays can be constructed of wood or metal materials until the risk of damage is over. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| END OF SECTION | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 | 0
[11 empty] | SUPPLIER 1 SCORE | SUPPLIER 2 SCORE | SUPPLIER 3 SCORE | SUPPLIER 4 SCORE | SUPPLIER 5 SCORE | SUPPLIER 6 SCORE
* For Requirements defined as ''Killer'', a ‘’Fully Compliant’’ score should be the sole acceptable outcome. Failing to obtain a ‘’Fully Compliant’’ score on the requirements defined as Killers, will mandate immediate disqualification for bidders.
Note on D9: Entity (Department/ Unit) that identified the requirement and that will be responsible for its evaluation.
Note on E9: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on F9: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on G9: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on H9: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on I9: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on J9: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on E11: Evaluators Comments
Note on F11: Evaluators Comments
Note on G11: Evaluators Comments
Note on H11: Evaluators Comments
Note on I11: Evaluators Comments
Note on J11: Evaluators Comments
Note on E12: Evaluators Comments
Note on F12: Evaluators Comments
Note on G12: Evaluators Comments
Note on H12: Evaluators Comments
Note on I12: Evaluators Comments
Note on J12: Evaluators Comments
Note on E13: Evaluators Comments
Note on F13: Evaluators Comments
Note on G13: Evaluators Comments
Note on H13: Evaluators Comments
Note on I13: Evaluators Comments
Note on J13: Evaluators Comments
Note on E14: Evaluators Comments
Note on F14: Evaluators Comments
Note on G14: Evaluators Comments
Note on H14: Evaluators Comments
Note on I14: Evaluators Comments
Note on J14: Evaluators Comments
Note on E15: Evaluators Comments
Note on F15: Evaluators Comments
Note on G15: Evaluators Comments
Note on H15: Evaluators Comments
Note on I15: Evaluators Comments
Note on J15: Evaluators Comments
Note on E16: Evaluators Comments
Note on F16: Evaluators Comments
Note on G16: Evaluators Comments
Note on H16: Evaluators Comments
Note on I16: Evaluators Comments
Note on J16: Evaluators Comments
Note on E17: Evaluators Comments
Note on F17: Evaluators Comments
Note on G17: Evaluators Comments
Note on H17: Evaluators Comments
Note on I17: Evaluators Comments
Note on J17: Evaluators Comments
Note on E18: Evaluators Comments
Note on F18: Evaluators Comments
Note on G18: Evaluators Comments
Note on H18: Evaluators Comments
Note on I18: Evaluators Comments
Note on J18: Evaluators Comments
Note on E19: Evaluators Comments
Note on F19: Evaluators Comments
Note on G19: Evaluators Comments
Note on H19: Evaluators Comments
Note on I19: Evaluators Comments
Note on J19: Evaluators Comments
Note on E20: Evaluators Comments
Note on F20: Evaluators Comments
Note on G20: Evaluators Comments
Note on H20: Evaluators Comments
Note on I20: Evaluators Comments
Note on J20: Evaluators Comments
Note on E21: Evaluators Comments
Note on F21: Evaluators Comments
Note on G21: Evaluators Comments
Note on H21: Evaluators Comments
Note on I21: Evaluators Comments
Note on J21: Evaluators Comments
Note on E22: Evaluators Comments
Note on F22: Evaluators Comments
Note on G22: Evaluators Comments
Note on H22: Evaluators Comments
Note on I22: Evaluators Comments
Note on J22: Evaluators Comments
Note on E23: Evaluators Comments
Note on F23: Evaluators Comments
Note on G23: Evaluators Comments
Note on H23: Evaluators Comments
Note on I23: Evaluators Comments
Note on J23: Evaluators Comments
Note on E24: Evaluators Comments
Note on F24: Evaluators Comments
Note on G24: Evaluators Comments
Note on H24: Evaluators Comments
Note on I24: Evaluators Comments
Note on J24: Evaluators Comments
Note on E25: Evaluators Comments
Note on F25: Evaluators Comments
Note on G25: Evaluators Comments
Note on H25: Evaluators Comments
Note on I25: Evaluators Comments
Note on J25: Evaluators Comments
Note on E26: Evaluators Comments
Note on F26: Evaluators Comments
Note on G26: Evaluators Comments
Note on H26: Evaluators Comments
Note on I26: Evaluators Comments
Note on J26: Evaluators Comments
Note on E27: Evaluators Comments
Note on F27: Evaluators Comments
Note on G27: Evaluators Comments
Note on H27: Evaluators Comments
Note on I27: Evaluators Comments
Note on J27: Evaluators Comments
Note on E28: Evaluators Comments
Note on F28: Evaluators Comments
Note on G28: Evaluators Comments
Note on H28: Evaluators Comments
Note on I28: Evaluators Comments
Note on J28: Evaluators Comments
Note on E29: Evaluators Comments
Note on F29: Evaluators Comments
Note on G29: Evaluators Comments
Note on H29: Evaluators Comments
Note on I29: Evaluators Comments
Note on J29: Evaluators Comments
Note on E30: Evaluators Comments
Note on F30: Evaluators Comments
Note on G30: Evaluators Comments
Note on H30: Evaluators Comments
Note on I30: Evaluators Comments
Note on J30: Evaluators Comments
Note on E31: Evaluators Comments
Note on F31: Evaluators Comments
Note on G31: Evaluators Comments
Note on H31: Evaluators Comments
Note on I31: Evaluators Comments
Note on J31: Evaluators Comments
Note on E32: Evaluators Comments
Note on F32: Evaluators Comments
Note on G32: Evaluators Comments
Note on H32: Evaluators Comments
Note on I32: Evaluators Comments
Note on J32: Evaluators Comments
Note on E33: Evaluators Comments
Note on F33: Evaluators Comments
Note on G33: Evaluators Comments
Note on H33: Evaluators Comments
Note on I33: Evaluators Comments
Note on J33: Evaluators Comments
Note on E34: Evaluators Comments
Note on F34: Evaluators Comments
Note on G34: Evaluators Comments
Note on H34: Evaluators Comments
Note on I34: Evaluators Comments
Note on J34: Evaluators Comments
Note on E35: Evaluators Comments
Note on F35: Evaluators Comments
Note on G35: Evaluators Comments
Note on H35: Evaluators Comments
Note on I35: Evaluators Comments
Note on J35: Evaluators Comments
Note on E36: Evaluators Comments
Note on F36: Evaluators Comments
Note on G36: Evaluators Comments
Note on H36: Evaluators Comments
Note on I36: Evaluators Comments
Note on J36: Evaluators Comments
Note on E37: Evaluators Comments
Note on F37: Evaluators Comments
Note on G37: Evaluators Comments
Note on H37: Evaluators Comments
Note on I37: Evaluators Comments
Note on J37: Evaluators Comments
Note on E38: Evaluators Comments
Note on F38: Evaluators Comments
Note on G38: Evaluators Comments
Note on H38: Evaluators Comments
Note on I38: Evaluators Comments
Note on J38: Evaluators Comments
Note on E39: Evaluators Comments
Note on F39: Evaluators Comments
Note on G39: Evaluators Comments
Note on H39: Evaluators Comments
Note on I39: Evaluators Comments
Note on J39: Evaluators Comments
Note on E40: Evaluators Comments
Note on F40: Evaluators Comments
Note on G40: Evaluators Comments
Note on H40: Evaluators Comments
Note on I40: Evaluators Comments
Note on J40: Evaluators Comments
Note on E41: Evaluators Comments
Note on F41: Evaluators Comments
Note on G41: Evaluators Comments
Note on H41: Evaluators Comments
Note on I41: Evaluators Comments
Note on J41: Evaluators Comments
Note on E42: Evaluators Comments
Note on F42: Evaluators Comments
Note on G42: Evaluators Comments
Note on H42: Evaluators Comments
Note on I42: Evaluators Comments
Note on J42: Evaluators Comments
Note on E43: Evaluators Comments
Note on F43: Evaluators Comments
Note on G43: Evaluators Comments
Note on H43: Evaluators Comments
Note on I43: Evaluators Comments
Note on J43: Evaluators Comments
Note on E44: Evaluators Comments
Note on F44: Evaluators Comments
Note on G44: Evaluators Comments
Note on H44: Evaluators Comments
Note on I44: Evaluators Comments
Note on J44: Evaluators Comments
Note on E45: Evaluators Comments
Note on F45: Evaluators Comments
Note on G45: Evaluators Comments
Note on H45: Evaluators Comments
Note on I45: Evaluators Comments
Note on J45: Evaluators Comments
Note on E46: Evaluators Comments
Note on F46: Evaluators Comments
Note on G46: Evaluators Comments
Note on H46: Evaluators Comments
Note on I46: Evaluators Comments
Note on J46: Evaluators Comments
Note on E47: Evaluators Comments
Note on F47: Evaluators Comments
Note on G47: Evaluators Comments
Note on H47: Evaluators Comments
Note on I47: Evaluators Comments
Note on J47: Evaluators Comments
Note on E48: Evaluators Comments
Note on F48: Evaluators Comments
Note on G48: Evaluators Comments
Note on H48: Evaluators Comments
Note on I48: Evaluators Comments
Note on J48: Evaluators Comments
Note on E49: Evaluators Comments
Note on F49: Evaluators Comments
Note on G49: Evaluators Comments
Note on H49: Evaluators Comments
Note on I49: Evaluators Comments
Note on J49: Evaluators Comments
Note on E50: Evaluators Comments
Note on F50: Evaluators Comments
Note on G50: Evaluators Comments
Note on H50: Evaluators Comments
Note on I50: Evaluators Comments
Note on J50: Evaluators Comments
Note on E51: Evaluators Comments
Note on F51: Evaluators Comments
Note on G51: Evaluators Comments
Note on H51: Evaluators Comments
Note on I51: Evaluators Comments
Note on J51: Evaluators Comments
Note on E52: Evaluators Comments
Note on F52: Evaluators Comments
Note on G52: Evaluators Comments
Note on H52: Evaluators Comments
Note on I52: Evaluators Comments
Note on J52: Evaluators Comments
Note on E53: Evaluators Comments
Note on F53: Evaluators Comments
Note on G53: Evaluators Comments
Note on H53: Evaluators Comments
Note on I53: Evaluators Comments
Note on J53: Evaluators Comments
Note on E54: Evaluators Comments
Note on F54: Evaluators Comments
Note on G54: Evaluators Comments
Note on H54: Evaluators Comments
Note on I54: Evaluators Comments
Note on J54: Evaluators Comments
Note on E55: Evaluators Comments
Note on F55: Evaluators Comments
Note on G55: Evaluators Comments
Note on H55: Evaluators Comments
Note on I55: Evaluators Comments
Note on J55: Evaluators Comments
Note on E56: Evaluators Comments
Note on F56: Evaluators Comments
Note on G56: Evaluators Comments
Note on H56: Evaluators Comments
Note on I56: Evaluators Comments
Note on J56: Evaluators Comments
Note on E57: Evaluators Comments
Note on F57: Evaluators Comments
Note on G57: Evaluators Comments
Note on H57: Evaluators Comments
Note on I57: Evaluators Comments
Note on J57: Evaluators Comments
Note on E58: Evaluators Comments
Note on F58: Evaluators Comments
Note on G58: Evaluators Comments
Note on H58: Evaluators Comments
Note on I58: Evaluators Comments
Note on J58: Evaluators Comments
Note on E59: Evaluators Comments
Note on F59: Evaluators Comments
Note on G59: Evaluators Comments
Note on H59: Evaluators Comments
Note on I59: Evaluators Comments
Note on J59: Evaluators Comments
Note on E60: Evaluators Comments
Note on F60: Evaluators Comments
Note on G60: Evaluators Comments
Note on H60: Evaluators Comments
Note on I60: Evaluators Comments
Note on J60: Evaluators Comments
Note on E61: Evaluators Comments
Note on F61: Evaluators Comments
Note on G61: Evaluators Comments
Note on H61: Evaluators Comments
Note on I61: Evaluators Comments
Note on J61: Evaluators Comments
Note on E62: Evaluators Comments
Note on F62: Evaluators Comments
Note on G62: Evaluators Comments
Note on H62: Evaluators Comments
Note on I62: Evaluators Comments
Note on J62: Evaluators Comments
Note on E63: Evaluators Comments
Note on F63: Evaluators Comments
Note on G63: Evaluators Comments
Note on H63: Evaluators Comments
Note on I63: Evaluators Comments
Note on J63: Evaluators Comments
Note on E64: Evaluators Comments
Note on F64: Evaluators Comments
Note on G64: Evaluators Comments
Note on H64: Evaluators Comments
Note on I64: Evaluators Comments
Note on J64: Evaluators Comments
Note on E65: Evaluators Comments
Note on F65: Evaluators Comments
Note on G65: Evaluators Comments
Note on H65: Evaluators Comments
Note on I65: Evaluators Comments
Note on J65: Evaluators Comments
Note on E66: Evaluators Comments
Note on F66: Evaluators Comments
Note on G66: Evaluators Comments
Note on H66: Evaluators Comments
Note on I66: Evaluators Comments
Note on J66: Evaluators Comments
Note on E67: Evaluators Comments
Note on F67: Evaluators Comments
Note on G67: Evaluators Comments
Note on H67: Evaluators Comments
Note on I67: Evaluators Comments
Note on J67: Evaluators Comments
Note on E68: Evaluators Comments
Note on F68: Evaluators Comments
Note on G68: Evaluators Comments
Note on H68: Evaluators Comments
Note on I68: Evaluators Comments
Note on J68: Evaluators Comments
Note on E69: Evaluators Comments
Note on F69: Evaluators Comments
Note on G69: Evaluators Comments
Note on H69: Evaluators Comments
Note on I69: Evaluators Comments
Note on J69: Evaluators Comments
Note on E70: Evaluators Comments
Note on F70: Evaluators Comments
Note on G70: Evaluators Comments
Note on H70: Evaluators Comments
Note on I70: Evaluators Comments
Note on J70: Evaluators Comments
Note on E71: Evaluators Comments
Note on F71: Evaluators Comments
Note on G71: Evaluators Comments
Note on H71: Evaluators Comments
Note on I71: Evaluators Comments
Note on J71: Evaluators Comments
Note on E72: Evaluators Comments
Note on F72: Evaluators Comments
Note on G72: Evaluators Comments
Note on H72: Evaluators Comments
Note on I72: Evaluators Comments
Note on J72: Evaluators Comments
Note on E73: Evaluators Comments
Note on F73: Evaluators Comments
Note on G73: Evaluators Comments
Note on H73: Evaluators Comments
Note on I73: Evaluators Comments
Note on J73: Evaluators Comments
Note on E74: Evaluators Comments
Note on F74: Evaluators Comments
Note on G74: Evaluators Comments
Note on H74: Evaluators Comments
Note on I74: Evaluators Comments
Note on J74: Evaluators Comments
Note on E75: Evaluators Comments
Note on F75: Evaluators Comments
Note on G75: Evaluators Comments
Note on H75: Evaluators Comments
Note on I75: Evaluators Comments
Note on J75: Evaluators Comments
Note on E76: Evaluators Comments
Note on F76: Evaluators Comments
Note on G76: Evaluators Comments
Note on H76: Evaluators Comments
Note on I76: Evaluators Comments
Note on J76: Evaluators Comments
Note on E77: Evaluators Comments
Note on F77: Evaluators Comments
Note on G77: Evaluators Comments
Note on H77: Evaluators Comments
Note on I77: Evaluators Comments
Note on J77: Evaluators Comments
Note on E78: Evaluators Comments
Note on F78: Evaluators Comments
Note on G78: Evaluators Comments
Note on H78: Evaluators Comments
Note on I78: Evaluators Comments
Note on J78: Evaluators Comments
Note on E79: Evaluators Comments
Note on F79: Evaluators Comments
Note on G79: Evaluators Comments
Note on H79: Evaluators Comments
Note on I79: Evaluators Comments
Note on J79: Evaluators Comments
Note on E80: Evaluators Comments
Note on F80: Evaluators Comments
Note on G80: Evaluators Comments
Note on H80: Evaluators Comments
Note on I80: Evaluators Comments
Note on J80: Evaluators Comments
Note on E81: Evaluators Comments
Note on F81: Evaluators Comments
Note on G81: Evaluators Comments
Note on H81: Evaluators Comments
Note on I81: Evaluators Comments
Note on J81: Evaluators Comments
Note on E82: Evaluators Comments
Note on F82: Evaluators Comments
Note on G82: Evaluators Comments
Note on H82: Evaluators Comments
Note on I82: Evaluators Comments
Note on J82: Evaluators Comments
Note on E83: Evaluators Comments
Note on F83: Evaluators Comments
Note on G83: Evaluators Comments
Note on H83: Evaluators Comments
Note on I83: Evaluators Comments
Note on J83: Evaluators Comments
Note on E84: Evaluators Comments
Note on F84: Evaluators Comments
Note on G84: Evaluators Comments
Note on H84: Evaluators Comments
Note on I84: Evaluators Comments
Note on J84: Evaluators Comments
Note on E85: Evaluators Comments
Note on F85: Evaluators Comments
Note on G85: Evaluators Comments
Note on H85: Evaluators Comments
Note on I85: Evaluators Comments
Note on J85: Evaluators Comments
Note on E86: Evaluators Comments
Note on F86: Evaluators Comments
Note on G86: Evaluators Comments
Note on H86: Evaluators Comments
Note on I86: Evaluators Comments
Note on J86: Evaluators Comments
Note on E87: Evaluators Comments
Note on F87: Evaluators Comments
Note on G87: Evaluators Comments
Note on H87: Evaluators Comments
Note on I87: Evaluators Comments
Note on J87: Evaluators Comments
Note on E88: Evaluators Comments
Note on F88: Evaluators Comments
Note on G88: Evaluators Comments
Note on H88: Evaluators Comments
Note on I88: Evaluators Comments
Note on J88: Evaluators Comments
Note on E89: Evaluators Comments
Note on F89: Evaluators Comments
Note on G89: Evaluators Comments
Note on H89: Evaluators Comments
Note on I89: Evaluators Comments
Note on J89: Evaluators Comments
Note on E90: Evaluators Comments
Note on F90: Evaluators Comments
Note on G90: Evaluators Comments
Note on H90: Evaluators Comments
Note on I90: Evaluators Comments
Note on J90: Evaluators Comments
Note on E91: Evaluators Comments
Note on F91: Evaluators Comments
Note on G91: Evaluators Comments
Note on H91: Evaluators Comments
Note on I91: Evaluators Comments
Note on J91: Evaluators Comments
Note on E92: Evaluators Comments
Note on F92: Evaluators Comments
Note on G92: Evaluators Comments
Note on H92: Evaluators Comments
Note on I92: Evaluators Comments
Note on J92: Evaluators Comments
Note on E93: Evaluators Comments
Note on F93: Evaluators Comments
Note on G93: Evaluators Comments
Note on H93: Evaluators Comments
Note on I93: Evaluators Comments
Note on J93: Evaluators Comments
Note on E94: Evaluators Comments
Note on F94: Evaluators Comments
Note on G94: Evaluators Comments
Note on H94: Evaluators Comments
Note on I94: Evaluators Comments
Note on J94: Evaluators Comments
Note on E95: Evaluators Comments
Note on F95: Evaluators Comments
Note on G95: Evaluators Comments
Note on H95: Evaluators Comments
Note on I95: Evaluators Comments
Note on J95: Evaluators Comments
Note on E96: Evaluators Comments
Note on F96: Evaluators Comments
Note on G96: Evaluators Comments
Note on H96: Evaluators Comments
Note on I96: Evaluators Comments
Note on J96: Evaluators Comments
Note on E97: Evaluators Comments
Note on F97: Evaluators Comments
Note on G97: Evaluators Comments
Note on H97: Evaluators Comments
Note on I97: Evaluators Comments
Note on J97: Evaluators Comments
Note on E98: Evaluators Comments
Note on F98: Evaluators Comments
Note on G98: Evaluators Comments
Note on H98: Evaluators Comments
Note on I98: Evaluators Comments
Note on J98: Evaluators Comments
Note on E99: Evaluators Comments
Note on F99: Evaluators Comments
Note on G99: Evaluators Comments
Note on H99: Evaluators Comments
Note on I99: Evaluators Comments
Note on J99: Evaluators Comments
Note on E100: Evaluators Comments
Note on F100: Evaluators Comments
Note on G100: Evaluators Comments
Note on H100: Evaluators Comments
Note on I100: Evaluators Comments
Note on J100: Evaluators Comments
Note on E101: Evaluators Comments
Note on F101: Evaluators Comments
Note on G101: Evaluators Comments
Note on H101: Evaluators Comments
Note on I101: Evaluators Comments
Note on J101: Evaluators Comments
Note on E102: Evaluators Comments
Note on F102: Evaluators Comments
Note on G102: Evaluators Comments
Note on H102: Evaluators Comments
Note on I102: Evaluators Comments
Note on J102: Evaluators Comments
Note on E103: Evaluators Comments
Note on F103: Evaluators Comments
Note on G103: Evaluators Comments
Note on H103: Evaluators Comments
Note on I103: Evaluators Comments
Note on J103: Evaluators Comments
Note on E104: Evaluators Comments
Note on F104: Evaluators Comments
Note on G104: Evaluators Comments
Note on H104: Evaluators Comments
Note on I104: Evaluators Comments
Note on J104: Evaluators Comments
Note on E105: Evaluators Comments
Note on F105: Evaluators Comments
Note on G105: Evaluators Comments
Note on H105: Evaluators Comments
Note on I105: Evaluators Comments
Note on J105: Evaluators Comments
Note on E106: Evaluators Comments
Note on F106: Evaluators Comments
Note on G106: Evaluators Comments
Note on H106: Evaluators Comments
Note on I106: Evaluators Comments
Note on J106: Evaluators Comments
Note on E107: Evaluators Comments
Note on F107: Evaluators Comments
Note on G107: Evaluators Comments
Note on H107: Evaluators Comments
Note on I107: Evaluators Comments
Note on J107: Evaluators Comments
Note on E108: Evaluators Comments
Note on F108: Evaluators Comments
Note on G108: Evaluators Comments
Note on H108: Evaluators Comments
Note on I108: Evaluators Comments
Note on J108: Evaluators Comments
Note on E109: Evaluators Comments
Note on F109: Evaluators Comments
Note on G109: Evaluators Comments
Note on H109: Evaluators Comments
Note on I109: Evaluators Comments
Note on J109: Evaluators Comments
Note on E110: Evaluators Comments
Note on F110: Evaluators Comments
Note on G110: Evaluators Comments
Note on H110: Evaluators Comments
Note on I110: Evaluators Comments
Note on J110: Evaluators Comments
Note on E111: Evaluators Comments
Note on F111: Evaluators Comments
Note on G111: Evaluators Comments
Note on H111: Evaluators Comments
Note on I111: Evaluators Comments
Note on J111: Evaluators Comments
Note on E112: Evaluators Comments
Note on F112: Evaluators Comments
Note on G112: Evaluators Comments
Note on H112: Evaluators Comments
Note on I112: Evaluators Comments
Note on J112: Evaluators Comments
Note on E113: Evaluators Comments
Note on F113: Evaluators Comments
Note on G113: Evaluators Comments
Note on H113: Evaluators Comments
Note on I113: Evaluators Comments
Note on J113: Evaluators Comments
Note on E114: Evaluators Comments
Note on F114: Evaluators Comments
Note on G114: Evaluators Comments
Note on H114: Evaluators Comments
Note on I114: Evaluators Comments
Note on J114: Evaluators Comments
Note on E115: Evaluators Comments
Note on F115: Evaluators Comments
Note on G115: Evaluators Comments
Note on H115: Evaluators Comments
Note on I115: Evaluators Comments
Note on J115: Evaluators Comments
Note on E116: Evaluators Comments
Note on F116: Evaluators Comments
Note on G116: Evaluators Comments
Note on H116: Evaluators Comments
Note on I116: Evaluators Comments
Note on J116: Evaluators Comments
Note on E117: Evaluators Comments
Note on F117: Evaluators Comments
Note on G117: Evaluators Comments
Note on H117: Evaluators Comments
Note on I117: Evaluators Comments
Note on J117: Evaluators Comments
Note on E118: Evaluators Comments
Note on F118: Evaluators Comments
Note on G118: Evaluators Comments
Note on H118: Evaluators Comments
Note on I118: Evaluators Comments
Note on J118: Evaluators Comments
Note on E119: Evaluators Comments
Note on F119: Evaluators Comments
Note on G119: Evaluators Comments
Note on H119: Evaluators Comments
Note on I119: Evaluators Comments
Note on J119: Evaluators Comments
Note on E120: Evaluators Comments
Note on F120: Evaluators Comments
Note on G120: Evaluators Comments
Note on H120: Evaluators Comments
Note on I120: Evaluators Comments
Note on J120: Evaluators Comments
Note on E121: Evaluators Comments
Note on F121: Evaluators Comments
Note on G121: Evaluators Comments
Note on H121: Evaluators Comments
Note on I121: Evaluators Comments
Note on J121: Evaluators Comments
Note on E122: Evaluators Comments
Note on F122: Evaluators Comments
Note on G122: Evaluators Comments
Note on H122: Evaluators Comments
Note on I122: Evaluators Comments
Note on J122: Evaluators Comments
Note on E123: Evaluators Comments
Note on F123: Evaluators Comments
Note on G123: Evaluators Comments
Note on H123: Evaluators Comments
Note on I123: Evaluators Comments
Note on J123: Evaluators Comments
Note on E124: Evaluators Comments
Note on F124: Evaluators Comments
Note on G124: Evaluators Comments
Note on H124: Evaluators Comments
Note on I124: Evaluators Comments
Note on J124: Evaluators Comments
Note on E125: Evaluators Comments
Note on F125: Evaluators Comments
Note on G125: Evaluators Comments
Note on H125: Evaluators Comments
Note on I125: Evaluators Comments
Note on J125: Evaluators Comments
Note on E126: Evaluators Comments
Note on F126: Evaluators Comments
Note on G126: Evaluators Comments
Note on H126: Evaluators Comments
Note on I126: Evaluators Comments
Note on J126: Evaluators Comments
Note on E127: Evaluators Comments
Note on F127: Evaluators Comments
Note on G127: Evaluators Comments
Note on H127: Evaluators Comments
Note on I127: Evaluators Comments
Note on J127: Evaluators Comments