## General Requirements
| RFT Compliance Matrix |  |  |  | Reference Number | SF-CF-25
[5 empty] | Owner | PRO
[5 empty] | Revision Code | 3.0
[5 empty] | Implementation Date | 2024-03-01
Project Name:
Reference Number:
RFT Article (Part Number or Title) | Requirements (Description) | Killer | Fully Compliant | Partially Compliant | Non-Compliant | Reference (Specify document & page nb)
Article 4 | Conditions for the Participation of the Eligible Bidders
4.1 | 1- Bidders shall meet the following conditions, declared in accordance with the required documents in the First section of this Article mentioned below as (First: Envelope No. (1) Administrative Documents and Transactions):
a- That there is no proven violation, by the bidders, of professional ethics generally accepted and stipulated in the relevant provisions, if any;
b- Bidders have the legal capacity to enter into the procurement contract;
c- Bidders have fulfilled their obligations to pay taxes and social security contributions;
d- Bidders have not been convicted, neither their directors nor employees involved with the procurement process, by a court decision of any criminal offence - even if the verdict can still be appealed - related to their professional conduct or the making of false statements or misrepresentations as to their qualifications to enter into a procurement contract, or corrupting a public procurement or a contract awarding process, or have not been otherwise disqualified pursuant to administrative suspension or debarment proceedings, or have been in a situation of exclusion from participation in public procurements;
e- Bidders are not the subject of legal proceedings for insolvency or bankruptcy, or were declared bankrupt by a court of law;
f- Bidders have not been convicted by a court decision - even if the verdict can still be appealed - of usury or money laundering;
g- Bidders have not participated in the decision-making process of the contracting authority or have any conflict of interest, or any material interest linking them to any of the decision makers;
h- Any other conditions set forth by the contracting authority in the tender documents that are commensurate with the required works;
i- Certificate from the Ministry of Economy proving compliance with the provisions of the Law on Boycott of Israel for foreign companies (added by Law No. 309, dated April 19, 2023).
j- Declaration of the economic beneficiaries (according to Law No. 309, dated April 19, 2023).
4.2 | 2- The bid must be submitted clearly and unequivocally without any deletion, alteration, or modification.
4.3 | 3- The bidders state in their offer that they have reviewed the Tender document and its complementary documents and have obtained a copy. They accept and undertake to adhere to all the conditions outlined therein without any reservations or exceptions. The bidder submits their offer on this basis and affixes financial stamps worth fifty thousand Lebanese pounds covering all the documents.
4.4 | 4- Any bid containing reservations or exceptions is rejected.
4.5 | 5- The bidder mentions in their offer a clear address and place of residence for prompt communication.
Administrative Documents and Transactions | First: Envelope No. (1) Administrative Documents and Transactions
A- General Conditions:
1- Undertaking Letter (Declaration), according to the attached form, signed and stamped by the bidder, this Undertaking includes the bidder's confirmation of their commitment to the price and the validity of the offer. A financial stamp of 50,000 L.L. is affixed.
2- Commercial Circular specifying the authorized signatory of the bidder and a sample of their signature.
3- Legal Authorization: If the offer is signed by someone other than the person authorized to sign according to the commercial circular, it must be notarized by a notary public.
4- Police Record of the Authorized Signatory or his “legal representative”, not exceeding three months from the bid opening date.
5- Partnership Contract legalized by a notary public if required.
6- Registration Certificate before the Directorate of Value Added Tax, if applicable, or a certificate of non-registration if not subject to it. In the latter case, the bidder commits to their bid price even if they become registered for VAT during the execution period.
7- Registration Certificate issued by the Ministry of Finance – Department of Revenue.
8- Certificate issued by the Ministry of Finance proving the bidder's compliance with tax obligations.
9- Clearance Certificate from the National Social Security Fund “comprehensive or valid for participation in public tenders and bids” valid on the date of the bid opening session, stating that the bidder has paid all his subscriptions (the bidder must be registered before the National Social Security Fund and any statement mentioning the phrase “unregistered institution” will be rejected).
10- Certificate issued by the Municipality, proving full payment of municipal fees by the bidder, issued by the municipality within its jurisdiction based on the commercial registration certificate.
11- Comprehensive Certificate issued by the Commercial Register showing founders, members, contributors, or partners, authorized signatories, the manager, capital, the bidder's activity, and ongoing liabilities.
12- Certificate issued by the relevant authorities proving that the bidder is not in a state of bankruptcy.
13- Certificate issued by the relevant authorities proving that the bidder is not in a state of judicial liquidation.
14- Bid bond as required in the specific Tender document of the procurement project, in accordance with Articles 34 and 36 of the Public Procurement Law.
15- Declaration from the Bidder identifying the economic beneficiary/beneficiaries according to Form M18 issued by the Ministry of Finance (any natural person who owns or effectively controls the ultimate outcome of the activity practiced by the bidder, either directly or indirectly, whether the bidder is a natural person or a legal entity.)
16- Copies of Identification Cards (ID/Passport) for the economic beneficiary/beneficiaries.
17- Copies of Identification Cards (ID/Passport) for each person representing the bidder (those acting on behalf of the bidder in their relationship with the contracting authority: legal representative, representative of the legal entity, or authorized signatory).
18- Integrity Declaration Document signed by the bidder in accordance with the prescribed format
Miscellaneous | The bidder shall declare any relative relations with any Alfa employee up to the 4th degree under Clause 30 of the PPL, for MIC1 to be able to assess the existing of any potential conflict of interests which may lead to deprive the bidder from participating to the tender under the risk of disqualification.
The bidder or any of his employees, partners, agents, contributors, consultants, or their relatives shall declare any relationships that may lead to a conflict of interest in the subject of this contract.
Special Conditions | B- Special Conditions Regarding the Subject of the Contract:
Financial Qualifications | 1- Financial Qualifications (To be determined based on the size and nature of the contract).
Technical/Professional Qualifications | 2- Technical/Professional Qualifications (To be determined based on the nature of the contract):
1- Certificate from the Chamber of Commerce, Industry, and Agriculture confirming that the bidder is engaged in the activities related to the subject of the contract, valid as of the date of the bidding session and valid for participation in public tenders.
2- Clearance certificate from the Order of Engineers…
3- Clearance certificate from the Contractors Syndicate…
4- ISO certificate.
5- Five Certificates of good execution and completion for similar projects in terms of size and type.
6- Technical proposal according to the required specifications in the appendix (1) of the RFT.
7- Declaration of site inspection by the bidder, denying any unfamiliarity, according to the attached model.
Participation of a foreign bidder | C- In case of the participation of a foreign bidder, the bidder must comply with one of the following conditions:
1- is part of a coalition that includes at least one Lebanese company that meets the conditions required by the specific Tender document of the procurement project.
2- The personal presence of the legal representative of the company to participate in the procurement proceedings (not mandatory).
3- Has an authorized agent or representative in Lebanon responsible for signing the contract on its behalf.
In addition to the above conditions, the foreign bidder must submit the following:
1- Certificate registration of the company or certificate of establishment issued by the relevant authorities in their country.
2- Certificate from the Lebanese Ministry of Economy and Trade confirming compliance with the provisions of the Law on Israel Boycott.
3- The required certificates according to paragraph (First) above, according to the laws of the country where the bidder is located, provided that these certificates are authenticated according to the regulations of the competent authorities.
For certificates issued without an expiration date, the validity date of each certificate is determined according to its nature, not exceeding six months from the date of the bid opening session.
Information Security Specifications | Information Security Specifications Issuing Department to determine whether all or part of this Article is applicable to their specific RFT
The Bidder shall commit to refrain from offering any product / equipment which can cause security threat or information leakage that jeopardizes MIC1 network security. (K)
The Bidder shall accept that MIC1 runs a vulnerability scan on the proposed solution prior to issuing the acceptance and in case any vulnerability is found, the Bidder undertakes to take the necessary actions to remedy such vulnerability within _____________________ days from its notification.
The Bidder shall mention the security standards adopted/followed in designing the proposed solution.
The Bidder should specify if it has acquired the ISO27001 certification or any other equivalent security certification and submit with the Offer a copy of such certificate.
The Bidder shall not hard code passwords in the proposed solution.
The provided application should run without the need of root (unix) and / or admin (win) privileges.
Source code of proposed application should be owned by MIC1.
System shall allow generation of user, operator as well as alarms logs.
Solution and storage shall be sized to host history logs for at least 1 year back.
The Bidder should submit a data flow diagram and schema of the solution architecture.
In case of online payment, the Bidder shall use encryption. (K)
The Bidder shall harden systems servers / storage before being published online, and describe hardening aspects applied on each type.
The Bidder shall describe security checking and audits performed on the designed solution prior to putting it on the market.
The Bidder shall change default errors / messages and configuration.
Application should support role-based access, specific privileges per user (i.e specific access to application modules and reports)
Database should support restricted access per user or groups to data (i.e access per field or per table, …)
Encryption shall be used in all communications / interactions between systems, especially if the communication is through web access. Web based access shall always be used through HTTP+SSL.
Each user shall have only one account / profile to access data.
Least-privileges should always be specified on nodes / applications.
Pseudocode flow chart shall be provided by the Bidders.
The Bidder should commit to improve solution / systems information security weaknesses whenever needed or highlighted by MIC1 information security team.
Health, Safety and Environmental Specifications | To ensure that the proposed products and services bidders are compliant with HSE culture, bidders should state basic HSE specifications and compliance information:
Bidder shall provide the product’s specifications that have an environmental impact (power consumption, gas emissions, etc…)
Bidder shall provide the product specifications that contribute into preserving the environment (made of recycled material, ozone friendly, low volatile organic compounds, etc…)
Bidder shall provide the product’s specifications that contribute towards the health and safety of the users (ergonomic design, safety features, etc)
Bidder shall state the safety measures being followed by personnel performing the work on Alfa’s sites (ISO45001 certification, specific best practices, etc…).
Bidder shall provide the product’s life cycle data if available.

## Technical Requirements
| RFT Compliance Matrix |  |  |  | Reference Number | SF-CF-25
[5 empty] | Owner | PRO
[5 empty] | Revision Code | 3.0
[5 empty] | Implementation Date | 2024-03-01
Project Name: | JDEIDET DATA CENTER
Reference Number: | 26 05 53 - Identification for Electrical Systems - 10.2023
RFT Article (Part Number or Title) | Requirements (Description) | Killer | Fully Compliant | Partially Compliant | Non-Compliant | Reference (Specify document & page nb)
1 GENERAL
1.1 SUMMARY
A. Identification for electrical systems, equipment, conduit and related components.
1.2 REFERENCES
A. American National Standards Institute (ANSI) Publications:
1. ANSI/ASME A13.1 - Scheme for the Identification of Piping Systems
2. ANSI Z535.4 - Safety Labels Construction
B. Institute of Electrical and Electronics Engineers (IEEE) Publications
1. C2 - ASC C2 Eighth Interim Collection of the National Electrical Safety Code”
C. National Fire Protection Association (NFPA) Publications:
1. 70 - National Electric Code
D. Occupational Safety and Health Standards - Code of Federal Regulations (CFR)
1. 1910.144 - Safety color code for marking physical hazards
2. 1910.145 - Specifications for accident prevention signs and tags
E. Underwriters Laboratories
1. UL 969 - Standard for Marking and Labeling Systems
1.3 SUBMITTALS
A. Product Data: For each electrical identification product indicated.
B. Include construction details, material descriptions, dimensions of individual components and profiles, and finishes for electrical identification products.
1.4 WARRANTY
A. Equipment
1. The supplied products shall be covered by full supplier warranty for a minimum period of one (1) year from delivery to site at a full repair and replacement service.
2. Warranty shall include all defected spare parts and workmanship.
2 PRODUCTS
2.1 PERFORMANCE REQUIREMENTS
A. Comply with ASME A13.1 and IEEE C2.
B. Comply with NFPA 70.
C. Comply with 29 CFR 1910.144 and 29 CFR 1910.145.
D. Comply with ANSI Z535.4 for safety signs and labels.
E. Adhesive-attached labeling materials, including label stocks, laminating adhesives, and inks used by label printers, shall comply with UL 969.
F. Thermal Movements: Allow for thermal movements from ambient and surface temperature changes.
1. Temperature Change: 50 °C ambient; 85°C material surfaces.
2.2 COLOR AND LEGEND REQUIREMENTS
A. Raceways and Cables Carrying Circuits at More Than 600 V:
1. Black letters on an orange field.
2. Legend: "DANGER - CONCEALED HIGH VOLTAGE WIRING."
B. Raceways and Cables Carrying Circuits at 600 V or Less:
1. Black letters on an orange field.
2. Legend: Indicate voltage and system or service type.
C. Warning labels and signs shall include, but are not limited to, the following legends:
1. Multiple Power Source Warning: "DANGER - ELECTRICAL SHOCK HAZARD - EQUIPMENT HAS MULTIPLE POWER SOURCES."
2. Workspace Clearance Warning: "WARNING - OSHA REGULATION - AREA IN FRONT OF ELECTRICAL EQUIPMENT MUST BE KEPT CLEAR FOR 100 CM."
3. Arc Flash Warning: As required by the arc flash study.
2.3 LABELS
A. Vinyl Labels for Raceways Carrying Circuits at 600 V or Less: Preprinted, flexible labels laminated with a clear, weather- and chemical-resistant coating and matching wrap-around clear adhesive tape for securing label ends.
1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:
a. Brady Corporation
b. Champion America
c. Emedco
d. Grafoplast Wire Markers
e. LEM Products Inc.
f. Marking Services, Inc.
g. Panduit Corporation
h. or Equivalent
B. Snap-Around Labels for Raceways and Cables Carrying Circuits at 600 V or Less: Slit, pre-tensioned, flexible, preprinted, color-coded acrylic sleeves, with diameters sized to suit diameters of raceways they identify, and that stay in place by gripping action.
1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:
a. Brady Corporation
b. Marking Services, Inc.
c. Panduit Corp.
d. or Equivalent
C. Self-Adhesive Labels:
1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:
a. Brady Corporation.
b. Brother International Corporation
c. Emedco
d. Grafoplast Wire Markers
e. Ideal Industries, Inc.
f. LEM Products Inc.
g. Marking Services, Inc.
h. Panduit Corp.
i. or Equivalent
2. Preprinted or Write-on, 0.08 mm thick, polyester or vinyl flexible label with acrylic pressure-sensitive adhesive.
a. Self-Lamination: Clear; UV-, weather- and chemical-resistant; self-laminating, protective shield over the legend. Labels sized to fit the cable and raceway diameter, such that the clear shield overlaps the entire printed legend.
3. Vinyl, thermal, transfer-printed, 0.08 mm thick, multicolor, weather- and UV-resistant, pressure-sensitive adhesive labels, configured for display on front cover, door, or other access to equipment unless otherwise indicated.
a. Nominal Size: 8 by 12 cm
4. Marker for Tags: Machine-printed, permanent, waterproof, black ink recommended by printer manufacturer.
2.4 BANDS AND TUBES
A. Snap-Around, Color-Coding Bands for Raceways and Cables: Slit, pre-tensioned, flexible, solid colored acrylic sleeves, 5 cm long, with diameters sized to suit diameters of raceways or cables they identify, and that stay in place by gripping action.
1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:
a. Brady Corporation
b. Marking Services, Inc.
c. or Equivalent
B. Heat-Shrink Preprinted Tubes: Flame-retardant polyolefin tubes with machine-printed identification labels, sized to suit diameters of and shrunk to fit firmly around cables they identify. Full shrink recovery occurs at a maximum of 90°C. Comply with UL 224.
1. Manufacturers: Subject to compliance with requirements, provide products by the following:
a. Brady Corporation
b. 3M
c. or Equivalent
2.5 TAPES AND STENCILS
A. Marker Tapes: Vinyl or vinyl-cloth, self-adhesive wraparound type, with circuit identification legend machine printed by thermal transfer or equivalent process.
1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:
a. Carlton Industries, LP.
b. Champion America.
c. Ideal Industries, Inc.
d. Marking Services, Inc.
e. or Equivalent
B. Self-Adhesive Vinyl Tape: Colored, heavy duty, waterproof, fade resistant; not less than 0.08 mm thick by 2.5 to 5 cm wide; compounded for outdoor use.
1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:
a. Brady Corporation
b. Carlton Industries, LP.
c. Emedco
d. or Equivalent
C. Tape and Stencil for Raceways Carrying Circuits 600 V or Less: 10 cm wide black stripes on 25cm centers placed diagonally over orange background that extends full length of raceway or duct and is 30 cm wide. Stop stripes at legends.
1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:
a. LEM Products Inc.
b. Marking Services, Inc.
c. or Equivalent
D. Floor Marking Tape: 5 cm wide, 0.13 mm pressure-sensitive vinyl tape, with yellow and black stripes and clear vinyl overlay.
E. Underground-Line Warning Tape
1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:
a. Brady Corporation.
b. Ideal Industries, Inc.
c. LEM Products Inc.
d. Marking Services, Inc.
e. Reef Industries, Inc.
f. or Equivalent
2. Tape:
a. Recommended by manufacturer for the method of installation and suitable to identify and locate underground electrical and communications utility lines.
b. Printing on tape shall be permanent and shall not be damaged by burial operations.
c. Tape material and ink shall be chemically inert and not subject to degradation when exposed to acids, alkalis, and other destructive substances commonly found in soils.
3. Color and Printing:
a. Comply with ANSI Z535.1, ANSI Z535.2, ANSI Z535.3, ANSI Z535.4, and ANSI Z535.5.
b. Inscriptions for Red-Colored Tapes: "ELECTRIC LINE, HIGH VOLTAGE".
c. Inscriptions for Orange-Colored Tapes: "TELEPHONE CABLE, CATV CABLE, COMMUNICATIONS CABLE, OPTICAL FIBER CABLE".
F. Stenciled Legend: In nonfading, waterproof, black ink or paint. Minimum letter height shall be 2.5cm.
2.6 TAGS
A. Metal Tags: Brass or aluminum, height 5 and thickness 0.13 cm, with engraved or stamped legend, punched for use with self-locking cable tie fastener.
B. Nonmetallic Preprinted Tags: Polyethylene tags, 0.4 mm thick, color-coded for phase and voltage level, with factory screened or printed permanent designations; punched for use with self-locking cable tie fastener.
C. Write-On Tags:
1. Manufacturers: Subject to compliance with requirements, provide products by one of the following:
a. Carlton Industries, LP.
b. LEM Products Inc.
c. or Equivalent
2. Polyester Tags 0.4 mm thick, with corrosion-resistant grommet and cable tie for attachment to raceway, conductor, or cable.
3. Marker for Tags: Permanent, waterproof, black ink marker recommended by tag manufacturer.
2.7 SIGNS
A. Baked-Enamel Signs:
1. Preprinted aluminum signs, punched or drilled for fasteners, with colors, legend, and size required for application.
2. 65 mm grommets in corners for mounting.
3. Nominal Size: 18 by 25 cm
B. Metal-Backed Butyrate Signs:
1. Weather-resistant, nonfading, preprinted, cellulose-acetate butyrate signs, with 1 mm galvanized-steel backing and with colors, legend, and size required for application.
2. 65 mm grommets in corners for mounting.
3. Nominal Size: 25 by 35 cm
C. Laminated Acrylic or Melamine Plastic Signs:
1. Engraved legend.
2. Thickness:
a. For signs up to 130 cm², minimum 1.6 mm.
b. For signs larger than 130 cm², 3.2 mm thick.
c. Engraved legend with black letters on white face.
d. Punched or drilled for mechanical fasteners.
e. Framed with mitered acrylic molding and arranged for attachment at applicable equipment.
2.8 CABLE TIES
A. General-Purpose Cable Ties: Fungus inert, self-extinguishing, one piece, self-locking, Type 6/6 nylon.
1. Minimum Width: 5 mm
2. Tensile Strength at 22°C according to ASTM D 638: 12,000 psi.
3. Temperature Range: -10° to +85° Celsius
4. Color: Black, except where used for color-coding
B. UV-Stabilized Cable Ties: Fungus inert, designed for continuous exposure to exterior sunlight, self-extinguishing, one piece, self-locking, Type 6/6 nylon.
1. Minimum Width: 9 mm
2. Tensile Strength: 25 kg minimum.
3. Temperature Range: -10° to +85° Celsius
4. Color: Black
C. Plenum-Rated Cable Ties: Self-extinguishing, UV stabilized, one piece, self-locking.
1. Minimum Width: 9 mm
2. Tensile Strength at 22°C according to ASTM D 638: 480 Bar.
3. UL 94 Flame Rating: 94V-0
4. Temperature Range: -10° to +140° Celsius
5. Color: Black
2.9 MISCELLANEOUS IDENTIFICATION PRODUCTS
A. Paint: Comply with requirements in painting Sections for paint materials and application requirements. Retain paint system applicable for surface material and location (exterior or interior).
B. Fasteners for Labels and Signs: Self-tapping, stainless-steel screws or stainless-steel machine screws with nuts, flat, and lock washers.
3 EXECUTION
3.1 PREPARATION
A. Self-Adhesive Identification Products: Before applying electrical identification products, clean substrates of substances that could impair bond, using materials and methods recommended by manufacturer of identification product.
3.2 INSTALLATION
A. Verify and coordinate identification names, abbreviations, colors, and other features with requirements in other Sections requiring identification applications, Drawings, Shop Drawings, manufacturer's wiring diagrams, and operation and maintenance manual. Use consistent designations throughout Project.
B. Install identifying devices before installing acoustical ceilings and similar concealment.
C. Verify identity of each item before installing identification products.
D. Install identification materials and devices at locations for most convenient viewing without interference with operation and maintenance of equipment. Install access doors or panels to provide view of identifying devices.
E. Apply identification devices to surfaces that require finish after completing finish work.
F. Attach signs and plastic labels that are not self-adhesive type with mechanical fasteners appropriate to the location and substrate.
G. Cable Ties: For attaching tags. Use general-purpose type, except as listed below:
1. Outdoors: UV-stabilized nylon.
2. In Spaces Handling Environmental Air: Plenum rated.
H. Painted Identification: Comply with requirements in painting Sections for surface preparation and paint application.
I. Aluminum Wraparound Marker Labels and Metal Tags: Secure tight to surface of conductor or cable at a location with high visibility and accessibility.
J. System Identification Color-Coding Bands for Raceways and Cables: Each color-coding band shall completely encircle cable or conduit. Place adjacent bands of two-color markings in contact, side by side. Locate bands at changes in direction, at penetrations of walls and floors, at 15m maximum intervals in straight runs, and at 75m maximum intervals in congested areas.
K. During backfilling of trenches, install continuous underground-line warning tape directly above cable or raceway at 15 to 20 cm below finished grade. Use multiple tapes where width of multiple lines installed in a common trench or concrete envelope exceeds 40m overall.
3.3 IDENTIFICATION SCHEDULE
A. Concealed Raceways, Duct Banks, More Than 600 V, within Buildings: Tape and stencil 10cm wide black stripes on 25cm centers over orange background that extends full length of raceway or duct and is 30cm wide. Stencil legend "DANGER CONCEALED HIGH VOLTAGE WIRING" with 7.5cm high black letters on 50cm centers. Stop stripes at legends. Apply stripes to the following finished surfaces:
1. Floor surface directly above conduits running beneath and within 30cm of a floor that is in contact with earth or is framed above unexcavated space.
2. Wall surfaces directly external to raceways concealed within wall.
3. Accessible surfaces of concrete envelope around raceways in vertical shafts, exposed in the building, or concealed above suspended ceilings.
B. Accessible Raceways, Armored and Metal-Clad Cables, More Than 600 V: Self-adhesive vinyl labels. Install labels 10m maximum intervals.
C. Accessible Raceways and Metal-Clad Cables, 600 V or Less, for Service, Feeder, and Branch Circuits, More Than 30 A and 220 V to Ground: Identify with self-adhesive vinyl label. Install labels at 30m maximum intervals.
D. Accessible Raceways and Cables within Buildings: Identify the covers of each junction and pull box of the following systems with self-adhesive vinyl labels containing the wiring system legend and system voltage. System legends shall be as follows:
1. “EMERGENCY POWER”
2. “POWER”
3. “UPS”
4. “CONTROLS”
5. “DATA”
E. Power-Circuit Conductor Identification, 600 V or Less: For conductors in vaults, pull and junction boxes, manholes, and hand holes, use color-coding conductor tape to identify the phase.
1. 1. Color-Coding for Phase- and Voltage-Level Identification, 600 V or Less: Use colors listed below for ungrounded service feeder and branch-circuit conductors.
a. Color shall be factory applied or field applied for sizes larger than No. 8 AWG if authorities having jurisdiction permit.
b. Colors for 380/220-V Circuits:
1) Phase L1: Red
2) Phase L2: Yellow
3) Phase L3: Blue
c. Field-Applied, Color-Coding Conductor Tape: Apply in half-lapped turns for a minimum distance of 12cm from terminal points and in boxes where splices or taps are made. Apply last two turns of tape with no tension to prevent possible unwinding. Locate bands to avoid obscuring factory cable markings.
F. Power-Circuit Conductor Identification, More Than 600 V: For conductors in vaults, pull and junction boxes, manholes, and hand holes, use nonmetallic preprinted tags colored and marked to indicate phase, and a separate tag with the circuit designation.
G. Install instructional sign, including the color code for grounded and ungrounded conductors using adhesive-film-type labels.
H. Control-Circuit Conductor Identification: For conductors and cables in pull and junction boxes, manholes, and hand holes, use self-adhesive, self-laminating polyester labels with the conductor or cable designation, origin, and destination.
I. Control-Circuit Conductor Termination Identification: For identification at terminations, provide heat-shrink preprinted tubes with the conductor designation.
J. Conductors To Be Extended in the Future: Attach marker tape to conductors and list source.
K. Auxiliary Electrical Systems Conductor Identification: Identify field-installed alarm, control, and signal connections.
1. Identify conductors, cables, and terminals in enclosures and at junctions, terminals, and pull points. Identify by system and circuit designation.
2. Use system of marker-tape designations that is uniform and consistent with system used by manufacturer for factory-installed connections.
3. Coordinate identification with Project Drawings, manufacturer's wiring diagrams, and operation and maintenance manual.
L. Locations of Underground Lines: Identify with underground-line warning tape for power, lighting, communication, and control wiring and optical-fiber cable.
1. Limit use of underground-line warning tape to direct-buried cables.
2. Install underground-line warning tape for direct-buried cables and cables in raceways.
M. Workspace Indication: Install floor marking tape to show working clearances in the direction of access to live parts. Workspace shall comply with NFPA 70 and 29 CFR 1926.403 unless otherwise indicated. Do not install at flush-mounted panel boards and similar equipment in finished spaces.
N. Warning Labels for Indoor Cabinets, Boxes, and Enclosures for Power and Lighting: Self-adhesive warning labels.
1. Comply with 29 CFR 1910.145.
2. Identify system voltage with black letters on an orange background.
3. Apply to exterior of door, cover, or other access.
4. For equipment with multiple power or control sources, apply to door or cover of equipment, including, but not limited to, the following:
a. Power-transfer switches
b. Controls with external control power connections
O. Arc Flash Warning Labeling: Self-adhesive thermal transfer vinyl labels comply with NFPA 70E and ANSI Z535.4.
P. Operating Instruction Signs: Install instruction signs to facilitate proper operation and maintenance of electrical systems and items to which they connect. Install instruction signs with approved legend where instructions are needed for system or equipment operation.
Q. Emergency Operating Instruction Signs: Install instruction signs with white legend on a red background with minimum 1cm high letters for emergency instructions at equipment used for power transfer.
R. Equipment Identification Labels: On each unit of equipment, install unique designation label that is consistent with wiring diagrams, schedules, and operation and maintenance manual.
S. Apply labels to disconnect switches and protection equipment, central or master units, control panels, control stations, terminal cabinets, and racks of each system. Systems include power, lighting, control, communication, signal, monitoring, and alarm unless equipment is provided with its own identification.
1. Labeling Instructions:
a. Indoor Equipment: Self-adhesive, engraved, laminated acrylic or melamine plastic label. Unless otherwise indicated, provide a single line of text with 1.5cm high letters on 4cm high label; where two lines of text are required, use labels 5cm high.
b. Outdoor Equipment: Engraved, laminated acrylic or melamine label Stenciled legend 10cm high.
c. Elevated Components: Increase sizes of labels and letters to those appropriate for viewing from the floor.
d. Unless labels are provided with self-adhesive means of attachment, fasten them with appropriate mechanical fasteners that do not change the NEMA or NRTL rating of the enclosure.
2. Equipment To Be Labeled:
a. Panel boards: Typewritten directory of circuits in the location provided by panel board manufacturer. Panel board identification shall be in the form of a self-adhesive, engraved, laminated acrylic or melamine label.
b. Enclosures and electrical cabinets.
c. Access doors and panels for concealed electrical items.
d. Switchgear
e. Switchboards
f. Transformers: Label that includes tag designation shown on Drawings for the transformer, feeder, and panel boards or equipment supplied by the secondary.
g. Substations
h. Emergency system boxes and enclosures.
i. Motor-control centers
j. Enclosed switches
k. Enclosed circuit breakers
l. Enclosed controllers
m. Variable-speed controllers
n. Push-button stations
o. Power-transfer equipment
p. Contactors
q. Remote-controlled switches, dimmer modules, and control devices.
r. Battery-inverter units
s. Battery racks
t. Power-generating units
u. Monitoring and control equipment
v. UPS equipment
END OF SECTION

## Grade of Compliancy
| RFT Compliance Matrix | Reference Number | SF-CF-25
|  | Owner | PRO
|  | Revision Code | 3.0
|  | Implementation Date | 2024-03-01
Grade of Compliance range from 0 to 15 with a step of 1 unit:
15 : Compliant with additional value, not initially included in the requirements
10 : Fully compliant
4 - 5 - 6: Partially compliant
0 : Not compliant
K : Disqualification