## General Requirements
| RFT Compliance Matrix |  |  |  | Reference Number | SF-CF-25
[5 empty] | Owner | PRO
[5 empty] | Revision Code | 3.0
[5 empty] | Implementation Date | 2024-03-01
Project Name:
Reference Number:
RFT Article (Part Number or Title) | Requirements (Description) | Killer | Fully Compliant | Partially Compliant | Non-Compliant | Reference (Specify document & page nb)
Article 4 | Conditions for the Participation of the Eligible Bidders
4.1 | 1- Bidders shall meet the following conditions, declared in accordance with the required documents in the First section of this Article mentioned below as (First: Envelope No. (1) Administrative Documents and Transactions):
a- That there is no proven violation, by the bidders, of professional ethics generally accepted and stipulated in the relevant provisions, if any;
b- Bidders have the legal capacity to enter into the procurement contract;
c- Bidders have fulfilled their obligations to pay taxes and social security contributions;
d- Bidders have not been convicted, neither their directors nor employees involved with the procurement process, by a court decision of any criminal offence - even if the verdict can still be appealed - related to their professional conduct or the making of false statements or misrepresentations as to their qualifications to enter into a procurement contract, or corrupting a public procurement or a contract awarding process, or have not been otherwise disqualified pursuant to administrative suspension or debarment proceedings, or have been in a situation of exclusion from participation in public procurements;
e- Bidders are not the subject of legal proceedings for insolvency or bankruptcy, or were declared bankrupt by a court of law;
f- Bidders have not been convicted by a court decision - even if the verdict can still be appealed - of usury or money laundering;
g- Bidders have not participated in the decision-making process of the contracting authority or have any conflict of interest, or any material interest linking them to any of the decision makers;
h- Any other conditions set forth by the contracting authority in the tender documents that are commensurate with the required works;
i- Certificate from the Ministry of Economy proving compliance with the provisions of the Law on Boycott of Israel for foreign companies (added by Law No. 309, dated April 19, 2023).
j- Declaration of the economic beneficiaries (according to Law No. 309, dated April 19, 2023).
4.2 | 2- The bid must be submitted clearly and unequivocally without any deletion, alteration, or modification.
4.3 | 3- The bidders state in their offer that they have reviewed the Tender document and its complementary documents and have obtained a copy. They accept and undertake to adhere to all the conditions outlined therein without any reservations or exceptions. The bidder submits their offer on this basis and affixes financial stamps worth fifty thousand Lebanese pounds covering all the documents.
4.4 | 4- Any bid containing reservations or exceptions is rejected.
4.5 | 5- The bidder mentions in their offer a clear address and place of residence for prompt communication.
Administrative Documents and Transactions | First: Envelope No. (1) Administrative Documents and Transactions
A- General Conditions:
1- Undertaking Letter (Declaration), according to the attached form, signed and stamped by the bidder, this Undertaking includes the bidder's confirmation of their commitment to the price and the validity of the offer. A financial stamp of 50,000 L.L. is affixed.
2- Commercial Circular specifying the authorized signatory of the bidder and a sample of their signature.
3- Legal Authorization: If the offer is signed by someone other than the person authorized to sign according to the commercial circular, it must be notarized by a notary public.
4- Police Record of the Authorized Signatory or his “legal representative”, not exceeding three months from the bid opening date.
5- Partnership Contract legalized by a notary public if required.
6- Registration Certificate before the Directorate of Value Added Tax, if applicable, or a certificate of non-registration if not subject to it. In the latter case, the bidder commits to their bid price even if they become registered for VAT during the execution period.
7- Registration Certificate issued by the Ministry of Finance – Department of Revenue.
8- Certificate issued by the Ministry of Finance proving the bidder's compliance with tax obligations.
9- Clearance Certificate from the National Social Security Fund “comprehensive or valid for participation in public tenders and bids” valid on the date of the bid opening session, stating that the bidder has paid all his subscriptions (the bidder must be registered before the National Social Security Fund and any statement mentioning the phrase “unregistered institution” will be rejected).
10- Certificate issued by the Municipality, proving full payment of municipal fees by the bidder, issued by the municipality within its jurisdiction based on the commercial registration certificate.
11- Comprehensive Certificate issued by the Commercial Register showing founders, members, contributors, or partners, authorized signatories, the manager, capital, the bidder's activity, and ongoing liabilities.
12- Certificate issued by the relevant authorities proving that the bidder is not in a state of bankruptcy.
13- Certificate issued by the relevant authorities proving that the bidder is not in a state of judicial liquidation.
14- Bid bond as required in the specific Tender document of the procurement project, in accordance with Articles 34 and 36 of the Public Procurement Law.
15- Declaration from the Bidder identifying the economic beneficiary/beneficiaries according to Form M18 issued by the Ministry of Finance (any natural person who owns or effectively controls the ultimate outcome of the activity practiced by the bidder, either directly or indirectly, whether the bidder is a natural person or a legal entity.)
16- Copies of Identification Cards (ID/Passport) for the economic beneficiary/beneficiaries.
17- Copies of Identification Cards (ID/Passport) for each person representing the bidder (those acting on behalf of the bidder in their relationship with the contracting authority: legal representative, representative of the legal entity, or authorized signatory).
18- Integrity Declaration Document signed by the bidder in accordance with the prescribed format
Miscellaneous | The bidder shall declare any relative relations with any Alfa employee up to the 4th degree under Clause 30 of the PPL, for MIC1 to be able to assess the existing of any potential conflict of interests which may lead to deprive the bidder from participating to the tender under the risk of disqualification.
The bidder or any of his employees, partners, agents, contributors, consultants, or their relatives shall declare any relationships that may lead to a conflict of interest in the subject of this contract.
Special Conditions | B- Special Conditions Regarding the Subject of the Contract:
Financial Qualifications | 1- Financial Qualifications (To be determined based on the size and nature of the contract).
Technical/Professional Qualifications | 2- Technical/Professional Qualifications (To be determined based on the nature of the contract):
1- Certificate from the Chamber of Commerce, Industry, and Agriculture confirming that the bidder is engaged in the activities related to the subject of the contract, valid as of the date of the bidding session and valid for participation in public tenders.
2- Clearance certificate from the Order of Engineers…
3- Clearance certificate from the Contractors Syndicate…
4- ISO certificate.
5- Five Certificates of good execution and completion for similar projects in terms of size and type.
6- Technical proposal according to the required specifications in the appendix (1) of the RFT.
7- Declaration of site inspection by the bidder, denying any unfamiliarity, according to the attached model.
Participation of a foreign bidder | C- In case of the participation of a foreign bidder, the bidder must comply with one of the following conditions:
1- is part of a coalition that includes at least one Lebanese company that meets the conditions required by the specific Tender document of the procurement project.
2- The personal presence of the legal representative of the company to participate in the procurement proceedings (not mandatory).
3- Has an authorized agent or representative in Lebanon responsible for signing the contract on its behalf.
In addition to the above conditions, the foreign bidder must submit the following:
1- Certificate registration of the company or certificate of establishment issued by the relevant authorities in their country.
2- Certificate from the Lebanese Ministry of Economy and Trade confirming compliance with the provisions of the Law on Israel Boycott.
3- The required certificates according to paragraph (First) above, according to the laws of the country where the bidder is located, provided that these certificates are authenticated according to the regulations of the competent authorities.
For certificates issued without an expiration date, the validity date of each certificate is determined according to its nature, not exceeding six months from the date of the bid opening session.
Information Security Specifications | Information Security Specifications Issuing Department to determine whether all or part of this Article is applicable to their specific RFT
The Bidder shall commit to refrain from offering any product / equipment which can cause security threat or information leakage that jeopardizes MIC1 network security. (K)
The Bidder shall accept that MIC1 runs a vulnerability scan on the proposed solution prior to issuing the acceptance and in case any vulnerability is found, the Bidder undertakes to take the necessary actions to remedy such vulnerability within _____________________ days from its notification.
The Bidder shall mention the security standards adopted/followed in designing the proposed solution.
The Bidder should specify if it has acquired the ISO27001 certification or any other equivalent security certification and submit with the Offer a copy of such certificate.
The Bidder shall not hard code passwords in the proposed solution.
The provided application should run without the need of root (unix) and / or admin (win) privileges.
Source code of proposed application should be owned by MIC1.
System shall allow generation of user, operator as well as alarms logs.
Solution and storage shall be sized to host history logs for at least 1 year back.
The Bidder should submit a data flow diagram and schema of the solution architecture.
In case of online payment, the Bidder shall use encryption. (K)
The Bidder shall harden systems servers / storage before being published online, and describe hardening aspects applied on each type.
The Bidder shall describe security checking and audits performed on the designed solution prior to putting it on the market.
The Bidder shall change default errors / messages and configuration.
Application should support role-based access, specific privileges per user (i.e specific access to application modules and reports)
Database should support restricted access per user or groups to data (i.e access per field or per table, …)
Encryption shall be used in all communications / interactions between systems, especially if the communication is through web access. Web based access shall always be used through HTTP+SSL.
Each user shall have only one account / profile to access data.
Least-privileges should always be specified on nodes / applications.
Pseudocode flow chart shall be provided by the Bidders.
The Bidder should commit to improve solution / systems information security weaknesses whenever needed or highlighted by MIC1 information security team.
Health, Safety and Environmental Specifications | To ensure that the proposed products and services bidders are compliant with HSE culture, bidders should state basic HSE specifications and compliance information:
Bidder shall provide the product’s specifications that have an environmental impact (power consumption, gas emissions, etc…)
Bidder shall provide the product specifications that contribute into preserving the environment (made of recycled material, ozone friendly, low volatile organic compounds, etc…)
Bidder shall provide the product’s specifications that contribute towards the health and safety of the users (ergonomic design, safety features, etc)
Bidder shall state the safety measures being followed by personnel performing the work on Alfa’s sites (ISO45001 certification, specific best practices, etc…).
Bidder shall provide the product’s life cycle data if available.

## Technical Requirements
| RFT Compliance Matrix |  |  |  | Reference Number | SF-CF-25
[5 empty] | Owner | PRO
[5 empty] | Revision Code | 3.0
[5 empty] | Implementation Date | 2024-03-01
Project Name: | JDEIDET DATA CENTER
Reference Number: | 27 11 16 - Communications Cabinets, Racks, Frames, and Enclosures
RFT Article (Part Number or Title) | Requirements (Description) | Killer | Fully Compliant | Partially Compliant | Non-Compliant | Reference (Specify document & page nb)
1 GENERAL
1.1 SUMMARY
1. Supply of telecommunication racks/cabinets
1.2 REFERENCES
A. Compliancy with international standards:
1. TIA – 569-B – Commercial Building Standard for Telecommunications Pathways and Spaces, 2004
2. ANSI/TIA – 568-C – Commercial Building Telecommunications Cabling Standard, 2009
3. ANSI/NECA/BICSI 568-2006 – Standard for Installing Commercial Building Telecommunications Cabling
4. TIA – 606-A – Administration Standard for Commercial Telecommunications Infrastructure, 2007
5. ANSI-J-STD – 607 – A Joint Standard for Commercial Building Grounding (Earthing) and Bonding Requirements for Telecommunications, 2002
6. ANSI/TIA-942 – Telecommunications Infrastructure Standard for Data Centers, 2005
7. NFPA 70 – National Electric Code, 2008
B. Laboratory approvals
1. UL 2416 - Standard for Audio/Video, Information and Communication Technology Equipment Cabinet, Enclosure and Rack Systems
2. UL 60950-1 - nformation Technology Equipment - Safety - Part 1: General Requirements
1.3 APPLICATIONS
A. Universal server enclosures
B. Storage equipment
C. Termination equipment
D. Network equipment
1.4 SUBMITTALS
A. Documentation
1. Products data sheet
1.5 WARRANTY
A. Equipment
1. The supplied products shall be covered by full supplier warranty for a minimum period of one (1) year from delivery to site at a full repair and replacement service.
2. Warranty shall include all defected spare parts and workmanship.
B. Services
1. Installation and dismantling
a. The supplier is responsible for the dismantling, hoisting, transportation and re-installation for parts that cannot be repaired or replaced on site
2. Part replacement/repair
a. For any part replacement or repair service the warranty for the repaired or new part shall be a minimum of 6 (six) months from the date of receipt of the repaired or new part. In case a part was repaired twice already under this warranty and the equipment becomes faulty again within up to six months the Operator on its discretion may request replacement of the complete equipment.
3. Major defect
a. In case of major defect in the supplied products, the Operator reserves the right to reject the equipment. The supplier shall replace the defected system/parts under no cost from the Operator, including dismantling, hoisting, transportation and re-installation.
2 PRODUCTS
2.1 MANUFACTURERS
A. Recommended manufacturers:
1. Kendall Howard
2. Liebert
3. APC
4. Rittal
5. Belkin
6. Beldin
7. Schneider
8. Hewlett Packard
9. Or equivalent
B. Provide all components of the cabinet system (cabinet, cable, thermal, cable and power management accessories) from a single manufacturer.
2.2 FREE STANDING RACKS/CABINETS
A. Rack/Cabinet
1. Provide floor-mounting, freestanding equipment cabinets to store computer, data storage, networking and security equipment in the data centers, computer rooms and equipment rooms.
2. Each cabinet enclosure shall have a rectangular frame and removable top panel, side panels and doors.
3. Installed cabinets shall include thermal, power, and cable management accessories that control airflow through the cabinet and keep network and power cables separate and organized.
B. Rack/Cabinet Frame
1. The cabinet frame shall be manufactured from 2.5mm thick steel sheet with welded and bolted frame construction. The front and rear of the cabinet shall be welded rectangular frames. The corner posts shall have a rectangular cross-section.
C. Supporting Load
1. The cabinet frame shall support a static (non-seismic) load of 1000 kg of equipment when secured to the structural floor. The static load must be qualified through testing per UL2416 and the cabinet must be UL Listed for this load.
2. Total weight must not exceed: 1500 Kg/m²
D. Dimensions
1. The cabinet shall be 2000 mm high by 600-800 mm wide by 800-1100 mm deep when casters, doors and side panels are installed.
2. Installation height for components: 42 U
E. Front Door
1. The cabinet shall include a single curved perforated metal front door with quick-release hinge pins.
2. The primary door panel shall be constructed using a single perforated sheet (78% open at perforation) with a solid outer perimeter.
3. The door shall be removable and reversible to open from the right or left.
4. The front door shall have a swing handle with a single-point cam latch and a keyed lock.
5. The front door shall be bonded to the cabinet frame with a jumper wire through an integrated quick connect tab.
F. Rear Door
1. The cabinet shall include a double (vertically split) perforated metal rear door with quick-release hinge pins.
2. Each door panel shall be constructed using a single perforated sheet (78% open at perforation) with a solid outer perimeter.
3. The doors shall be removable.
4. The double rear door shall have a swing handle with a three-point latch and a keyed lock.
5. Both halves of the rear door shall be bonded to the cabinet frame with jumper wires through integrated quick connect tabs.
G. Equipment Mounting Rails
1. Each cabinet shall include two pairs of equipment mounting rails.
2. Mounting rails shall bolt to the side supports (slides) located near the top, middle and bottom of the frame and shall be fully adjustable in depth to provide front and rear support for equipment.
3. Equipment Mounting Rails shall be spaced horizontally to support 19” wide EIA/ECA-310-E compliant rack-mount equipment and shall provide up to 1000mm of rail-to-rail depth for equipment.
4. Mounting rails shall be square-punched according to the EIA/ECA-310-E Universal hole pattern with equipment mounting holes on alternating 15.9 mm – 15.9 mm – 12.7 mm vertical hole centers.
5. Square-punched holes shall accept cage nut hardware with various threads.
6. Rack mount spaces or units (U) shall be 1-3/4” (44.45 mm) high and shall be marked and numbered on the mounting rails. Numbering shall start at the bottom of the rail.
7. Mounting rails shall provide 42U for equipment.
8. The mounting rails shall be fully bonded to the frame without wiring.
H. Top Panel
1. The cabinet shall include a solid top panel.
2. The top panel shall be bonded to the cabinet frame through installation hardware.
I. Side Panels
1. The cabinet shall include two side panels - full-depth, solid side panels.
2. Each side panel shall attach to the cabinet frame with two bolts and shall have a keyed latch located at the top center of the panel to secure the panel to the frame.
3. Each side panel shall be bonded to the cabinet frame with a jumper wire through an integrated quick connect tab.
J. Casters & Feet
1. Four swivel casters are pre-installed.
2. Cabinet rests on leveling feet.
K. Material/Construction
1. The front and rear of the cabinet frame, side supports/slides of the cabinet frame, mounting rails, top panel, side panels and doors shall be manufactured from steel.
2. Structural components, the front and rear of the cabinet frame, side supports/slides of the cabinet frame and mounting rails shall be formed from 2.5mm thick or thicker sheet steel.
3. Non-structural components, top panels, side panels, doors, may be formed from lighter gauge material.
4. Covers for cable openings shall be plastic.
5. The front and rear of the cabinet shall be welded rectangular frames.
6. Vertical corner posts shall have a rectangular cross-section.
7. The front and rear cabinet frames, mounting rail supports, mounting rails, doors and side panels shall assemble with hardware.
L. Grounding/Bonding
1. The mounting rails, top panel, side panels and doors shall be electrically bonded to the cabinet frame.
2. The cabinet frame shall have a prepared location for attaching a grounding lug at the top and bottom of the frame.
3. All internal accessory mounting tracks shall provide a bonding path to the main cabinet ground without the need for additional surface preparation.
M. Color/Finish
1. The cabinet frame, top panel, side panels, mounting rails and doors shall be painted Black with epoxy-polyester hybrid powder coat paint.
2. Plastic components, hinges and door handles shall be black.
2.3 SHELVES
A. Shelves shall be made of heavy duty steel and rated for 100Kg
B. Shelves shall be black.
2.4 THERMAL MANAGEMENT ACCESSORIES
A. General Requirements
1. Each installed cabinet shall be equipped with additional thermal management accessories that prevent the mixing of hot and cold air within the cabinet and bypass airflow through or around the cabinet.
2. Thermal management accessories may include any combination of Air Dam, Equipment Rail Grommet Kit, Snap-In Filler Panels, Label Seal Kit and Baying Seal Kits.
B. Snap-In Filler Panels
1. Each installed cabinet shall be equipped with filler (blanking) panels that seal any open rack-mount unit space (spaces not occupied by other equipment).
2. The filler (blanking) panels shall be made of plastic and shall be designed to attach to square-punched equipment mounting rails without hardware.
3. The filler (blanking) panel design shall allow the panels to be installed and removed from the equipment mounting rails without tools.
4. Panels shall be sized to fit 1U x 19”EIA, 2U x 19”EIA, and 3U x 19”EIA rack-mount panel spaces.
C. Integral Raised Floor Grommets
1. Integral Raised Floor Grommets should be installed to seal openings in new raised floor cutouts prior to the installation of communications or power cabling.
2. The Integral Raised Floor Grommet frame is molded from durable polypropylene.
3. The Split Integral Raised Floor Grommet frame consists of two, interlocking polypro­pylene halves.
4. Dimensions (WxDxH): 280 mm x 210 mm x 40 mm
5. Usable cable area: 200 mm x 100 mm
6. Product height above the raised floor: 3 mm
7. Color: Black
8. Should allow tiles to be moved without capturing cables
9. Should contain no loose or partially fastened parts, which can become separated or fall through the raised floor
10. The grommets are impact resistant and durable.
11. The grommets satisfy NFPA 75 Section 5-4.4 requirement by self-dressing the raw metal edges of raised floor tile cable cutouts
2.5 CABLE MANAGEMENT ACCESSORIES
A. General Requirements
1. Each installed cabinet shall be equipped with additional cable management accessories that provide a specific vertical and front-to-rear pathway for cables and manage cable slack.
2. Install and align one vertical cable manager with the cable openings in the top panel so that cable is supported as it enters or exits the cabinet.
3. Install and align additional vertical cable managers, as required.
4. Install a front-to-rear manager between the front and rear equipment mounting rails in wider cabinets to provide a front-to-rear pathway for cables, if required.
B. Ring Cable Manager
1. Each installed cabinet shall be equipped with a ring cable manager to store network cables.
2. The ring cable manager shall be a pair of half-height metal brackets each with four plastic D-rings for securing cables.
3. The ring cable manager shall attach in a vertical orientation to the slides on the side of the cabinet frame and shall be independent of the equipment mounting rails.
C. Cable Lashing Bracket
1. Each installed cabinet shall be equipped with a cable lashing bracket to secure network cables.
2. The cable lashing bracket shall include two half-height brackets. Each bracket will be 1.6” (41 mm) wide with one vertical column of attachment points for securing cable bundles with Velcro straps or tie-wraps.
3. The cable lashing bracket shall attach in a vertical orientation to the slides on the side of the cabinet frame and shall be independent of the equipment mounting rails.
D. Front-to-Rear Cable Manager
1. Each installed cabinet shall be equipped with a front-to-rear cable trough to support cables horizontally between the front and rear equipment mounting rails in the space along the side of the cabinet.
2. The front-to-rear cable trough shall be a minimum of 2.5” (63 mm) wide and shall extend to attach to equipment mounting rails spaced 445 mm to 775 mm apart.
3 EXECUTION
3.1 INSTALLATION
A. Free-standing Equipment Cabinets
1. Install and adjust to position all cabinet/frame accessories including thermal management accessories, vertical cable managers, vertical power managers and equipment-mounting rails, using the manufacturer’s installation instructions prior to baying and/or placing the cabinet for attachment to the Data Center and before installing any rack-mount equipment into the cabinet. Shelves, horizontal cable managers and filler panels (rack-mount accessories), if used, may be installed after the cabinet is placed.
2. Equipment shall be installed correctly to ensure that cabinet doors be fully closed. No equipment, devices, and cables shall protrude from the rack.
3. When used in a multi-cabinet bay, cabinets shall be attached side-by-side using included baying kits according to the manufacturer’s instructions.
4. Cabinets shall be securely bonded to the Telecommunications Grounding Busbar (TGB). Attach a bonding conductor sized 16mm² Green/Yellow between the Telecommunications Grounding Busbar and the cabinet. Attach the bonding conductor to the cabinet using a ground terminal block according to the manufacturer’s installation instructions. The installer shall provide the bonding conductor and other necessary hardware required to make the connections between the cabinet and the Telecommunications Grounding Busbar.
5. The equipment load will be evenly distributed and uniform on the rack/cabinet. Place large and heavy equipment towards the bottom of the rack. Secure all equipment to the rack/cabinet with equipment mounting screws.
6. Cold air intake shall be from the front side and hot air outflow from the back of the panel.
7. Labels shall be applied to the cabinet, each PDU, Server or Chassis.
END OF SECTION

## Grade of Compliancy
| RFT Compliance Matrix | Reference Number | SF-CF-25
|  | Owner | PRO
|  | Revision Code | 3.0
|  | Implementation Date | 2024-03-01
Grade of Compliance range from 0 to 15 with a step of 1 unit:
15 : Compliant with additional value, not initially included in the requirements
10 : Fully compliant
4 - 5 - 6: Partially compliant
0 : Not compliant
K : Disqualification