## General Requirements
| RFT Compliance Matrix |  |  |  | Reference Number | SF-CF-25
[5 empty] | Owner | PRO
[5 empty] | Revision Code | 3.0
[5 empty] | Implementation Date | 2024-03-01
Project Name:
Reference Number:
RFT Article (Part Number or Title) | Requirements (Description) | Killer | Fully Compliant | Partially Compliant | Non-Compliant | Reference (Specify document & page nb)
Article 4 | Conditions for the Participation of the Eligible Bidders
4.1 | 1- Bidders shall meet the following conditions, declared in accordance with the required documents in the First section of this Article mentioned below as (First: Envelope No. (1) Administrative Documents and Transactions):
a- That there is no proven violation, by the bidders, of professional ethics generally accepted and stipulated in the relevant provisions, if any;
b- Bidders have the legal capacity to enter into the procurement contract;
c- Bidders have fulfilled their obligations to pay taxes and social security contributions;
d- Bidders have not been convicted, neither their directors nor employees involved with the procurement process, by a court decision of any criminal offence - even if the verdict can still be appealed - related to their professional conduct or the making of false statements or misrepresentations as to their qualifications to enter into a procurement contract, or corrupting a public procurement or a contract awarding process, or have not been otherwise disqualified pursuant to administrative suspension or debarment proceedings, or have been in a situation of exclusion from participation in public procurements;
e- Bidders are not the subject of legal proceedings for insolvency or bankruptcy, or were declared bankrupt by a court of law;
f- Bidders have not been convicted by a court decision - even if the verdict can still be appealed - of usury or money laundering;
g- Bidders have not participated in the decision-making process of the contracting authority or have any conflict of interest, or any material interest linking them to any of the decision makers;
h- Any other conditions set forth by the contracting authority in the tender documents that are commensurate with the required works;
i- Certificate from the Ministry of Economy proving compliance with the provisions of the Law on Boycott of Israel for foreign companies (added by Law No. 309, dated April 19, 2023).
j- Declaration of the economic beneficiaries (according to Law No. 309, dated April 19, 2023).
4.2 | 2- The bid must be submitted clearly and unequivocally without any deletion, alteration, or modification.
4.3 | 3- The bidders state in their offer that they have reviewed the Tender document and its complementary documents and have obtained a copy. They accept and undertake to adhere to all the conditions outlined therein without any reservations or exceptions. The bidder submits their offer on this basis and affixes financial stamps worth fifty thousand Lebanese pounds covering all the documents.
4.4 | 4- Any bid containing reservations or exceptions is rejected.
4.5 | 5- The bidder mentions in their offer a clear address and place of residence for prompt communication.
Administrative Documents and Transactions | First: Envelope No. (1) Administrative Documents and Transactions
A- General Conditions:
1- Undertaking Letter (Declaration), according to the attached form, signed and stamped by the bidder, this Undertaking includes the bidder's confirmation of their commitment to the price and the validity of the offer. A financial stamp of 50,000 L.L. is affixed.
2- Commercial Circular specifying the authorized signatory of the bidder and a sample of their signature.
3- Legal Authorization: If the offer is signed by someone other than the person authorized to sign according to the commercial circular, it must be notarized by a notary public.
4- Police Record of the Authorized Signatory or his “legal representative”, not exceeding three months from the bid opening date.
5- Partnership Contract legalized by a notary public if required.
6- Registration Certificate before the Directorate of Value Added Tax, if applicable, or a certificate of non-registration if not subject to it. In the latter case, the bidder commits to their bid price even if they become registered for VAT during the execution period.
7- Registration Certificate issued by the Ministry of Finance – Department of Revenue.
8- Certificate issued by the Ministry of Finance proving the bidder's compliance with tax obligations.
9- Clearance Certificate from the National Social Security Fund “comprehensive or valid for participation in public tenders and bids” valid on the date of the bid opening session, stating that the bidder has paid all his subscriptions (the bidder must be registered before the National Social Security Fund and any statement mentioning the phrase “unregistered institution” will be rejected).
10- Certificate issued by the Municipality, proving full payment of municipal fees by the bidder, issued by the municipality within its jurisdiction based on the commercial registration certificate.
11- Comprehensive Certificate issued by the Commercial Register showing founders, members, contributors, or partners, authorized signatories, the manager, capital, the bidder's activity, and ongoing liabilities.
12- Certificate issued by the relevant authorities proving that the bidder is not in a state of bankruptcy.
13- Certificate issued by the relevant authorities proving that the bidder is not in a state of judicial liquidation.
14- Bid bond as required in the specific Tender document of the procurement project, in accordance with Articles 34 and 36 of the Public Procurement Law.
15- Declaration from the Bidder identifying the economic beneficiary/beneficiaries according to Form M18 issued by the Ministry of Finance (any natural person who owns or effectively controls the ultimate outcome of the activity practiced by the bidder, either directly or indirectly, whether the bidder is a natural person or a legal entity.)
16- Copies of Identification Cards (ID/Passport) for the economic beneficiary/beneficiaries.
17- Copies of Identification Cards (ID/Passport) for each person representing the bidder (those acting on behalf of the bidder in their relationship with the contracting authority: legal representative, representative of the legal entity, or authorized signatory).
18- Integrity Declaration Document signed by the bidder in accordance with the prescribed format
Miscellaneous | The bidder shall declare any relative relations with any Alfa employee up to the 4th degree under Clause 30 of the PPL, for MIC1 to be able to assess the existing of any potential conflict of interests which may lead to deprive the bidder from participating to the tender under the risk of disqualification.
The bidder or any of his employees, partners, agents, contributors, consultants, or their relatives shall declare any relationships that may lead to a conflict of interest in the subject of this contract.
Special Conditions | B- Special Conditions Regarding the Subject of the Contract:
Financial Qualifications | 1- Financial Qualifications (To be determined based on the size and nature of the contract).
Technical/Professional Qualifications | 2- Technical/Professional Qualifications (To be determined based on the nature of the contract):
1- Certificate from the Chamber of Commerce, Industry, and Agriculture confirming that the bidder is engaged in the activities related to the subject of the contract, valid as of the date of the bidding session and valid for participation in public tenders.
2- Clearance certificate from the Order of Engineers…
3- Clearance certificate from the Contractors Syndicate…
4- ISO certificate.
5- Five Certificates of good execution and completion for similar projects in terms of size and type.
6- Technical proposal according to the required specifications in the appendix (1) of the RFT.
7- Declaration of site inspection by the bidder, denying any unfamiliarity, according to the attached model.
Participation of a foreign bidder | C- In case of the participation of a foreign bidder, the bidder must comply with one of the following conditions:
1- is part of a coalition that includes at least one Lebanese company that meets the conditions required by the specific Tender document of the procurement project.
2- The personal presence of the legal representative of the company to participate in the procurement proceedings (not mandatory).
3- Has an authorized agent or representative in Lebanon responsible for signing the contract on its behalf.
In addition to the above conditions, the foreign bidder must submit the following:
1- Certificate registration of the company or certificate of establishment issued by the relevant authorities in their country.
2- Certificate from the Lebanese Ministry of Economy and Trade confirming compliance with the provisions of the Law on Israel Boycott.
3- The required certificates according to paragraph (First) above, according to the laws of the country where the bidder is located, provided that these certificates are authenticated according to the regulations of the competent authorities.
For certificates issued without an expiration date, the validity date of each certificate is determined according to its nature, not exceeding six months from the date of the bid opening session.
Information Security Specifications | Information Security Specifications Issuing Department to determine whether all or part of this Article is applicable to their specific RFT
The Bidder shall commit to refrain from offering any product / equipment which can cause security threat or information leakage that jeopardizes MIC1 network security. (K)
The Bidder shall accept that MIC1 runs a vulnerability scan on the proposed solution prior to issuing the acceptance and in case any vulnerability is found, the Bidder undertakes to take the necessary actions to remedy such vulnerability within _____________________ days from its notification.
The Bidder shall mention the security standards adopted/followed in designing the proposed solution.
The Bidder should specify if it has acquired the ISO27001 certification or any other equivalent security certification and submit with the Offer a copy of such certificate.
The Bidder shall not hard code passwords in the proposed solution.
The provided application should run without the need of root (unix) and / or admin (win) privileges.
Source code of proposed application should be owned by MIC1.
System shall allow generation of user, operator as well as alarms logs.
Solution and storage shall be sized to host history logs for at least 1 year back.
The Bidder should submit a data flow diagram and schema of the solution architecture.
In case of online payment, the Bidder shall use encryption. (K)
The Bidder shall harden systems servers / storage before being published online, and describe hardening aspects applied on each type.
The Bidder shall describe security checking and audits performed on the designed solution prior to putting it on the market.
The Bidder shall change default errors / messages and configuration.
Application should support role-based access, specific privileges per user (i.e specific access to application modules and reports)
Database should support restricted access per user or groups to data (i.e access per field or per table, …)
Encryption shall be used in all communications / interactions between systems, especially if the communication is through web access. Web based access shall always be used through HTTP+SSL.
Each user shall have only one account / profile to access data.
Least-privileges should always be specified on nodes / applications.
Pseudocode flow chart shall be provided by the Bidders.
The Bidder should commit to improve solution / systems information security weaknesses whenever needed or highlighted by MIC1 information security team.
Health, Safety and Environmental Specifications | To ensure that the proposed products and services bidders are compliant with HSE culture, bidders should state basic HSE specifications and compliance information:
Bidder shall provide the product’s specifications that have an environmental impact (power consumption, gas emissions, etc…)
Bidder shall provide the product specifications that contribute into preserving the environment (made of recycled material, ozone friendly, low volatile organic compounds, etc…)
Bidder shall provide the product’s specifications that contribute towards the health and safety of the users (ergonomic design, safety features, etc)
Bidder shall state the safety measures being followed by personnel performing the work on Alfa’s sites (ISO45001 certification, specific best practices, etc…).
Bidder shall provide the product’s life cycle data if available.

## Technical Requirements
| RFT Compliance Matrix |  |  |  | Reference Number | SF-CF-25
[5 empty] | Owner | PRO
[5 empty] | Revision Code | 3.0
[5 empty] | Implementation Date | 2024-03-01
Project Name: | JDEIDET DATA CENTER
Reference Number: | 33 81 16 - Telecom Towers 17.08
RFT Article (Part Number or Title) | Requirements (Description) | Killer | Fully Compliant | Partially Compliant | Non-Compliant | Reference (Specify document & page nb)
1 GENERAL
1.1 SUMMARY
The purpose of this document is to provide “GSM radio and transmission” towers’ specifications regarding design, manufacturing and material delivery.
1.2 REFERENCES
A. Issues of the following documents, in effect at the time of solicitation for bids, form a part of this specification. In the event of conflict between this specification and the codes, standards, and specifications below, the most stringent and/or current requirement shall govern.
1. American Institute of Steel Construction (AISC) Manual of Steel Construction OR French code for steel construction (CM66).
2. American Welding Society (AWS) OR (CM66): Structural Welding Code.
3. American Institute of Steel Construction (AISC) OR (CM66): Specification for Structural Joints using ASTM A325 or A490 Bolts.
4. American Concrete Institute (ACI) OR French Concrete code (BAEL91): Building Code Requirements for Reinforced Concrete.
5. Telecommunications Industry Association (ANSI/TIA 222-G): for Steel Antennas Towers OR French norms “NV65 et N84 modifiées 95”: Règles définissant les effetrs de la neige at du vent sur les constructions.
6. Lebanese Code for Civil Aviation: Obstruction Marking and Lighting.
1.3 SUBMITTALS
A. The following documentations shall be provided by the manufacturer. Documents should include:
1. Complete installation drawings are required for each height setup. The drawings must show all of the necessary pieces, their part section sizes. The manufacturer shall submit an elevation of the tower (synoptic) showing all the members (main legs, diagonals, struts, bolts…) sizes, grades and distances.
2. Multiple sections on different level of the tower are required showing the struts disposition and shape.
3. An assembly detailed plan is required showing the connection between different members of the towers along with bolts and plates section and grade.
4. Connection between diagonals and struts, if existing, must be clarified by typical details.
B. Tower manufacturer shall provide the tower detailed calculation notes:
1. The calculation note shall consist of the design hypothesis and criteria, the calculation and the results (sway, stresses in members, swing period…) for each height setup.
2. It is also required to provide the tower base calculation note:
For each height setup, the foundation drawings and design taking into account the ultimate wind effect. And using a soil capacity of 2 kg/cm2 unless the existence of another recommendation based on the geotechnical data.
3. The calculation note must include the calculation of the stability, dimensions, main steel, vertical steel and stirrups around anchoring bolts, anchoring bolts design, washer, soil reactions…
4. The base design shall be signed by a registered professional engineer in the country of origin.
1.4 WARRANTY
A. All materials provided shall be guaranteed by the manufacturer against mechanical, electrical and workmanship defects. In the event defects become evident within the warranty period, the manufacturer shall furnish replacement parts and materials at no additional cost to the state. The warranty period shall commence with the date of the communications tower’s acceptance and remain in effect for one (1) calendar year, except for expendable items.
B. The manufacturer shall provide all tower elements and accessories complete and in compliance with the submitted design drawings as approved by the customer.
C. In case of major defect in the supplied products, the Operator reserves the right to reject the equipment. The supplier shall replace the defected system/parts under no cost from the Operator, including dismantling, hoisting, transportation and re-installation.
D. Tower manufacturer shall be required to furnish all materials, equipment and/or services necessary to perform contractual requirements. Materials and workmanship in the construction of equipment for this contract shall conform to all codes, regulations and requirements for such equipment, specifications contained herein, and the normal uses for which intended. Materials shall be manufactured in accordance with the best commercial practices and standards for this type of equipment. Materials used in the production of any tower must be new.
1.5 MATERIALS AND WORKMANSHIP
A. The manufacturer shall be required to furnish all materials, equipment and/or services necessary to perform contractual requirements. Materials and workmanship in the construction of equipment for this contract shall conform to all codes, regulations and requirements for such equipment, specifications contained herein, and the normal uses for which intended. Materials shall be manufactured in accordance with the best commercial practices and standards for this type of equipment. Materials used in the production of any tower must be new.
2 PRODUCTS
2.1 MANUFACTURERS
A. Towers recommended countries of origin are one of the following: Sweden, Norway, Finland, France, Germany, Turkey or Romania.
However, all towers manufactured outside Europe shall be accepted if they provide proof that they meet European standards and specifications mentioned in this document.
B. Manufacturer should be ISO certified.
C. The tower vendor shall be a manufacturer, primarily and continuously involved in the design and production of communication towers for a period of at least ten (10) years.
D. The manufacturer should be certified according to American (AISC), French codes and norms (CM66 & NV65 modifiées 80), OR Eurocodes OR to Telecommunications Industry Association standards for towers load calculation (TIA).
2.2 TOWER TYPE
A. The self-support towers are with working and rest platforms, vertical waveguide ladder, climbing ladder with hinged anti-climb cover, lightning rod assembly, obstruction lighting system.
B. The tower is required to be triangular with tubular sections. Its shape will be in function of its type, height and capacity.
C. Tower segmentation:
1. Tower sections must be categorized and labeled into typical 5m or 6m sections with unified main legs, diagonals, struts, and footprint.
2. These sections are to be adopted in different tower heights and setups as needed.
3. Different Towers shall have similar arrangement order of sections in respect with height and required capacity.
2.3 TOWER DESIGN
A. The towers will be designed by or under the direct supervision of a registered and licensed professional engineer, specifically experienced in the design of Telecom towers.
B. The allowable unit stresses and the actual member stresses resulting from the specified design loads shall not exceed those given in the AISC or CM66 specifications.
C. All members of the structure shall be considered primary members for the purpose of establishing allowable compressive stresses per AISC or CM66, except those members whose sole function is to reduce the slenderness kl/r ratio of the primary members.
D. Combined tower wind loads and antenna loads shall be applied in combination such that the maximum axial forces are produced in girds, diagonals and legs. Multiple analyses/load cases/load combinations may be necessary to ensure that worst case design conditions have been investigated.
E. The tower design shall include all the required customer loading specifications. The design shall hold all antennas on path within the critical tower twist, sway, and displacement limits.
F. The tower load as required in the BoQ, represents the load generated solely by the antennas installation. The manufacturer shall calculate the total load on tower generated by all accessories and structure (platforms, cable ladder, etc.).
1. The tower load required in the BoQ as equivalent area on Top shall be applied on top, at the last three nodes of the tower.
2. Wind load on tower members shall be applied on bars.
G. The tower design must take into account the different height setup of the same tower. For each height setup, the tower must satisfy the customer loading specifications.
H. The manufacturer must provide the detailed towers synoptic, the assembly plans, the bolts at base and the anchorage system for each height setup.
I. The tower when fully loaded with the aforementioned antenna assemblies, transmission lines, and other appurtenances, shall be designed (stress analysis) using the below hypothesis:
1. According to French norms “NV65 et N84 modifiées 95”:
a. Site located in “Région II”, exposed site.
b. Nominal wind speed of 33.8 m/s (121.7 km/h) and a gust wind speed of 44.7 m/s (160.9 km/h) at 10m
c. Dynamic pressure @ 10m should be q10=70 daN/m²
d. Site coefficient Ks =1.30 (exposed site)
e. Ct =
1) Ct = 1.3 for the antennas
2) Ct = 0.9 for Ladder and cables
3) Ct = 1.0 for platforms
f. Stress ratio 1
g. Maximum allowable tower sway under service wind conditions is 0.5 degree.
h. Maximum allowable tower displacement at top under service wind conditions shall not exceed L/200 where L is the height of the tower.
2. According to EIA/TIA-222-G code:
a. Basic wind speed of 50mps (3 sec gust at 10m) (180 km/h)
b. Operational wind speed of 40mps (140 km/h)
c. Structure class II
d. Exposure C
e. Topographic category 3, adopt crest height = 14m.
f. Stress ratio 1
g. Maximum allowable tower sway under service wind conditions is 0.5 degree at operational wind speed
h. Maximum allowable tower displacement at top under service wind conditions shall not exceed L/200 where L is the height of the tower.
J. Additional design consideration must be respected:
1. Tower members are to be released depending on the connection type.
2. Tower’s antennas weight is to be considered equal to 50 kg/m2.
3. The period of the tower used in the wind generation shall be obtained from a modal analysis (including tower, antennas and equipment mass).
K. When the tower can be located on building rooftop:
1. A minimum building height of H = 50 meter shall be taken into account unless special consideration is requested.
2. The supporting beam system at base of the tower must be included in the 3D model from which the period for the wind calculation shall be extruded. Otherwise, use a value of period T=0.50 s.
3. The connection between the tower legs and the HEA beams can be directly through Bolts. But since 2 of the bolts can intersect with the HEA beam web, exclude these two bolts from the design of the connection (divide the load on n-2 bolts).
4. The supplier must provide a full design and drawings for the adaptation that can be used instead of item 2.3.K.3 between the tower and the beams (item to be included within the BoQ).
2.4 FOUNDATION DESIGN
A. Manufacturer is responsible for the design of the tower foundation and tower grounding system. The foundation design is to take into account the ultimate tower load. A foundation design must be submitted for each height setup for the two types:
1. Full concrete cast foundation (mat foundation, its top surface aligned with soil surface).
2. Full embedded in soil raft (füt, or embedded foundation related to tower legs through piers).
B. Soils capacity: For the design and construction of the tower foundation, a net allowable bearing pressure of 2 kg/cm2 at 1m below surface, should be considered for all sites.
1. If lower values are found on site, tower foundation redesign is required.
2.5 MANUFACTURING
A. All fabrication, erection and identification of structural steel shall conform to AISC or CM66 specifications.
B. Under no circumstances shall “dissimilar metals” be used in contact with one another.
C. All tower elements and accessories shall be factory hot-dipped galvanizing. Hot-dipped galvanizing of tubular sections shall be inside and outside as per standards and methods of tower vendor. Minimum galvanization thickness 88 microns guaranteed for a period of 10 years.
D. Qualify welding processes and welding operators in accordance with AWS “Standard Qualification Procedure.” or equivalent European Standards, if applicable.
E. Properly mark and match-mark materials for field assembly. Fabricate for a delivery sequence which will expedite erection and minimize field handling of materials.
F. Tower structure and elements shall be guaranteed against fatigue failure for a period of 50 years.
2.6 CONNECTIONS AND LOCKING DEVICES
A. No field welding shall be permitted unless specifically approved in writing.
B. All members shall be connected with galvanized structural bolts unless otherwise approved.
C. The number of excess bolts should be at least 3. The tower vendor shall provide bolts, nuts in a quantity in excess of the actual bolt count for each size required for each tower site.
Bolt Count
0-200
200-500
500-1000
1000 and over
D. All towers will be provided with the correct size and length of anchor bolts necessary to carry the anticipated tower loads for each height setup.
E. All threaded fasteners shall extend not less than 1-1/2 threads beyond nuts and locking devices.
F. Horizontal and diagonals bars must be fixed to main legs using a minimum of two bolts for each.
G. Each bolt connection should include 2 nuts.
H. Tower 3 top flanges to be sealed by another 3 closed flanges (caps).
2.7 CLIMBING LADDERS AND ANTI-FALL DEVICE
A. Towers shall be provided with inside climbing ladders which will extend to the ground with an anti-fall device, provided with each tower.
B. The anti-fall device will be a safety cable, so that climbing personnel can clip into the safety device attached to a safety climbing harness from the ground or platform.
C. As a minimum, the inside climbing ladder shall conform to the following:
1. Distance between rungs shall not be more than 30 centimeters.
2. Minimum clear length of rungs shall be 40 centimeters.
D. Provide anti-climb panels that shall encompass both sides of the ladder. The panels shall be lockable while easily removable for authorized access.
2.8 REST PLATFORMS
A. Rest platforms shall be placed at intervals of max 10 meter.
B. A rest platform will consist of a step platform which allows for a person to rest on while climbing the ladder (120kg concentrated load).
2.9 WORK PLATFORM
A. When work platforms are required they shall consist of level platforms of grating. They shall be either walkways with a minimum width of 60 centimeter or full coverage platforms and they shall provide reasonable access to appropriate work areas, to any microwave parabolic antenna from the climbing ladder.
B. Safety handrails shall be provided around the perimeter of the platforms and along the walkways with upper railing at 1 meter above the deck and the intermediate rail approximately halfway between the top rail and the deck.
C. Tower diagonals and legs may be used to support platform handrails. The handrails should be connected to the tower leg by means of standard plate clamps.
D. Work platforms shall be designed to support two concentrated live loads of 125 kg each. Live loads imposed by persons on the platform shall be considered to concentrate at such points that will cause minimum stress in the structural members being considered.
E. The top work platform shall be installed 1.5 meter below the top of the tower.
2.10 VERTICAL WAVEGUIDE LADDER
A. Typically, 50 centimeters wide with ladder rung spaced vertically 90 centimeters and with equally spaced factory drilled holes to support standard snap-in stainless steel hanger kits. Waveguide ladders on self-supporting towers may be fixed to the climbing ladder or to the inside of one or more of the tower legs.
B. Total waveguide ladder capacity is to accommodate the tower’s ultimate cables for all antennas (the waveguide installation may be done in layers).
2.11 TOWER FINISHING
A. All steel members and fasteners shall be galvanized (Zinc coated) per standards in Section 2.5.C of this specifications.
B. Under no circumstances shall any coating on any metal member or fastener be cathodic relative to the base material.
C. Use zinc rich paint, or approved equal, to touch up damaged galvanization or over Cadwelded ground cable connections to the tower members. Touch up may be done by either a spray or brush application.
D. Field painting shall be performed using an acrylic latex paint specifically formulated for application to galvanized material, “Geolite” or equivalent.
E. Painting method statement, mixture and quantity shall be provided by the manufacturer.
2.12 LIGHTNING PROTECTION
A. A copper tinned lightning rod supplied by the manufacturer, with a minimum height of 1.5m, shall be installed on a 2m extension member fixed to main tower leg:
1. Connection between 2m extension and main tower leg to be flange-flange.
2. Connection between 2m extension and lightning rod to be adaptive mechanical bolt connection which hoses 30x2mm tinned copper tape.
B. At the base of the tower, a prefabricated copper wire mesh shall be directly buried below tower foundation. The tower shall be connected to the wire mesh by means of four (4) 30x2mm tinned copper tapes wrapping around the foundation and connected at the base of the tower legs.
C. The climbing ladder base shall be connected to the earth system by means of 30x2mm tinned copper tape (at base and at top of tower).
D. A 30x2 tinned copper tape for the item 12.0.1 to 12.0.3 is to be supplied and included in the BOQ.
2.13 GROUNDING BUS BARS
A. Bus bars having the same width as the Stairs or 40 cm shall be provided with the tower.
G. Each bus bar to be drilled by 12 holes.
2.14 SPECIAL REQUIREMENTS FOR RADIO TOWERS
A. Straight Radio Towers (H≤ 30m):
1. The tower section shall not have tapered legs but vertical straight legs 5-6m each from bottom to top. Tower footprint is recommended to be 2m with last main section to be Ø114 mm.
2. The tower must have same leg flanges diameter (main legs connection) from bottom to top to be flexible to any height setup. Flanges diameters shall be capable to be fixed on HEA300 steel beams. Various height setups must be recommended by the supplier.
3. Provisions of 2.3.K shall be applied for parts of the tower that can be located on roof of buildings.
B. Tapered Radio Towers (H> 30m):
1. The tower section can be tapered but shall have vertical straight legs on the last 10m. Last main section is recommended to be Ø114 mm
2.15 SPECIAL REQUIREMENTS FOR TRANSMISSION TOWERS
A. The tower section can be tapered but shall have vertical straight legs on the last 10m. Last main section is recommended to be Ø114 mm.
B. For rooftop towers, flanges diameters shall be capable to be fixed on HEA500 steel beams.
C. Provisions of 2.3.K shall be applied for parts of the tower that can be located on roof of buildings.
2.16 OBSTRUCTION LIGHTING
A. Refer to specs “34 43 13.12 - Airport Obstruction Lights 16.05”.
2.17 ACCESSORIES
A. All necessary accessories required for the proper installation and operation should be included and delivered with the system.
3 EXECUTION
A. When the site is located on high altitude areas (>1500m), some provisions for the tower foundation shall be applied as listed below:
1. During concrete pouring, if the temperature during casting is below 10°C, special admixtures shall be added for the concrete.
2. The surface of concrete needs to be protected from long term freeze/very low temperatures effect:
a. Steel cover shall be increased by enlarging the foundation dimensions of 5cm from each side
b. The four internal sides of masonry walls shall be painted, one day prior to concrete pouring by multiple layers of SIKALASTIC 612 or any equivalent according the product specifications and method of application.
c. 14 days subsequent to pouring, the upper surface of the foundation shall be painted by multiple layers of SIKALASTIC 612 or any equivalent according the product specifications and method of application.
B. The 10cm blinding concrete under the foundation is mandatory.
C. Grout shall be installed on bottom of tower legs, at the connection between the tower and the face of the concrete foundation.
D. Contractor to completely abide by the designer/manufacturer drawings and installation procedures, as well as the customer instructions.
END OF SECTION

## Grade of Compliancy
| RFT Compliance Matrix | Reference Number | SF-CF-25
|  | Owner | PRO
|  | Revision Code | 3.0
|  | Implementation Date | 2024-03-01
Grade of Compliance range from 0 to 15 with a step of 1 unit:
15 : Compliant with additional value, not initially included in the requirements
10 : Fully compliant
4 - 5 - 6: Partially compliant
0 : Not compliant
K : Disqualification