## General Requirements
| RFT Compliance Matrix |  |  |  | Reference Number | SF-CF-25
[5 empty] | Owner | PRO
[5 empty] | Revision Code | 3.0
[5 empty] | Implementation Date | 2024-03-01
Project Name: | JDEIDEH CORE – Air Conditioners - Commercial Compliance
Reference Number: | Reference Number: MIC1/RFT/CFO-PRO/193-24
RFT Article (Part Number or Title) | Requirements (Description) | Killer | Fully Compliant | Partially Compliant | Non-Compliant | Reference (Specify document & page nb)
Article 4 | Conditions for the Participation of the Eligible Bidders
4.1 | 1- Bidders shall meet the following conditions, declared in accordance with the required documents in the First section of this Article mentioned below as (First: Envelope No. (1) Administrative Documents and Transactions):
a- That there is no proven violation, by the bidders, of professional ethics generally accepted and stipulated in the relevant provisions, if any;
b- Bidders have the legal capacity to enter into the procurement contract;
c- Bidders have fulfilled their obligations to pay taxes and social security contributions;
d- Bidders have not been convicted, neither their directors nor employees involved with the procurement process, by a court decision of any criminal offence - even if the verdict can still be appealed - related to their professional conduct or the making of false statements or misrepresentations as to their qualifications to enter into a procurement contract, or corrupting a public procurement or a contract awarding process, or have not been otherwise disqualified pursuant to administrative suspension or debarment proceedings, or have been in a situation of exclusion from participation in public procurements;
e- Bidders are not the subject of legal proceedings for insolvency or bankruptcy, or were declared bankrupt by a court of law;
f- Bidders have not been convicted by a court decision - even if the verdict can still be appealed - of usury or money laundering;
g- Bidders have not participated in the decision-making process of the contracting authority or have any conflict of interest, or any material interest linking them to any of the decision makers;
h- Any other conditions set forth by the contracting authority in the tender documents that are commensurate with the required works;
i- Certificate from the Ministry of Economy proving compliance with the provisions of the Law on Boycott of Israel for foreign companies (added by Law No. 309, dated April 19, 2023).
j- Declaration of the economic beneficiaries (according to Law No. 309, dated April 19, 2023).
4.2 | 2- The bid must be submitted clearly and unequivocally without any deletion, alteration, or modification.
4.3 | 3- The bidders state in their offer that they have reviewed the Tender document and its complementary documents and have obtained a copy. They accept and undertake to adhere to all the conditions outlined therein without any reservations or exceptions. The bidder submits their offer on this basis and affixes financial stamps worth fifty thousand Lebanese pounds covering all the documents.
4.4 | 4- Any bid containing reservations or exceptions is rejected.
4.5 | 5- The bidder mentions in their offer a clear address and place of residence for prompt communication.
Administrative Documents and Transactions | First: Envelope No. (1) Administrative Documents and Transactions
A- General Conditions:
1- Undertaking Letter (Declaration), according to the attached form, signed and stamped by the bidder, this Undertaking includes the bidder's confirmation of their commitment to the price and the validity of the offer. A financial stamp of 50,000 L.L. is affixed.
2- Commercial Circular specifying the authorized signatory of the bidder and a sample of their signature.
3- Legal Authorization: If the offer is signed by someone other than the person authorized to sign according to the commercial circular, it must be notarized by a notary public.
4- Police Record of the Authorized Signatory or his “legal representative”, not exceeding three months from the bid opening date.
5- Partnership Contract legalized by a notary public if required.
6- Registration Certificate before the Directorate of Value Added Tax, if applicable, or a certificate of non-registration if not subject to it. In the latter case, the bidder commits to their bid price even if they become registered for VAT during the execution period.
7- Registration Certificate issued by the Ministry of Finance – Department of Revenue.
8- Certificate issued by the Ministry of Finance proving the bidder's compliance with tax obligations.
9- Clearance Certificate from the National Social Security Fund “comprehensive or valid for participation in public tenders and bids” valid on the date of the bid opening session, stating that the bidder has paid all his subscriptions (the bidder must be registered before the National Social Security Fund and any statement mentioning the phrase “unregistered institution” will be rejected).
10- Certificate issued by the Municipality, proving full payment of municipal fees by the bidder, issued by the municipality within its jurisdiction based on the commercial registration certificate.
11- Comprehensive Certificate issued by the Commercial Register showing founders, members, contributors, or partners, authorized signatories, the manager, capital, the bidder's activity, and ongoing liabilities.
12- Certificate issued by the relevant authorities proving that the bidder is not in a state of bankruptcy.
13- Certificate issued by the relevant authorities proving that the bidder is not in a state of judicial liquidation.
14- Bid bond as required in the specific Tender document of the procurement project, in accordance with Articles 34 and 36 of the Public Procurement Law.
15- Declaration from the Bidder identifying the economic beneficiary/beneficiaries according to Form M18 issued by the Ministry of Finance (any natural person who owns or effectively controls the ultimate outcome of the activity practiced by the bidder, either directly or indirectly, whether the bidder is a natural person or a legal entity.)
16- Copies of Identification Cards (ID/Passport) for the economic beneficiary/beneficiaries.
17- Copies of Identification Cards (ID/Passport) for each person representing the bidder (those acting on behalf of the bidder in their relationship with the contracting authority: legal representative, representative of the legal entity, or authorized signatory).
18- Integrity Declaration Document signed by the bidder in accordance with the prescribed format
Miscellaneous | The bidder shall declare any relative relations with any Alfa employee up to the 4th degree under Clause 30 of the PPL, for MIC1 to be able to assess the existing of any potential conflict of interests which may lead to deprive the bidder from participating to the tender under the risk of disqualification.
The bidder or any of his employees, partners, agents, contributors, consultants, or their relatives shall declare any relationships that may lead to a conflict of interest in the subject of this contract.
Special Conditions | B- Special Conditions Regarding the Subject of the Contract:
Financial Qualifications | 1- Financial Qualifications (To be determined based on the size and nature of the contract).
Technical/Professional Qualifications | 2- Technical/Professional Qualifications (To be determined based on the nature of the contract):
1- Certificate from the Chamber of Commerce, Industry, and Agriculture confirming that the bidder is engaged in the activities related to the subject of the contract, valid as of the date of the bidding session and valid for participation in public tenders.
2- Clearance certificate from the Order of Engineers…
3- Clearance certificate from the Contractors Syndicate…
4- ISO certificate.
5- Five Certificates of good execution and completion for similar projects in terms of size and type.
6- Technical proposal according to the required specifications in the appendix (1) of the RFT.
7- Declaration of site inspection by the bidder, denying any unfamiliarity, according to the attached model.
Participation of a foreign bidder | C- In case of the participation of a foreign bidder, the bidder must comply with one of the following conditions:
1- is part of a coalition that includes at least one Lebanese company that meets the conditions required by the specific Tender document of the procurement project.
2- The personal presence of the legal representative of the company to participate in the procurement proceedings (not mandatory).
3- Has an authorized agent or representative in Lebanon responsible for signing the contract on its behalf.
In addition to the above conditions, the foreign bidder must submit the following:
1- Certificate registration of the company or certificate of establishment issued by the relevant authorities in their country.
2- Certificate from the Lebanese Ministry of Economy and Trade confirming compliance with the provisions of the Law on Israel Boycott.
3- The required certificates according to paragraph (First) above, according to the laws of the country where the bidder is located, provided that these certificates are authenticated according to the regulations of the competent authorities.
For certificates issued without an expiration date, the validity date of each certificate is determined according to its nature, not exceeding six months from the date of the bid opening session.
Information Security Specifications | Information Security Specifications Issuing Department to determine whether all or part of this Article is applicable to their specific RFT
The Bidder shall commit to refrain from offering any product / equipment which can cause security threat or information leakage that jeopardizes MIC1 network security. (K)
The Bidder shall accept that MIC1 runs a vulnerability scan on the proposed solution prior to issuing the acceptance and in case any vulnerability is found, the Bidder undertakes to take the necessary actions to remedy such vulnerability within _____________________ days from its notification.
The Bidder shall mention the security standards adopted/followed in designing the proposed solution.
The Bidder should specify if it has acquired the ISO27001 certification or any other equivalent security certification and submit with the Offer a copy of such certificate.
The Bidder shall not hard code passwords in the proposed solution.
The provided application should run without the need of root (unix) and / or admin (win) privileges.
Source code of proposed application should be owned by MIC1.
System shall allow generation of user, operator as well as alarms logs.
Solution and storage shall be sized to host history logs for at least 1 year back.
The Bidder should submit a data flow diagram and schema of the solution architecture.
In case of online payment, the Bidder shall use encryption. (K)
The Bidder shall harden systems servers / storage before being published online, and describe hardening aspects applied on each type.
The Bidder shall describe security checking and audits performed on the designed solution prior to putting it on the market.
The Bidder shall change default errors / messages and configuration.
Application should support role-based access, specific privileges per user (i.e specific access to application modules and reports)
Database should support restricted access per user or groups to data (i.e access per field or per table, …)
Encryption shall be used in all communications / interactions between systems, especially if the communication is through web access. Web based access shall always be used through HTTP+SSL.
Each user shall have only one account / profile to access data.
Least-privileges should always be specified on nodes / applications.
Pseudocode flow chart shall be provided by the Bidders.
The Bidder should commit to improve solution / systems information security weaknesses whenever needed or highlighted by MIC1 information security team.
Health, Safety and Environmental Specifications | To ensure that the proposed products and services bidders are compliant with HSE culture, bidders should state basic HSE specifications and compliance information:
Bidder shall provide the product’s specifications that have an environmental impact (power consumption, gas emissions, etc…)
Bidder shall provide the product specifications that contribute into preserving the environment (made of recycled material, ozone friendly, low volatile organic compounds, etc…)
Bidder shall provide the product’s specifications that contribute towards the health and safety of the users (ergonomic design, safety features, etc)
Bidder shall state the safety measures being followed by personnel performing the work on Alfa’s sites (ISO45001 certification, specific best practices, etc…).
Bidder shall provide the product’s life cycle data if available.

## Technical Requirements
| RFT Compliance Matrix |  |  |  | Reference Number | SF-CF-25
[5 empty] | Owner | PRO
[5 empty] | Revision Code | 3.0
[5 empty] | Implementation Date | 2024-03-01
Project Name: | JDEIDEH CORE – Air Conditioners - Commercial Compliance
Reference Number: | Reference Number: MIC1/RFT/CFO-PRO/193-24
RFT Article (Part Number or Title) | Requirements (Description) | Killer | Fully Compliant | Partially Compliant | Non-Compliant | Reference (Specify document & page nb)
1 GENERAL
1.1 SUMMARY
A. Section includes split-system air conditioning units.
1.2 REFERENCES
A. Air-Conditioning, Heating, and Refrigeration
1. ASHRAE 15 – Refrigeration system safety
2. ASHRAE/IESNA 90.1-10 – Energy Standard for Buildings except Low-Rise Residential Buildings
3. ARI 210/240 - Performance Rating of Unitary Air-Conditioning & Air-Source Heat Pump Equipment.
4. ARI 340/360 - Performance Rating of Commercial and Industrial Unitary Air Conditioning & Air-Source Heat Pump Equipment.
5. LEED Compliance: Supply refrigeration system utilizing HCFC free refrigerants.
B. Electrostatics
1. DIN EN 61340-5-1 - Protection of electronic devices from electrostatic phenomena - General requirements
1.3 SUBMITTALS
A. Manuals
1. Operation instructions manual
2. Maintenance instructions manual
3. Installation guide
4. Wiring diagrams
5. Refrigeration diagram
6. Replacement parts list
7. Warranty Certificate
B. Test Reports
1. Test report and certificate of final acceptance
2. Test report and certificate of safety test
3. Test certificate for pressure test
1.4 WARRANTY
A. Equipment
1. The supplied products shall be covered by full supplier warranty for a minimum period of one (1) year from delivery to site at a full repair and replacement service.
2. Warranty shall include all defected spare parts and workmanship.
B. Services
1. Installation and dismantling
a. The supplier is responsible for the dismantling, hoisting, transportation and re-installation for parts that cannot be repaired or replaced on site
2. Part replacement/repair
a. For any part replacement or repair service the warranty for the repaired or new part shall be a minimum of 6 (six) months from the date of receipt of the repaired or new part. In case a part was repaired twice already under this warranty and the equipment becomes faulty again within up to six months the Operator on its discretion may request replacement of the complete equipment
3. Major defect
a. In case of major defect in the supplied products, the Operator reserves the right to reject the equipment. The supplier shall replace the defected system/parts under no cost from the Operator, including dismantling, hoisting, transportation and re-installation
2 PRODUCTS
2.1 MANUFACTURERS
A. Manufactured in a company certified according to DIN ISO 9001/ EN 29001
2.2 APPROVED BRANDS
A. Mitsubishi Electric (Japan)
B. Hitachi (Japan)
C. Panasonic Corporation (Japan)
D. LG Electronics (Korea)
E. Sharp Corporation (Japan)
F. Samsung (Korea)
G. Or equivalent
2.3 COOLING CAPACITY
A. Rated cooling capacity at 35°C ambient temperature:
1. 9,000BTU
2. 12,000BTU
3. 18,000BTU
4. 24,000BTU
5. 32,000BTU
6. 36,000BTU
7. 40,000BTU
2.4 GENERAL CHARACTERISTICS
A. Type: split-system
B. Mounting type (refer to implementation drawings):
1. Floor standing (standard mounting type)
2. Wall mount
3. Ceiling mount
C. Mains supply:
1. 380Vac ±10% 3ph @ 50 Hz
2. 220Vac ±10% 1ph @ 50Hz
D. Working ambient temperature: -10°C to +50°c
E. Cooling and heat pump
F. Noise level (dBA @ 1m):
1. Indoor unit: 33/37
2. Outdoor unit: 42/46
G. Energy efficiency rating (EER), (Btu/h.W): > 8
H. Spare parts availability for at least 7 years.
I. Both refrigerant lines must be insulated.
2.5 INDOOR UNIT
A. Made of high gauge plastic and electrolytic zinc coated steel sheet with powder paint for rust extra protection.
B. Aluminum coil louver slit on inner groove copper tube, mechanically bonded for maximum efficiency of heat transfer.
C. Direct drive motor and fan set. Operate at very low noise and are removable for easy services. Fan is of multi-blade centrifugal type.
D. Three (3) fan speeds
E. Adjustable multidirectional swing louvers.
F. High efficiency air-filter for dust trapping and easy in maintenance, cleanable and reusable.
G. Flare type fittings.
H. Drain hose should be cotton meshed.
2.6 OUTDOOR UNIT
A. Casing is made of high gauge electrolytic zinc coated sheet steel with powder paint for rust extra protection.
B. Compressor type: reciprocating
C. Pre-charged units with refrigerant for up to 8 meters lines.
D. Aluminium coil louver slit on inner groove copper tube, mechanically bonded for maximum efficiency of heat transfer.
E. The compressor is hermetically sealed, mounted on vibration absorber and sound absorption chamber for quiet operation.
F. Evaporator coil shall be constructed of aluminium fins mechanically bonded to seamless copper tubes. (0.375” seamless copper evaporator coil tube.)
G. Motor and fan with horizontal discharge designed to prevent motor burn out and easy service, operation with low RPM for super quiet operation.
H. Evaporator case shall rest on anti-vibrating pads.
I. Flare type fittings.
2.7 CONTROLS AND PROTECTION
A. On/OFF switch
B. Fan speed control: high, medium, low
C. Graduated thermostat in °C (scale 1°)
D. High and low pressure protection
E. Phase rotation protection
F. Compressor is equipped with contactor thermally protected
G. Compressor starts after timed setting (3min)
H. The expansion device for refrigerant control is indoor orifice.
I. Auto-restart after mains return
J. Auto-resume feature: during a power cutoff, all instructions are memorized and restored when power is on again.
2.8 REFRIGERANT
A. Standard: R410A
B. Components: HFC-32/125
C. Ozone depletion potential (ODP): 0
D. Global Warming Potential (GWP): 1730
2.9 REFRIGERANT COPPER PIPEWORK
A. Annealed copper tubing is used for halocarbon refrigeration systems.
B. Refrigerant pipes shall be of seamless copper tube type “L”, jointed by silver brazing, using 45% silver brazing alloy.
C. The nominal size is based on the outside diameter (OD).
D. Typical sizes include 1/4 inch 1/2 inch, 3/8 inch, 5/8 inch, 7/8 inch, 1-1/8 inch, etc.
E. Copper tubing intended for ACR applications is dehydrated, charged with nitrogen, and plugged by the manufacturer
F. Formed fittings, such as elbows and tees, are used with the hard drawn copper tubing.
G. All joints are brazed with oxy-acetylene torches by a qualified technician.
H. As mentioned before, refrigerant line sizes are selected to balance pressure drop with initial cost, in this case of the copper tubing while also maintaining enough refrigerant velocity to carry oil back to the compressor.
I. Pressure drops are calculated by adding the length of tubing required to the equivalent meters of all fittings in the line. This is then converted to PSI (kPa).
2.10 PIPEWORK THERMAL INSULATION
A. This type of insulation shall apply to refrigerant pipes, condensate drain pipes from air conditioning equipment
B. Pipes shall be insulated with rubber type insulation Armaflex 12 mm thick. Insulation shall be closed cell tubing with finished skin, chemical and oil resistant with minimum water absorption.
C. Insulation shall stand extremes temperatures ranging from 40°C to 120°C.
D. Inner tubing insulation diameter shall be equal to outer utility pipe diameter.
2.11 WIRING
A. Cables, power and control, should be terminated with crimp terminals and numbered.
2.12 WINTER KIT
A. Winter kit shall be installed to air-conditioning units for sites located at altitudes of 1000m and above and where ambient temperature is below 0°C (-5 to 10°C ambient temperature).
B. Winter kit should have dual pressure controls for regulation of low pressure (Cut in) on left and pressure difference on right side.
C. Specifications:
1. Range: -0.2 to 7.5 bar Pe
2. Difference: 0.7 to 4 bar
3. Connection: ¼ in flare
4. Ambient temperature: –40 - +65°C (+80°C for max. 2 hours)
5. DIN-approved units: –40 - +65°C (+80°C for max. 2 hours)
6. Max. working pressure: 17 bar
7. Max. test pressure: 20 bar
8. Contact load, AC:
a. AC1: 16 A, 400 V
b. AC3: 16 A, 400 V
c. AC15: 10 A, 400 V
9. Enclosure rating: IP44
10. Similar to Danfoss, Low Pressure Control, KP1, Ref 060-110166
D. Capillary tube of length of 900mm with nuts and depressor shall be used to connected the winter kit to compressor gas pipe.
2.13 LABELS
A. Each A/C UNIT shall be clearly and permanently labeled identifying:
1. Indoor unit number
2. Outdoor condenser number
3. Supply circuit breaker: panel name and circuit breaker number
2.14 ACCESSORIES
A. All necessary accessories required for the proper installation and operation of the system including:
1. Hangers,
2. Vibration isolators
3. all necessary accessories

## Commercial Requirements
| RFT Compliance Matrix |  |  |  | Reference Number | SF-CF-25
[5 empty] | Owner | PRO
[5 empty] | Revision Code | 3.0
[5 empty] | Implementation Date | 2024-03-01
Project Name: | JDEIDEH CORE – Air Conditioners - Commercial Compliance
Reference Number: | Reference Number: MIC1/RFT/CFO-PRO/193-24
Article 7: Period of Validity of Offer |  | Killer | Fully Compliant | Partially Compliant | Non-Compliant | Reference (Specify document & page nb)
6 months as of the deadline for proposals Submission |  | Yes
9.1. Terms of Payment
The following payment terms should be applied: - 50% down payment - 40% upon delivery and Provisional Acceptance (PAC), 30 days from invoice receipt. - 10% upon Final Acceptance (FAC), 30 days from invoice receipt. Payments should be done cash in LBP at market rate on payment date.
9.2. Commercial/Financial Conditions
• A Bid Bond from the participating bidders’ bank to MIC1 with a value of 5,000 USD should be presented for participation within envelop 2. The validity of this bid bond should be for 28 days as of the end of the proposals' validity; it will be returned to non-selected bidders. This LG will be returned to selected bidder after submission of the Performance Bond mentioned below. The Bid Bond is ruled by the article 34 of Public Procurement Law 244 dated 19 July 2021. It can be provided as LG from bidders’ bank or in Cash, or banker’s cheque.
Another mandatory Performance bond from winning bidder’ bank to MIC1 with a value of 10% of the quoted services should be presented upon tender award only within 15 days from contract start date. |  | Yes
9.1. Delivery Penalty / Liquidated Damages
• In case of delay in the delivery, a penalty of 1% per day of delay shall be deducted from the total amount for a maximum of 20% from the total PO amount after which MIC1 has the right to cancel the PO without any liability towards the supplier.
9.4. Project Implementation
All bidders should submit within their proposals a clear and detailed Project Implementation Plan (PIP) with a maximum duration/implementation plan of 3 months noting that this PIP will be binding and part of the contractual agreement based on which the PO will be issued to the winning bidder. A maximum project implementation of 3 months should be considered whereas a higher weight/score will be provided to bidders proposing a PIP less than 3 months.

## Grade of Compliancy
| RFT Compliance Matrix | Reference Number | SF-CF-25
|  | Owner | PRO
|  | Revision Code | 3.0
|  | Implementation Date | 2024-03-01
Grade of Compliance range from 0 to 15 with a step of 1 unit:
15 : Compliant with additional value, not initially included in the requirements
10 : Fully compliant
4 - 5 - 6: Partially compliant
0 : Not compliant
K : Disqualification