## TOTAL
JDEIDET MOT - CORE SITE Air Conditionning
BILL OF QUANTITIES - AIR CONDITIONING
ITEM | DESCRIPTION | TOTAL (USD)
1 | Precision Air Conditioners | 0
2 | Precision Air Conditioners Installation | 0
3 | Comfort Air Conditioners | 0
| GRAND TOTAL | 0

## Precision AirCon Unit
BILL OF QUANTITIES - PRECISION AIR-CONDITIONERS
SECTION | DESCRIPTION | UNIT | QTY | UNIT PRICE | TOTAL USD
SECTION 23 81 23.00.AC01 Computer-Room Air-Conditioners - Precision
1 | Supply and installation of 36KW precision Air-Conditiong Unit inluding the following (for data center): | U | 6 |  | 0
DOWNFLOW
T/RH SENSOR
FILTER
FAN
EVAPORATOR COIL
REFRIGERANT
REFRIGERATING UNIT
SCROLL-COMPRESSOR
TUBE INSULATION
PRESSURE SWITCHES (adjustable)
ELECTRIC CABINET
POWER SUPPLY
INDOOR UNIT DIMENSIONS
CONTROLLER
ELECTRICAL HEATING, 6 - 12KW, Two stages
STEAM HUMIDIFIER, 8 Kg/h
DUAL MAINS SUPPLY, 63A
OUTDOOR TEMPERATURE SENSOR
CONDENSER
WATER DETECTION SYSTEM
SHUTDOWN BY EXTERNAL FIRE ALARM
2 | Supply and installation of 10KW precision Air-Conditiong upflow cold air, front hot air intake, with dual mains supply (inside UPS and DC systems room) | U | 4 |  | 0
REMOTE MONITORING – WEB INTERFACE BOARD as per SECTION 23 81 23.00.AC01 / 2.29
3 | Communication system (controller, sensors, interfaces, etc…) for monitoring and controlling the precision A/C units remotely through IP network. Shall control all new six (6) units inside the Data Center | LS | 1 |  | 0
|  |  |  | TO SUMMARY | 0

## Precision AirCon Installation
BILL OF QUANTITIES - PRECISION AIR-CONDITIONERS INSTALLATION |  |  | PACES SAL
ITEM | DESCRIPTION | QTY | UNIT | UNIT PRICE | TOTAL US$
Copper pipes to be complete with pipe fittings, traps, hangers, sight glass and all necessary accessories insulated with 12mm "Armaflex" or equivalent. SECTION 23 81 23.00.AC01 - §2.27 & §2.28
1 | Copper pipes for precision A/C units * 6 units + 2 spare units for data center * 4 units for UPS and DC systems room | 1600 | m |  | 0
2 | Discharge pipe 1" 1/8 | 75 | m |  | 0
3 | Metallic chassis under the indoor precision A/C unit | 6 | U |  | 0
4 | A/C water drain pipes 2" dia. Supply & installation | 60 | m |  | 0
5 | Cover outdoor precision A/C units condensers air intake area with metallic grills | 6 | U |  | 0
6 | Hot air duct on top of indoor AC unit in data center- 1m above AC | 6 | U |  | 0
7 | Cold air ceiling distribution duct for precision AC units inside UPS and DC systems room | 1 | LS |  | 0
Anti-Vibration Pads
Pad with elastomeric type vibration isolation on 6 Hz natural frequency, thickness to be done as per vibration calculation result (Sylomer or equivalent).
Contractor shall be responsible for the dimensions of the anti-vibration pads. A computerized software shall calculate the vibrations and define the dimensions and type of the pads.
Pads shall be glued to galvanized metal plates soldered to indoor unit base. A reinforcement of the technical raised floor might be required.
Pads shall be Sylomer L type or equivalent to be approved by the client or his engineer representative on site
8 | Anti-vibration pads, Similar to Sylomer L type (set of 4) for the precision A/C units | 10 | U |  | 0
Water Supply
9 | A/C water supply pipes 1" dia. Supply & installation | 200 | m |  | 0
10 | 2000L water tank, PVC three layers | 1 | U |  | 0
11 | Particle filters multi-stage 10μm/5μm/1μm | 1 | U |  | 0
12 | Valves and related accessories | 1 | LS |  | 0
Cold Aisle Containement
13 | Dimensions: W1.2 x L4.8 x H2.2 m Sliding door on both side of the aisle Roof unfolds automatically upon fire incident to make sure the extinguishant gas can enter into the cold aisle containment ceiling panels and sliding doors made from steel frame and tempered glass | 4 | U |  | 0
|  |  |  | TO SUMMARY | 0

## Comfort A-C
BILL OF QUANTITIES - COMFORT AIR-CONDITIONING |  |  | PACES SAL
ITEM | DESCRIPTION | QTY | UNIT | UNIT PRICE | TOTAL US$
SECTION 23 81 26.00.SS01 Split-System Air-Conditioners
AIR CONDITIONING SPLIT UNIT
Supply and installation of cooling only split A/C unit. The unit shall be factory assembled and shall include high and low pressure switch, filter drier, time delay control, overload protection relay, thermostat. The indoor shall include a filter, insulated and sloped drain pan, with electrical power and control wiring between thermostat, panel and unit. The indoor and outdoor units to have a steel base with anti-vibrator pads.
The thermostat shall be hardwired (not wireless). The A/C unit shall be autorestart (upon failure and reconnection of the power supply, the unit automatically restarts).
Copper pipes to be complete with pipe fittings, traps, hangers, sight glass and all necessary accessories insulated with 12mm "Armaflex" or equivalent.
COMFORT AIR CONDITIONING
1 | Split A/C 12,000 Btu/hr nominal capacity, wall type, 1 phase 220Vac Electrical Room | 2 | U |  | 0
| Split A/C 12,000 Btu/hr nominal capacity, wall type, 1 phase 220Vac Utility UPS Room | 2 | U |  | 0
2 | Copper pipes for 12KBTU/hr A/C units | 120 | m |  | 0
3 | Metallic supports for the outdoor unit | 4 | U |  | 0
|  |  |  | TO SUMMARY | 0