## General Requirements
| RFT Compliance Matrix |  |  |  | Reference Number | SF-CF-25
[5 empty] | Owner | PRO
[5 empty] | Revision Code | 3.0
[5 empty] | Implementation Date | 2024-03-01
Project Name:
Reference Number:
RFT Article (Part Number or Title) | Requirements (Description) | Killer | Fully Compliant | Partially Compliant | Non-Compliant | Reference (Specify document & page nb)
Article 4 | Conditions for the Participation of the Eligible Bidders
4.1 | 1- Bidders shall meet the following conditions, declared in accordance with the required documents in the First section of this Article mentioned below as (First: Envelope No. (1) Administrative Documents and Transactions):
a- That there is no proven violation, by the bidders, of professional ethics generally accepted and stipulated in the relevant provisions, if any;
b- Bidders have the legal capacity to enter into the procurement contract;
c- Bidders have fulfilled their obligations to pay taxes and social security contributions;
d- Bidders have not been convicted, neither their directors nor employees involved with the procurement process, by a court decision of any criminal offence - even if the verdict can still be appealed - related to their professional conduct or the making of false statements or misrepresentations as to their qualifications to enter into a procurement contract, or corrupting a public procurement or a contract awarding process, or have not been otherwise disqualified pursuant to administrative suspension or debarment proceedings, or have been in a situation of exclusion from participation in public procurements;
e- Bidders are not the subject of legal proceedings for insolvency or bankruptcy, or were declared bankrupt by a court of law;
f- Bidders have not been convicted by a court decision - even if the verdict can still be appealed - of usury or money laundering;
g- Bidders have not participated in the decision-making process of the contracting authority or have any conflict of interest, or any material interest linking them to any of the decision makers;
h- Any other conditions set forth by the contracting authority in the tender documents that are commensurate with the required works;
i- Certificate from the Ministry of Economy proving compliance with the provisions of the Law on Boycott of Israel for foreign companies (added by Law No. 309, dated April 19, 2023).
j- Declaration of the economic beneficiaries (according to Law No. 309, dated April 19, 2023).
4.2 | 2- The bid must be submitted clearly and unequivocally without any deletion, alteration, or modification.
4.3 | 3- The bidders state in their offer that they have reviewed the Tender document and its complementary documents and have obtained a copy. They accept and undertake to adhere to all the conditions outlined therein without any reservations or exceptions. The bidder submits their offer on this basis and affixes financial stamps worth fifty thousand Lebanese pounds covering all the documents.
4.4 | 4- Any bid containing reservations or exceptions is rejected.
4.5 | 5- The bidder mentions in their offer a clear address and place of residence for prompt communication.
Administrative Documents and Transactions | First: Envelope No. (1) Administrative Documents and Transactions
A- General Conditions:
1- Undertaking Letter (Declaration), according to the attached form, signed and stamped by the bidder, this Undertaking includes the bidder's confirmation of their commitment to the price and the validity of the offer. A financial stamp of 50,000 L.L. is affixed.
2- Commercial Circular specifying the authorized signatory of the bidder and a sample of their signature.
3- Legal Authorization: If the offer is signed by someone other than the person authorized to sign according to the commercial circular, it must be notarized by a notary public.
4- Police Record of the Authorized Signatory or his “legal representative”, not exceeding three months from the bid opening date.
5- Partnership Contract legalized by a notary public if required.
6- Registration Certificate before the Directorate of Value Added Tax, if applicable, or a certificate of non-registration if not subject to it. In the latter case, the bidder commits to their bid price even if they become registered for VAT during the execution period.
7- Registration Certificate issued by the Ministry of Finance – Department of Revenue.
8- Certificate issued by the Ministry of Finance proving the bidder's compliance with tax obligations.
9- Clearance Certificate from the National Social Security Fund “comprehensive or valid for participation in public tenders and bids” valid on the date of the bid opening session, stating that the bidder has paid all his subscriptions (the bidder must be registered before the National Social Security Fund and any statement mentioning the phrase “unregistered institution” will be rejected).
10- Certificate issued by the Municipality, proving full payment of municipal fees by the bidder, issued by the municipality within its jurisdiction based on the commercial registration certificate.
11- Comprehensive Certificate issued by the Commercial Register showing founders, members, contributors, or partners, authorized signatories, the manager, capital, the bidder's activity, and ongoing liabilities.
12- Certificate issued by the relevant authorities proving that the bidder is not in a state of bankruptcy.
13- Certificate issued by the relevant authorities proving that the bidder is not in a state of judicial liquidation.
14- Bid bond as required in the specific Tender document of the procurement project, in accordance with Articles 34 and 36 of the Public Procurement Law.
15- Declaration from the Bidder identifying the economic beneficiary/beneficiaries according to Form M18 issued by the Ministry of Finance (any natural person who owns or effectively controls the ultimate outcome of the activity practiced by the bidder, either directly or indirectly, whether the bidder is a natural person or a legal entity.)
16- Copies of Identification Cards (ID/Passport) for the economic beneficiary/beneficiaries.
17- Copies of Identification Cards (ID/Passport) for each person representing the bidder (those acting on behalf of the bidder in their relationship with the contracting authority: legal representative, representative of the legal entity, or authorized signatory).
18- Integrity Declaration Document signed by the bidder in accordance with the prescribed format
Miscellaneous | The bidder shall declare any relative relations with any Alfa employee up to the 4th degree under Clause 30 of the PPL, for MIC1 to be able to assess the existing of any potential conflict of interests which may lead to deprive the bidder from participating to the tender under the risk of disqualification.
The bidder or any of his employees, partners, agents, contributors, consultants, or their relatives shall declare any relationships that may lead to a conflict of interest in the subject of this contract.
Special Conditions | B- Special Conditions Regarding the Subject of the Contract:
Financial Qualifications | 1- Financial Qualifications (To be determined based on the size and nature of the contract).
Technical/Professional Qualifications | 2- Technical/Professional Qualifications (To be determined based on the nature of the contract):
1- Certificate from the Chamber of Commerce, Industry, and Agriculture confirming that the bidder is engaged in the activities related to the subject of the contract, valid as of the date of the bidding session and valid for participation in public tenders.
2- Clearance certificate from the Order of Engineers…
3- Clearance certificate from the Contractors Syndicate…
4- ISO certificate.
5- Five Certificates of good execution and completion for similar projects in terms of size and type.
6- Technical proposal according to the required specifications in the appendix (1) of the RFT.
7- Declaration of site inspection by the bidder, denying any unfamiliarity, according to the attached model.
Participation of a foreign bidder | C- In case of the participation of a foreign bidder, the bidder must comply with one of the following conditions:
1- is part of a coalition that includes at least one Lebanese company that meets the conditions required by the specific Tender document of the procurement project.
2- The personal presence of the legal representative of the company to participate in the procurement proceedings (not mandatory).
3- Has an authorized agent or representative in Lebanon responsible for signing the contract on its behalf.
In addition to the above conditions, the foreign bidder must submit the following:
1- Certificate registration of the company or certificate of establishment issued by the relevant authorities in their country.
2- Certificate from the Lebanese Ministry of Economy and Trade confirming compliance with the provisions of the Law on Israel Boycott.
3- The required certificates according to paragraph (First) above, according to the laws of the country where the bidder is located, provided that these certificates are authenticated according to the regulations of the competent authorities.
For certificates issued without an expiration date, the validity date of each certificate is determined according to its nature, not exceeding six months from the date of the bid opening session.
Information Security Specifications | Information Security Specifications Issuing Department to determine whether all or part of this Article is applicable to their specific RFT
The Bidder shall commit to refrain from offering any product / equipment which can cause security threat or information leakage that jeopardizes MIC1 network security. (K)
The Bidder shall accept that MIC1 runs a vulnerability scan on the proposed solution prior to issuing the acceptance and in case any vulnerability is found, the Bidder undertakes to take the necessary actions to remedy such vulnerability within _____________________ days from its notification.
The Bidder shall mention the security standards adopted/followed in designing the proposed solution.
The Bidder should specify if it has acquired the ISO27001 certification or any other equivalent security certification and submit with the Offer a copy of such certificate.
The Bidder shall not hard code passwords in the proposed solution.
The provided application should run without the need of root (unix) and / or admin (win) privileges.
Source code of proposed application should be owned by MIC1.
System shall allow generation of user, operator as well as alarms logs.
Solution and storage shall be sized to host history logs for at least 1 year back.
The Bidder should submit a data flow diagram and schema of the solution architecture.
In case of online payment, the Bidder shall use encryption. (K)
The Bidder shall harden systems servers / storage before being published online, and describe hardening aspects applied on each type.
The Bidder shall describe security checking and audits performed on the designed solution prior to putting it on the market.
The Bidder shall change default errors / messages and configuration.
Application should support role-based access, specific privileges per user (i.e specific access to application modules and reports)
Database should support restricted access per user or groups to data (i.e access per field or per table, …)
Encryption shall be used in all communications / interactions between systems, especially if the communication is through web access. Web based access shall always be used through HTTP+SSL.
Each user shall have only one account / profile to access data.
Least-privileges should always be specified on nodes / applications.
Pseudocode flow chart shall be provided by the Bidders.
The Bidder should commit to improve solution / systems information security weaknesses whenever needed or highlighted by MIC1 information security team.
Health, Safety and Environmental Specifications | To ensure that the proposed products and services bidders are compliant with HSE culture, bidders should state basic HSE specifications and compliance information:
Bidder shall provide the product’s specifications that have an environmental impact (power consumption, gas emissions, etc…)
Bidder shall provide the product specifications that contribute into preserving the environment (made of recycled material, ozone friendly, low volatile organic compounds, etc…)
Bidder shall provide the product’s specifications that contribute towards the health and safety of the users (ergonomic design, safety features, etc)
Bidder shall state the safety measures being followed by personnel performing the work on Alfa’s sites (ISO45001 certification, specific best practices, etc…).
Bidder shall provide the product’s life cycle data if available.

## Technical Requirements
| RFT Compliance Matrix |  |  |  | Reference Number | SF-CF-25
[5 empty] | Owner | PRO
[5 empty] | Revision Code | 3.0
[5 empty] | Implementation Date | 2024-03-01
Project Name: | JDEIDET DATA CENTER
Reference Number: | 21 22 00.00.FM - Clean-Agent Fire-Extinguishing Systems - FM200 - 10.2023
RFT Article (Part Number or Title) | Requirements (Description) | Killer | Fully Compliant | Partially Compliant | Non-Compliant | Reference (Specify document & page nb)
1 GENERAL
1.1 SUMMARY
A. Provide a "Total Flood" Clean Agent Fire Suppression System with automatic detection and control.
B. Include all engineering, labor, materials, equipment and services necessary, and required, to complete and test the suppression system.
C. Design, installation and testing of a calculated automatic and manual fixed total flooding clean agent fire extinguishing system and releasing system in accordance with NFPA 2001, NFPA 72, NFPA 70, and NFPA 75 and manufacturer’s written instructions for the locations shown on the contract drawings.
D. The installation shall include all mechanical, controls and electrical components necessary for a complete and operating clean agent fire suppression system.
E. Each room to be protected shall be considered a single zone for fire suppression protection.
F. Locate extinguishing agent supply and back-up supply in each hazard area.
G. System is fixed installation with equipment designed and installed to provide fire-extinguishing capability for the area as indicated.
H. Shall utilize fixed nozzle agent distribution network.
I. Design and provide piping layout of each system to give full consideration to blind spaces, piping, electrical equipment, ductwork, and other construction and equipment in accordance with detail working drawings to be submitted for approval.
J. Devices and equipment for fire protection service shall be listed in LPCB Directory for use in Clean Agent Fire Suppression System.
K. Shall be capable of automatic detection and manual actuation.
L. Shall be capable of extinguishing fire in Class A, B, and C hazards.
M. Detection system shall be tested to applicable NFPA & BS Standards and Regulations.
1.2 REFERENCES
A. Compliancy with international standards:
1. National Fire Protection Association (NFPA):
a. NFPA 2001 - 2022 – Clean Agent Fire Extinguishing Systems
b. NFPA 70 – National Electrical Code
c. NFPA 72 – Standard for Protective Signaling Systems
d. NFPA 75 - 2020 – Standard for the Protection of Information Technology Equipment
2. BS 5839 – Part 1 (Fire detection and alarm systems for buildings. Code of practice for system design, installation, and servicing.
3. LPS 1204 – Requirements for firms engaged in the design, installation, commissioning and servicing of gas extinguishing systems. In accordance with the following standards/codes:
4. ISO 14520 – Gaseous fire-extinguishing systems – physical properties and system design
5. American National Standards Institute (ANSI)
a. ANSI B2.1 – Pipe Threads (Except Dryseal)
b. ANSI B16.3 – Malleable-Iron Threaded Fittings
6. ASME INTERNATIONAL (ASME)
a. ASME B16.11 (2011) – Forged Fittings, Socket-Welding and Threaded
b. ASME B16.3 (2011) – Malleable Iron Threaded Fittings, Classes 150 and 300
c. ASME B36.10M (2015) – Standard for Welded and Seamless Wrought Steel Pipe
d. ASME B16.18 Cast Copper Alloy Solder Joint Pressure Fittings
e. ASME B16.22 Wrought Copper and Copper Alloy Solder Joint Pressure Fittings
f. ASME B31.1 Power Piping
g. ASME B40.1 Gages – Pressure Indicating Dial Type – Elastic Element
h. ASME Boiler and Pressure Vessel Code, Section VIII, Division 1 – Rules for Construction of Pressure Vessels.
i. ASME Boiler and Pressure Vessel Code, Section IX – Welding and Brazing Qualifications.
7. American Society for Testing and Materials (ASTM)
a. ASTM A106/A106M (2014) – Standard Specification for Seamless Carbon Steel Pipe for High-Temperature Service
b. ASTM A53/A53M (2012) – Standard Specification for Pipe, Steel, Black and Hot-Dipped, Zinc-Coated, Welded and Seamless
c. ASTM A135 – Standard Specification for Electric-Resistance-Welded Steel Pipe
d. ASTM A234/A234M – Standard Specification for Pipe Fittings of Wrought Carbon Steel and Alloy Steel for Moderate and Elevated Temperatures
e. ASTM B32 – Standard Specification for Solder Metal
f. ASTM B88 Standard Specification for Seamless Copper Water Tube (ASTM B88M – Standard Specifications for Seamless Copper Water Tube (Metric).
g. ASTM A234/A234M, Pipe Fittings of Wrought Carbon Steel and Alloy Steel for Moderate and Elevated Temperatures.
B. Laboratory Approvals
1. Loss Prevention Standard (LPS / LPCB)
a. LPS 1204- 3.1 Requirements for firms engaged in the design installation, commissioning and servicing of gas extinguishing systems.
b. LPS 1230- 1.2 Requirements for fire testing of fixed gaseous fire extinguishing systems.
1.3 SUBMITTALS
A. Shop Drawings and Data:
1. All drawings and calculations shall be prepared in accordance with NFPA 2001.
2. Drawings shall bear stamp of approval of authority having jurisdiction and shall indicate locations, installation details, and operation details of all equipment and piping, control diagram, wiring diagram and sequence of operation associated with the fire suppression system.
3. Piping plan view and detail drawings shall be drawn to scale and isometrics dimensioned to show the entire storage and distribution system, the nozzle and detector location, and layout of annunciator final graphics.
4. The detector and nozzle locations shall be coordinated with lighting fixtures, diffusers, ductwork, and other equipment installed in the protected room. Indicate manual pull station, control panel, and accessory locations and details.
5. Electrical drawings shall indicate the complete sequence of operations of the system, termination diagrams and locations of interfaces with other systems.
6. Calculations shall be submitted demonstrating that the proposed system can provide the design concentration within the design discharge time. Submit design calculations bearing stamp of approval of authority having jurisdiction.
7. Calculations shall be submitted showing required battery capacity, verify system pressure, nozzle flow rate, orifice code numbers, piping pressure losses, component flow data and pipe sizes.
8. Indicate any required construction phasing.
B. Calculation Notes
1. Detailed installation drawings of the complete detection and suppression system.
2. Include manufacturer's name(s), model numbers, ratings, power requirements, equipment layout, device arrangement, complete wiring point-to-point diagrams, and conduit layouts.
3. Sufficient information, clearly presented, shall be included to determine compliance with drawings and specifications.
4. AS-BUILT drawings after system commission
5. Wiring diagram of the FACP and all connected devices
6. Battery sizing calculation notes
7. FM-200 Quantity calculation notes
8. FM-200 Hydraulic discharge calculation run on a licensed software
9. Isometric drawings
C. Submit design calculations for the following:
1. System terminal pressures
2. Nozzle flow rates
3. Orifice code number
4. Piping pressure losses
5. Component flow data
6. Pipe sizes
7. Minimum design concentration
8. Minimum design agent quantity
9. Actual agent quantity
10. Highest expected actual concentration
11. Discharge time
12. Concentration hold time
13. Enclosure pressure venting
D. Drawings should include:
1. Piping installation layout
2. Connection diagram
3. Storage cylinders
4. Discharge head
5. Manifolds
6. Pipe and fittings
7. Pipe hangers and supports
8. Pressure switch
9. Dampers
10. Main and reserve switch
11. Warning signs
12. Annotate descriptive data to show the specific model, type, and size of each item.
E. Product Data: Material and equipment information shall include manufacturer's catalog cuts and technical data for each of the following components or devices used in the system:
1. FM200 Storage containers
2. Mounting brackets
3. Piping material
4. Nozzles
5. Piping hangers
6. Escutcheons
F. Operating and Maintenance Manuals that include step-by-step procedures required for operation, shutdown, and routine maintenance and testing. The manuals shall include the manufacturer’s name, model number, parts list, the name of the local supplier, simplified wiring and controls diagrams, troubleshooting guide, and recommended service organization, including address and telephone number, for each item of equipment.
G. Include recommended spare parts list.
H. Test Plan:
1. Provide a detailed test plan to MIC1.
2. The testing plan shall describe the procedures to be used to test the system.
3. The testing plan shall include a step-by-step procedure of all tests to be performed, including indication of which tests will present a disruption to facility.
4. No tests shall be conducted until the testing plan is approved by MIC1 representative.
I. Certificates of Compliance: Submit such certified test reports for materials and equipment to demonstrate compliance with specification requirements including:
1. Storage Cylinders
2. Piping material
3. Site commissioning certificate – Signed
J. Certified Test Reports: Submit certified test reports that indicate successful completion of all tests performed. Test repots to include:
1. Pressure Tests
2. System Tests
3. Request for Inspection and Test
K. Manufacturer: Certify that system meets or exceeds specified requirements and NFPA 2001.
1.4 QUALITY ASSURANCE
A. Qualifications for FM-200 System:
1. Manufacturer: The manufacturer of the system components shall have minimum of 10 years’ experience in the manufacture and design of FM-200 fire suppression systems and related fire detection and control equipment.
2. Designer and Installer: The installer shall be authorized and trained by manufacturer to design, install, and maintain FM-200 fire suppression systems with a minimum of 10 years’ experience in the field.
B. Welding Materials and Procedures: Conform to ASME Boiler and Pressure Vessel Code, Section IX – Welding and Brazing Qualifications.
C. Regulatory Requirements for FM-200 system:
1. All system components must be approved by Loss Prevention Certification Board (LPCB).
1.5 DESIGN REQUIREMENTS
A. Provide sufficient amount of fire extinguishing agent liquid to convert into fire extinguishing agent vapor. Consider the following when computing volume:
1. Volume of hazard area
2. Specific volume of fire extinguishing agent vapor
3. Additional quantities of fire extinguishing agent required to compensate for openings, pipe losses, and nitrogen dilution.
4. Forced ventilation, fan coast-down time, and damper actuation time.
5. Mechanical smoke control system
6. Other special conditions affecting extinguishing efficiency.
B. Ensure system is free from operating and maintenance difficulties.
C. Design the system and construct to include a fixed supply of FM-200 cylinders connected to properly sized, fixed piping with fittings and nozzles to direct this agent into an enclosure surrounding the hazard.
D. Provide devices and equipment of a make and type listed by the LPCB laboratories.
E. Provide an approved low-pressure FM-200 total flooding type system conforming to NFPA 2001.
F. Ensure electrical work associated with the system meets the requirements of the appropriate electrical sections pertaining to fire detection.
1.6 WARRANTY
A. Equipment
1. The supplied products shall be covered by full supplier warranty for a minimum period of one (1) year from the commissioning date at a full repair and replacement service.
2. Warranty shall include all defected spare parts and workmanship.
B. Services
1. Installation and Dismantling
a. The supplier is responsible for the dismantling, hoisting, transportation and re-installation for parts that cannot be repaired or replaced on site.
2. Part Replacement/Repair
a. For any part replacement or repair service the warranty for the repaired or new part shall be a minimum of 6 (six) months from the date of receipt of the repaired or new part. In case a part was repaired twice already under this warranty and the equipment becomes faulty again within up to six months the Operator, on its discretion, may request replacement of the complete equipment
3. Major Defect
a. In case of major defect in the supplied products, the Operator reserves the right to reject the equipment. The supplier shall replace the defected system/parts under no cost from the Operator, including dismantling, hoisting, transportation and re-installation
2 PRODUCTS
2.1 MANUFACTURERS
A. The FACP and peripheral devices shall be manufactured 100% by a single manufacturer (or division thereof).
B. The FM-200 suppression system shall be manufactured by an ISO 9001 certified company and meet the requirements of BS EN9001: ANSI/ASQC Q9001:2015.
2.2 GENERAL
A. System includes detectors, sound and visual alarms manual release/abort stations and control panel. The detectors to be as shown on drawings and shall conform to the relevant electrical specifications’ sections.
B. Used to operate a single or multiple fire suppression or alarm system based on inputs received from fire detection devices.
C. Circuits to be configured using cross, counting, and independent or priority-zone concepts.
D. Provision should be made to alert plant staff that FM-200 has been dis-charged.
E. Arrange system for fully automatic, manually operated, and remote-pushbutton electric control operation.
2.3 FIRE SUPPRESSION AGENT
A. The agent shall be FM-200, heptafluoropropane, HFC-227ea.
B. The physical and chemical properties of FM-200 shall conform with the following requirements:
1. NFPA 2001 Standard
2. UL Listed - Ex4623
3. FM Approved – 3014476
C. The FM-200 agent shall have the following characteristics:
1. Ozone depletion potential of zero
2. Atmospheric lifetime less than 50 years
3. 4-hour LC50 > 788,696 ppm
D. The FM-200 agent shall be manufactured to these specifications:
1. Mole%: 99.0 Minimum
2. Acidity, ppm by weight: 3.0 Maximum
3. Water content, % by weight: 0.001 Maximum
4. Non-volatile residues, gram/100mL: 0.05 Maximum
E. Approved manufacturers:
1. Fike Corporation
2. Kidde
3. Fenwal
4. or equivalent
F. The agent shall be stored in containers, super-pressurized with nitrogen to a maximum total pressure level at 70 degrees F of 360 psig. Higher-pressure agents will not be acceptable.
2.4 Agent Storage Containers
A. Standard model and size for ease or replacement and addition. Design, fabricate, certify, and stamp cylinders in accordance with ASME Section VIII.
B. The supply area of agent shall be central storage by design. The storage vessels shall be capable of being checked for liquid level without the aid of scales or other special tools. The supply shall be located as indicated, so that proper hydraulic agent distribution is achieved.
C. Agent storage containers shall be floor mounted and shall include bracket assemblies designed to withstand 1000 pounds (453Kg) thrust for 10 seconds. Floor space is limited, therefore, alternatives requiring more floor space will not be considered.
D. The storage containers shall be actuated by means of an electronic initiator. Each container shall be actuated individually. Master/slave solenoid configurations will not be considered.
E. Identification: Permanent plate, specifying manufacturer's name, part number, agent type, tare and gross weight, weight of fire extinguishing agent, and pressurization level, installed so that plate is visible and readable.
F. Cylinder valves: Heavy duty forged brass, incorporating safety release pressure operated manual control, solenoid discharge valve, and pressure gage. Provide solenoid pilot valves for each cylinder or bank of cylinders.
G. Manifold: Provide for systems with more than one cylinder with rack to secure each cylinder and check valves between each cylinder discharge and manifold.
H. The container and valve shall be capable of releasing the agent as fast as possible and shall in no case exceed 10 seconds.
I. Safety Release: Equip cylinder with frangible disc safety device that operates when internal pressure exceeds 730 pounds per square inch.
2.5 ACTUATOR
A. Release of the agent shall be accomplished by an electrical signal from the system control panel in conjunction with a specifically designed agent release module.
B. Systems that employ more than one cylinder shall have all electric initiators connected in parallel.
C. The electric actuator should be easily removed and installed without a means of toolkit.
2.6 MANUAL STATIONS WITH DIGITAL COUNTDOWN TIMER
A. A manual release shall also consist of a digital countdown timer and abort switch combined as one unit.
B. Identification: “AGENT RELEASE” caption, and red finish.
C. Unit shall have a metal housing with a dual action release configuration requiring two distinct operations to initiate a system actuation in order to prevent accidental system discharge.
D. The countdown timer provides a digital readout, indicating the number of seconds remaining until the clean agent discharges. There shall be a label stating “Seconds Remaining to Discharge” at the digital readout.
E. Each manual release shall include a contact monitor module to provide for a custom message and device location at the control panel (FACP).
F. Locate manual release switch at each exit from the protected hazard.
2.7 ABORT STATION
A. "Dead Man" type, located next to each manual switch.
B. Each abort station shall include a contact monitor module to provide for a custom message and device location at the control panel.
C. Supervised with indication of a trouble condition at the control panel, if depressed and no alarm condition exist.
D. Identification: “ABORT” caption, momentary contact, with yellow button.
2.8 SWITCHES
A. Listed and approved type, 220-Vac or low voltage compatible with controls.
B. Include contacts for connection to control panel.
1. Low-Agent Pressure Switches: Pneumatic operation
2. Door Closers: Magnetic retaining and release device or electrical interlock to cause the door operator to drive the door closed.
2.9 LOW PRESSURE SWITCH
A. The agent storage container shall be equipped with a low-pressure switch to indicate a loss of container pressure. A decrease in pressure from 360 psi to 275/272 psi will cause the normally closed contact to open, thereby indicating a trouble condition.
B. Low pressure switch shall be monitored by the system control panel (FACP) and shall provide a specific indication of cylinder low pressure.
2.10 LIQUID LEVEL INDICATOR
A. Tanks holding in excess of 60 pounds (27Kg) of agent shall contain a liquid level indicator to monitor vessel contents, in addition to the low-pressure switch.
2.11 DISCHARGE NOZZLES
A. Nozzles shall distribute the agent throughout the protected area. Single nozzle shall not discharge more than 250 pounds (113kG) of agent.
B. The nozzles shall utilize a 180 or 360-degree pattern and shall be designed to direct the discharge of agent parallel to the ceiling, thus minimizing the possibility of disturbance to objects within the room.
C. Deflector plates shall be used with the nozzles when sensitive ceiling tiles must be protected.
D. A maximum nozzle flow rate of 17 lbs./sec (7.7Kg/sec) shall be designed for all areas with false ceilings or delicate operations. Higher flow rates may dislodge objects, which could damage or affect equipment and/or process.
E. Construction: One-piece chrome plated brass or aluminum nozzle with textured finish with female pipe thread integral on body. Direct discharge parallel to ceiling.
F. Identification: Permanently mark nozzles to show equivalent single orifices diameter.
2.12 PIPE AND FITTINGS
A. Pipe
1. Meets requirements of ASTM A53/A53M T, Type E (electric-resistance welded, Grade A or Grade B) or Type S (seamless, Grade A or Grade B).
2. Meets requirements of ASTM A106/A106M, Grade A or Grade B.
3. Pipe shall be threaded end connections, Schedule 80 or Weight Class XS (Extra Strong), except that sizes smaller than one inch may be Schedule 40 or Weight Class STD (Standard).
4. Pipe shall be epoxy coated, installed exposed, including all kind of supports and hangers.
5. Pipe and pipefittings shall conform with the requirements of NFPA 2001.
6. Provide pipe and fittings having a minimum bursting pressure of 41.37 Mega Pascal (6,000 psi).
B. Threaded Fittings
1. Use hot-dipped galvanized, ASME B16.11, except sizes 50 mm (2 inches) and smaller may conform to ASME B16.3, Class 300
2. Use hot-dipped galvanized, ASME B16.11, for continuous pressure pipe fittings between storage tank and selector valves, and ASME B16.3, Class 150, hot-dipped galvanized fittings, for pipe not under continuous pressure.
3. Use pipe cement and oil, or graphite and oil for pipe thread joint compound.
C. Unions
1. ASME B16.39, Class 300
2.13 PIPING ACCESSORIES
A. Escutcheon Plates
1. Provide split hinge metal plates for piping entering floors, walls, and ceilings in exposed spaces.
2. Provide polished stainless steel plates or chromium plated finish on copper alloy plates in finished spaces.
3. Provide paint finish on metal plates in unfinished spaces.
B. Pipe Sleeves
1. Provide where piping passes entirely through partitions, walls, ceilings, roofs, and floors.
2. Provide sleeves of sufficient length to pass through entire thickness of walls, ceilings, roofs, and floors.
3. Provide 25 mm (one inch) minimum clearance between exterior of piping and interior of sleeve or core-drilled hole.
4. Firmly pack space with mineral wool insulation and seal both ends of sleeve or core-drilled hole with plastic waterproof cement which will dry to a firm but pliable mass, or provide mechanically adjustable segmented elastomeric seal.
5. In fire walls and fire floors, seal both ends of sleeves or core-drilled holes with UL listed fill, void, or cavity material.
6. Provide schedule 40 zinc-coated steel pipe sleeves: in outside walls below and above grade, in floor, or in roof slabs.
7. Provide zinc-coated sheet steel sleeves in partitions having a nominal weight of not less than 4.4 kilogram per square meter 0.90 pound per square foot.
8. Core-drilling of masonry and concrete may be provided in lieu of sleeves provided that cavities in the core-drilled holes are completely grouted smooth.
9. Sleeves in other than masonry and concrete: Provide 26 gage galvanized steel sheets.
2.14 PIPE HANGERS AND SUPPORTS
A. Provide zinc-coated, adjustable pipe hangers and supports conforming to MSS SP-58 and MSS SP-69.
A. Comply to MSS SP-58 - Pipe Hangers and Supports - Materials, Design, Manufacture, Selection, Application, and Installation
B. Comply to MSS SP-69 - Pipe Hangers and Supports ‚ Selection and Application
C. Provide MSS SP-58 and MSS SP-69, Type 1, with adjustable type support rods, except as specified or indicated otherwise.
D. Attach to steel joists with Type 19 or 23 clamps and retaining straps.
E. Attach to steel W or S beams with Type 21, 28, 29, or 30 clamps.
F. Attach to steel angles and vertical web steel channels with Type 20 clamp with beam clamp channel adapter.
G. Attach to horizontal web steel channel and wood with drilled hole on centerline and double nut and washer.
H. Attach to concrete with Type 18 insert or drilled expansion anchor.
I. Maximum spacing is as follows:
1. Maximum Nominal Pipe Size (Diameter Nominal) – Maximum Spacing
a. 15 mm Diameter and under – 2130 mm Maximum spacing
b. 32 mm Diameter – 2440 mm Maximum spacing
c. 40 mm Diameter – 2470 mm Maximum spacing
d. 50 mm Diameter – 3050 mm Maximum spacing
e. 65 mm Diameter – 3350 mm Maximum spacing
f. 80 mm Diameter – 3660 mm Maximum spacing
g. 90 mm Diameter – 3960 mm Maximum spacing
h. 100 mm Diameter – 4270 mm Maximum spacing
i. 125 mm Diameter – 4570 mm Maximum spacing
j. 150 mm Diameter – 4880 mm Maximum spacing
2.15 AUTOMATIC SMOKE-FIRE DAMPERS
A. Provide automatic control of smoke-fire dampers in openings and ductwork penetrating the envelope of the protected area.
B. Smoke-fire dampers are specified in Section 23 00 00 - Air Supply, Distribution, Ventilation, and Exhaust Systems.
2.16 PRESSURE RELIEF DEVICE
A. Provide each system with an approved device designed to operate between 16.50 and 20.70 MPa (gage) 2400 and 3000 psi.
B. Locate the device between the storage cylinder manifolds and normally closed valves.
2.17 PRESSURE-OPERATED FIRE ALARM
A. Sends signal to FACP when FM200 gas is released/discharged.
B. Pressure Switch is connected to cylinder head with a flexible hose.
2.18 SIGNS AND IDENTIFICATION
A. Provide signs and identification for Facility Services, and in conformance with NFPA 2001.
B. Provide signs and identification to each valve required to be identified.
C. Provide engraved nameplates for all manual discharge stations and abort switch locations to indicate their function. All alarm devices shall have similar identification plates.
D. Each entrance door shall include a caution placard indicating that the area is being protected by a clean agent fire suppression system.
2.19 LABELS
A. FM200 Cylinders should be labeled with:
1. Country of origin
2. Filling date
3. Net FM200 agent
4. Gross Weight
B. FM200 cylindered should be numbered with large readable markings
2.20 ACCESSORIES
1. All accessories necessary for the installation and proper operation of the system should be delivered with the system free of charge.
3 EXECUTION
3.1 INSTALLATION
A. Install materials and equipment in accordance with NFPA 2001.
B. Piping
1. Ensure space between piping and the sleeve is not less than 6 millimeters. Securely place sleeves in proper position and location during construction. Ensure sleeves are of sufficient length to pass through the entire thickness of walls, partitions, or slabs. Ensure sleeves extend 5.08 cm above finished floor slabs. Pack space between the pipe and sleeve with insulation and seal both ends of the sleeve with plastic waterproof cement.
2. Set and securely fasten escutcheons in place with setscrews or other positive means.
3. Reduce pipe sizes in the fitting. Flush bushings are not allowed. When used, fuse brazed joints with an alloy having a melting point above 538 degrees C.
4. Inspect and test piping before concealing. Provide fittings for direction changes in piping and for connections. Use Jointing compound for pipe threads are polytetrafluoroethylene (PTFE) pipe thread tape, pipe cement and oil, or PTFE powder and oil; apply only to male threads. Provide exposed ferrous pipe threads with one coat of FS TT-P-645 primer applied to a minimum dry film thickness of 0.025 mm 1.0 mil. Use Schedule 80 steel pipe, hot-dipped galvanized for pipe nipples 150 mm 6 inches long and shorter. Provide tapered-reducing pipe fittings for changes in piping size; bushings are not permitted. Minimum nominal pipe size for hose and systems is 20 mm.
5. Ensure each system has an approved pressure-relief device designed to operate between 20 Mega Pascal and located between the storage cylinder manifolds and any normally close valve.
C. Controls
1. Install a combination of electric and mechanical pull cable (where required only) actuating control system.
D. Electrical Work
1. Electrical work is specified in Section 28 31 12.00.F01 - Zoned (DC Loop) Fire-Alarm Systems.
E. Operating Instructions
1. Provide operating instructions at each remote control station, clearly indicating the necessary steps for the operation of the system.
2. Submit operating instructions for FM200 fire-protection systems, consisting of raised or embossed white letters on red rigid plastic or enameled steel background, and of adequate size to permit them to be easily read.
F. Field Painting
1. Clean, pretreat, prime, and paint new carbon dioxide fire extinguishing systems including valves, piping, conduit, hangers, miscellaneous metalwork, and accessories. Apply coatings to clean, dry surfaces, using clean brushes. Clean surfaces to remove dust, dirt, rust, and loose mill scale. Immediately after cleaning, provide metal surfaces with one coat of FS TT-P-645 primer applied to a minimum dry film thickness of 0.025 mm.
2. Shield operating devices with protective covering while painting is in process. Upon completion of painting, remove protective covering from operating devices. Remove devices which are painted and replace with new devices.
3. Provide primed surfaces with the following:
G. Systems in Unfinished Areas
1. Unfinished areas are defined as attic spaces, mechanical rooms, spaces above suspended ceilings, crawl spaces, pipe chases, and spaces where walls or ceiling are not painted or not constructed of a prefinished material.
2. Provide primed surfaces with one coat of CID A-A-2962 red enamel applied to a minimum dry film thickness of 0.025 mm 1.0 mil.
H. FIELD QUALITY CONTROL
1. Provide each system complete and ready for operation.
2. Conduct testing to determine conformance with the requirements in the presence of MIC1 representative.
I. Preliminary Tests
1. Perform and record pressure tests and system tests.
2. Test each piping system pneumatically at 1050 kilopascal gage and verify no leakage or reduction in gage pressure after 2 hours occurs. Upon completion and before final acceptance of the work, test each piping system by discharging a minimum of one 34 kilogram high-pressure cylinders of carbon dioxide to demonstrate the reliability and proper functioning of pressure-operated switches and the discharge of carbon dioxide gas from each system discharge nozzle.
3. Individually test all remote-control stations, and all other components, supporting elements and accessories individually to demonstrate proper functioning.
4. Provide test results to the Contracting Officer. Submit the test results with a cover letter/sheet clearly marked with the System name, date, and the words "Final Test Reports”.
5. At the completion of tests and corrections, submit a signed and dated certificate to the Contracting Officer attesting to the satisfactory completion of all testing and that the system is in operating condition.
6. Submit a written request for inspection and test to the MIC1 representative for systems formal tests.
3.2 FINAL TESTING
A. Include the NFPA 72 Certificate of Completion and NFPA 72 Inspection and Testing Form, with the appropriate test reports.
B. At a time to which MIC1 has agreed, the MIC1 representative will witness formal tests and approve systems before they are accepted. Ensure an experienced technician regularly employed by the system installer is present during the inspection. At this inspection, repeat any or all of the required tests as directed by the supplier. Furnish carbon dioxide, instruments, personnel, appliances, and equipment for testing at no cost to MIC1.
C. Update and resubmit data for final approval no later than 3 working days prior to contract completion.
3.3 TRAINING
A. Provide training course for the operations and maintenance staff.
B. Conduct the course in the building where the system is installed or as designated by the MIC1 engineer.
C. Submit lesson plans, operating instructions, maintenance procedures, and training data, furnished in manual format, for the training courses.
D. The operations training shall familiarize designated personnel with proper operation of the fire alarm system.
E. The training period for systems operation shall consist of 1 training day and shall start after the system is functionally completed but prior to final acceptance tests.
3.4 SITE DOCUMENT
A. AS BUILT plans
B. FM200 quantity calculations
C. FM200 hydraulic flow calculations
D. Certificate of testing and commissioning
END OF SECTION

## Grade of Compliancy
| RFT Compliance Matrix | Reference Number | SF-CF-25
|  | Owner | PRO
|  | Revision Code | 3.0
|  | Implementation Date | 2024-03-01
Grade of Compliance range from 0 to 15 with a step of 1 unit:
15 : Compliant with additional value, not initially included in the requirements
10 : Fully compliant
4 - 5 - 6: Partially compliant
0 : Not compliant
K : Disqualification