## General Requirements
| RFT Compliance Matrix |  |  |  | Reference Number | SF-CF-25
[5 empty] | Owner | PRO
[5 empty] | Revision Code | 3.0
[5 empty] | Implementation Date | 2024-03-01
Project Name:
Reference Number:
RFT Article (Part Number or Title) | Requirements (Description) | Killer | Fully Compliant | Partially Compliant | Non-Compliant | Reference (Specify document & page nb)
Article 4 | Conditions for the Participation of the Eligible Bidders
4.1 | 1- Bidders shall meet the following conditions, declared in accordance with the required documents in the First section of this Article mentioned below as (First: Envelope No. (1) Administrative Documents and Transactions):
a- That there is no proven violation, by the bidders, of professional ethics generally accepted and stipulated in the relevant provisions, if any;
b- Bidders have the legal capacity to enter into the procurement contract;
c- Bidders have fulfilled their obligations to pay taxes and social security contributions;
d- Bidders have not been convicted, neither their directors nor employees involved with the procurement process, by a court decision of any criminal offence - even if the verdict can still be appealed - related to their professional conduct or the making of false statements or misrepresentations as to their qualifications to enter into a procurement contract, or corrupting a public procurement or a contract awarding process, or have not been otherwise disqualified pursuant to administrative suspension or debarment proceedings, or have been in a situation of exclusion from participation in public procurements;
e- Bidders are not the subject of legal proceedings for insolvency or bankruptcy, or were declared bankrupt by a court of law;
f- Bidders have not been convicted by a court decision - even if the verdict can still be appealed - of usury or money laundering;
g- Bidders have not participated in the decision-making process of the contracting authority or have any conflict of interest, or any material interest linking them to any of the decision makers;
h- Any other conditions set forth by the contracting authority in the tender documents that are commensurate with the required works;
i- Certificate from the Ministry of Economy proving compliance with the provisions of the Law on Boycott of Israel for foreign companies (added by Law No. 309, dated April 19, 2023).
j- Declaration of the economic beneficiaries (according to Law No. 309, dated April 19, 2023).
4.2 | 2- The bid must be submitted clearly and unequivocally without any deletion, alteration, or modification.
4.3 | 3- The bidders state in their offer that they have reviewed the Tender document and its complementary documents and have obtained a copy. They accept and undertake to adhere to all the conditions outlined therein without any reservations or exceptions. The bidder submits their offer on this basis and affixes financial stamps worth fifty thousand Lebanese pounds covering all the documents.
4.4 | 4- Any bid containing reservations or exceptions is rejected.
4.5 | 5- The bidder mentions in their offer a clear address and place of residence for prompt communication.
Administrative Documents and Transactions | First: Envelope No. (1) Administrative Documents and Transactions
A- General Conditions:
1- Undertaking Letter (Declaration), according to the attached form, signed and stamped by the bidder, this Undertaking includes the bidder's confirmation of their commitment to the price and the validity of the offer. A financial stamp of 50,000 L.L. is affixed.
2- Commercial Circular specifying the authorized signatory of the bidder and a sample of their signature.
3- Legal Authorization: If the offer is signed by someone other than the person authorized to sign according to the commercial circular, it must be notarized by a notary public.
4- Police Record of the Authorized Signatory or his “legal representative”, not exceeding three months from the bid opening date.
5- Partnership Contract legalized by a notary public if required.
6- Registration Certificate before the Directorate of Value Added Tax, if applicable, or a certificate of non-registration if not subject to it. In the latter case, the bidder commits to their bid price even if they become registered for VAT during the execution period.
7- Registration Certificate issued by the Ministry of Finance – Department of Revenue.
8- Certificate issued by the Ministry of Finance proving the bidder's compliance with tax obligations.
9- Clearance Certificate from the National Social Security Fund “comprehensive or valid for participation in public tenders and bids” valid on the date of the bid opening session, stating that the bidder has paid all his subscriptions (the bidder must be registered before the National Social Security Fund and any statement mentioning the phrase “unregistered institution” will be rejected).
10- Certificate issued by the Municipality, proving full payment of municipal fees by the bidder, issued by the municipality within its jurisdiction based on the commercial registration certificate.
11- Comprehensive Certificate issued by the Commercial Register showing founders, members, contributors, or partners, authorized signatories, the manager, capital, the bidder's activity, and ongoing liabilities.
12- Certificate issued by the relevant authorities proving that the bidder is not in a state of bankruptcy.
13- Certificate issued by the relevant authorities proving that the bidder is not in a state of judicial liquidation.
14- Bid bond as required in the specific Tender document of the procurement project, in accordance with Articles 34 and 36 of the Public Procurement Law.
15- Declaration from the Bidder identifying the economic beneficiary/beneficiaries according to Form M18 issued by the Ministry of Finance (any natural person who owns or effectively controls the ultimate outcome of the activity practiced by the bidder, either directly or indirectly, whether the bidder is a natural person or a legal entity.)
16- Copies of Identification Cards (ID/Passport) for the economic beneficiary/beneficiaries.
17- Copies of Identification Cards (ID/Passport) for each person representing the bidder (those acting on behalf of the bidder in their relationship with the contracting authority: legal representative, representative of the legal entity, or authorized signatory).
18- Integrity Declaration Document signed by the bidder in accordance with the prescribed format
Miscellaneous | The bidder shall declare any relative relations with any Alfa employee up to the 4th degree under Clause 30 of the PPL, for MIC1 to be able to assess the existing of any potential conflict of interests which may lead to deprive the bidder from participating to the tender under the risk of disqualification.
The bidder or any of his employees, partners, agents, contributors, consultants, or their relatives shall declare any relationships that may lead to a conflict of interest in the subject of this contract.
Special Conditions | B- Special Conditions Regarding the Subject of the Contract:
Financial Qualifications | 1- Financial Qualifications (To be determined based on the size and nature of the contract).
Technical/Professional Qualifications | 2- Technical/Professional Qualifications (To be determined based on the nature of the contract):
1- Certificate from the Chamber of Commerce, Industry, and Agriculture confirming that the bidder is engaged in the activities related to the subject of the contract, valid as of the date of the bidding session and valid for participation in public tenders.
2- Clearance certificate from the Order of Engineers…
3- Clearance certificate from the Contractors Syndicate…
4- ISO certificate.
5- Five Certificates of good execution and completion for similar projects in terms of size and type.
6- Technical proposal according to the required specifications in the appendix (1) of the RFT.
7- Declaration of site inspection by the bidder, denying any unfamiliarity, according to the attached model.
Participation of a foreign bidder | C- In case of the participation of a foreign bidder, the bidder must comply with one of the following conditions:
1- is part of a coalition that includes at least one Lebanese company that meets the conditions required by the specific Tender document of the procurement project.
2- The personal presence of the legal representative of the company to participate in the procurement proceedings (not mandatory).
3- Has an authorized agent or representative in Lebanon responsible for signing the contract on its behalf.
In addition to the above conditions, the foreign bidder must submit the following:
1- Certificate registration of the company or certificate of establishment issued by the relevant authorities in their country.
2- Certificate from the Lebanese Ministry of Economy and Trade confirming compliance with the provisions of the Law on Israel Boycott.
3- The required certificates according to paragraph (First) above, according to the laws of the country where the bidder is located, provided that these certificates are authenticated according to the regulations of the competent authorities.
For certificates issued without an expiration date, the validity date of each certificate is determined according to its nature, not exceeding six months from the date of the bid opening session.
Information Security Specifications | Information Security Specifications Issuing Department to determine whether all or part of this Article is applicable to their specific RFT
The Bidder shall commit to refrain from offering any product / equipment which can cause security threat or information leakage that jeopardizes MIC1 network security. (K)
The Bidder shall accept that MIC1 runs a vulnerability scan on the proposed solution prior to issuing the acceptance and in case any vulnerability is found, the Bidder undertakes to take the necessary actions to remedy such vulnerability within _____________________ days from its notification.
The Bidder shall mention the security standards adopted/followed in designing the proposed solution.
The Bidder should specify if it has acquired the ISO27001 certification or any other equivalent security certification and submit with the Offer a copy of such certificate.
The Bidder shall not hard code passwords in the proposed solution.
The provided application should run without the need of root (unix) and / or admin (win) privileges.
Source code of proposed application should be owned by MIC1.
System shall allow generation of user, operator as well as alarms logs.
Solution and storage shall be sized to host history logs for at least 1 year back.
The Bidder should submit a data flow diagram and schema of the solution architecture.
In case of online payment, the Bidder shall use encryption. (K)
The Bidder shall harden systems servers / storage before being published online, and describe hardening aspects applied on each type.
The Bidder shall describe security checking and audits performed on the designed solution prior to putting it on the market.
The Bidder shall change default errors / messages and configuration.
Application should support role-based access, specific privileges per user (i.e specific access to application modules and reports)
Database should support restricted access per user or groups to data (i.e access per field or per table, …)
Encryption shall be used in all communications / interactions between systems, especially if the communication is through web access. Web based access shall always be used through HTTP+SSL.
Each user shall have only one account / profile to access data.
Least-privileges should always be specified on nodes / applications.
Pseudocode flow chart shall be provided by the Bidders.
The Bidder should commit to improve solution / systems information security weaknesses whenever needed or highlighted by MIC1 information security team.
Health, Safety and Environmental Specifications | To ensure that the proposed products and services bidders are compliant with HSE culture, bidders should state basic HSE specifications and compliance information:
Bidder shall provide the product’s specifications that have an environmental impact (power consumption, gas emissions, etc…)
Bidder shall provide the product specifications that contribute into preserving the environment (made of recycled material, ozone friendly, low volatile organic compounds, etc…)
Bidder shall provide the product’s specifications that contribute towards the health and safety of the users (ergonomic design, safety features, etc)
Bidder shall state the safety measures being followed by personnel performing the work on Alfa’s sites (ISO45001 certification, specific best practices, etc…).
Bidder shall provide the product’s life cycle data if available.

## Technical Requirements
| RFT Compliance Matrix |  |  |  | Reference Number | SF-CF-25
[5 empty] | Owner | PRO
[5 empty] | Revision Code | 3.0
[5 empty] | Implementation Date | 2024-03-01
Project Name: | JDEIDET DATA CENTER
Reference Number: | 28 31 11.00.FA01 - Digital Addressable Fire-Alarm Systems - 10.2023
RFT Article (Part Number or Title) | Requirements (Description) | Killer | Fully Compliant | Partially Compliant | Non-Compliant | Reference (Specify document & page nb)
1 GENERAL
1.1 SUMMARY
A. This section of the specifications includes the furnishing, installation, and connection of the fire alarm equipment to form a complete coordinated system ready for operation. It shall include, but not be limited to, alarm initiating devices, alarm notification appliances, control units, fire safety control devices, annunciators, power supplies, and wiring as shown on the drawings and specified.
B. Shall be capable of automatic detection and manual actuation.
C. Detection system shall be tested to applicable NFPA & BS Standards and Regulations.
1.2 REFERENCES
A. Compliancy with international standards:
1. National Fire Protection Association (NFPA):
a. NFPA 70 – National Electrical Code.
b. NFPA 72 – Standard for Protective Signaling Systems.
2. British Standards
a. BS 5839 – Part 1 (Fire detection and alarm systems for buildings. Code of practice for system design, installation and servicing.
b. BS 6266 – Code of practice for fire protection for electronic data processing installations
c. BS 7273-1 – Code of practice for the operation of fire protection measures
B. Laboratory approvals
1. Loss Prevention Certification Board (LPCB)
2. Underwriter Laboratory (UL)
1.3 SUBMITTALS
A. Two (2) complete set of documentations shall be provided by the supplier. Documents should include:
B. Manuals
1. FACP technical and operational manual
2. Technical data sheets of all submitted products and accessories data with manual of installation and operation.
3. Devices list (filled in)
4. Manufacturer’s instruction for system maintenance and recharge.
C. Drawings and Calculation Notes
1. Detailed installation drawings of the complete detection and suppression system.
2. Include manufacturer's name(s), model numbers, ratings, power requirements, equipment layout, device arrangement, complete wiring point-to-point diagrams, and conduit layouts.
3. Sufficient information, clearly presented, shall be included to determine compliance with drawings and specifications.
4. AS-BUILT drawings after system commission
5. Wiring diagram of the FACP and all connected devices
6. Battery sizing calculation notes
D. Certificates
1. Product certificate of all components including:
a. FACP
b. Detectors
c. Abort push button
d. Siren
e. Strobe
f. Pressure switch
2. Site commissioning certificate – Signed
1.4 QUALITY ASSURANCE
A. Manufacturer: The manufacturer of the system components shall have minimum of 10 years’ experience in the manufacture and design of fire detection systems and control equipment.
B. Installer: The installer shall be authorized and trained by manufacturer to design, install, and maintain fire detection systems.
C. All system components must be approved by Loss Prevention Certification Board (LPCB).
1.5 WARRANTY
A. Equipment
1. The supplied products shall be covered by full supplier warranty for a minimum period of one (1) year from commissioning date at a full repair and replacement service.
2. Warranty shall include all defected spare parts and workmanship.
B. Services
1. Installation and dismantling
a. The supplier is responsible for the dismantling, hoisting, transportation and re-installation for parts that cannot be repaired or replaced on site
2. Part replacement/repair
a. For any part replacement or repair service the warranty for the repaired or new part shall be a minimum of 6 (six) months from the date of receipt of the repaired or new part. In case a part was repaired twice already under this warranty and the equipment becomes faulty again within up to six months the Operator on its discretion may request replacement of the complete equipment
3. Major defect
a. In case of major defect in the supplied products, the Operator reserves the right to reject the equipment. The supplier shall replace the defected system/parts under no cost from the Operator, including dismantling, hoisting, transportation and re-installation
2 PRODUCTS
2.1 MANUFACTURERS
1. The FACP and peripheral devices shall be manufactured 100% by a single manufacturer (or division thereof).
2. The fire alarm system shall be manufactured by an ISO 9001 certified company and meet the requirements of BS EN9001: ANSI/ASQC Q9001:2015.
2.2 GENERAL
A. System includes detectors, sound and visual alarms manual release/abort stations and control panel. The detectors to be as shown on drawings and shall conform to the relevant electrical specifications sections.
B. Used to operate a single or multiple fire alarm system based on inputs received from fire detection devices.
C. Circuits to be configured using cross, counting and independent or priority-zone concepts.
D. Provision should be made to alert plant staff that extinguishing agent has been dis-charged.
2.3 SYSTEMS OPERATIONAL DESCRIPTION
A. Fire-alarm signal initiation shall be by one or more of the following devices and systems:
1. Manual stations
2. Heat detectors
3. Smoke detectors
4. Duct smoke detectors.
5. Verified automatic alarm operation of smoke detectors.
6. Heat detectors in elevator shaft and pit.
7. Fire-extinguishing system operation
B. Fire-alarm signal shall initiate the following actions:
1. Continuously operate alarm notification appliances.
2. Identify alarm at fire-alarm control unit and remote annunciators.
3. Transmit an alarm signal to the remote alarm receiving station.
4. Unlock electric door locks in designated egress paths.
5. Release fire and smoke doors held open by magnetic door holders.
6. Activate voice/alarm communication system.
7. Switch heating, ventilating, and air-conditioning equipment controls to fire-alarm mode.
8. Activate smoke-control system (smoke management) at firefighter smoke-control system panel.
9. Activate stairwell and elevator-shaft pressurization systems.
10. Close smoke dampers in air ducts/HVAC units of designated air-conditioning duct systems serving zone where alarm was initiated.
11. Activate emergency lighting control in assembly spaces.
12. Activate emergency shutoffs for gas, fuel and power supplies for equipment under kitchen hoods. Provide additional contactors and relays and pushbuttons to control and monitor hoods, valves, makeup fans and equipment.
13. Record events in the system memory.
C. Supervisory signal initiation shall be by one or more of the following devices and actions:
1. Valve supervisory switch
2. Low pressure switch of an extinguishing agent cylinders.
D. System trouble signal initiation shall be by one or more of the following devices and actions:
1. Open circuits, shorts, and grounds in designated circuits.
2. Opening, tampering with, or removing alarm-initiating and supervisory signal-initiating devices.
3. Loss of primary power at fire-alarm control panel (FACP).
4. Ground or a single break in fire-alarm control unit internal circuits.
5. Abnormal ac voltage at fire-alarm control panel (FACP).
6. Break in standby battery circuitry.
7. Failure of battery charging.
8. Abnormal position of any switch at fire-alarm control unit or annunciator.
9. System Trouble and Supervisory Signal Actions: Initiate notification appliance and annunciate at fire-alarm control unit and remote annunciators.
2.4 FIRE ALARM CONTROL PANEL (FACP)
A. General Description
1. Modular, power-limited design with electronic modules, BS/LPCB or UL/FM listed.
2. Addressable initiation devices that communicate device identity and status.
a. Smoke sensors shall additionally communicate sensitivity setting and allow for adjustment of sensitivity at the FACP.
b. Temperature sensors shall additionally test for and communicate the sensitivity range of the device.
3. Addressable control circuits for operation of mechanical equipment.
B. Alphanumeric Display and System Controls: Arranged for interface between human operator at the FACP and addressable system components including annunciation and supervision. Display alarm, supervisory, and component status messages and the programming and control menu:
1. Annunciator and Display: Liquid-crystal type, six inch, 640 characters, minimum.
2. Keypad: Arranged to permit entry and execution of programming, display, and control commands; and to indicate control commands to be entered into the system for control of smoke-detector sensitivity and other parameters.
C. FACP User Interface: System events shall be stored in one of four event queues represented by alarm, supervisory, trouble or monitor. The alarm event shall have priority over the supervisory, trouble, and monitor event queues with the ability to alternate between queues with a single button depression. On the activation of a system event the following sequence shall occur:
1. On Alarm: The FACP interface shall display the first alarm event with the ability to scroll to the subsequent alarm events via the Alarm Queue button. The FACP interface shall on alarm display the following:
a. The Alarm Queue Led flashes indicating an alarm status is present.
b. A custom message is displayed detailing location.
c. The display shall indicate the number of active alarms present on the system.
d. The Alarm event status shall be identified as an active or restored event.
e. The Floor alarm zone LED is illuminated red indicating which floor(s) are in alarm.
f. The Floor Output LED is illuminated green indicating which floor(s) are sounding.
g. Alarm event acknowledge sequence shall execute as follows:
1) The Alarm Queue button will sequentially step the operator through the alarm events, acknowledging the event on each Alarm Queue button depression. On the completion of acknowledging all alarm events, the Alarm Queue Led illuminates steady.
2) A secondary means to view the alarm events shall be available via the up and down arrows. The Alarm Queue button shall return the display to the last acknowledged event.
3) The FACP shall be capable of reset, alarm silence, and trouble silence by the Operator free of the need for 100 percent operator acknowledgement of prior events.
2. On Supervisory: The FACP interface shall display the first supervisory event with the ability to scroll to the subsequent supervisory events via the Supervisory Queue button. The FACP interface shall on supervisory display the following:
a. The Supervisory Queue Led flashes indicating a Supervisory status is present.
b. A custom message is displayed detailing location.
c. The display shall indicate the number of active Supervisory(s) present on the system.
d. The Supervisory event status shall be identified as active or restored.
e. The Floor supervisory zone LED is illuminated amber indicating which floor(s) are in supervisory.
f. Supervisory event acknowledge sequence shall execute as follows:
1) The Supervisory Queue button will sequentially step the operator through the supervisory events, acknowledging the event on each Supervisory Queue button depression. On the completion of acknowledging all supervisory events, the Supervisory Queue Led illuminates steady.
2) A secondary means to view the supervisory events shall be available via the up and down arrows. The Supervisory Queue button shall return the display to the last acknowledged event.
3) The FACP shall be capable of reset, alarm silence, and trouble silence by the Operator free of the need for 100 percent operator acknowledgement of prior events.
3. On Trouble: The FACP interface shall display the first Trouble event with the ability to scroll to the subsequent Trouble events via the Trouble Queue button. The FACP interface shall on Trouble display the following:
a. The Trouble Queue Led flashes indicating a Trouble status is present.
b. A custom message is displayed detailing location.
c. The display shall indicate the number of active Troubles present on the system.
d. The Trouble event status shall be identified as active or restored event.
e. The Floor alarm zone trouble LED flashes amber indicating which floor(s) are in trouble.
f. Trouble event acknowledge sequence shall execute as follows:
1) The Trouble Queue button will sequentially step the operator through the trouble events, acknowledging the event on each Trouble Queue button depression. On the completion of acknowledging all trouble events, the Trouble Queue Led illuminates steady.
2) A secondary means to view the trouble events shall be available via the up and down arrows. The Trouble Queue button shall return the display to the last acknowledged event.
3) The FACP shall be capable of reset, alarm silence, and trouble silence by the Operator free of the need for 100 percent operator acknowledgement of prior events.
4. On Monitor: The FACP interface shall display the first Monitor event with the ability to scroll to the subsequent Monitor events via the Monitor Queue button. The FACP interface shall on Monitor display the following:
a. The Monitor Queue Led flashes indicating a monitor status is present.
b. A custom message is displayed detailing location.
c. The display shall indicate the number of active Monitors present on the system.
d. The Monitor event status shall be identified as active or restored event.
e. Monitor event acknowledge sequence shall execute as follows:
1) The Monitor Queue button will sequentially step the operator through the monitor events, acknowledging the event on each Monitor Queue button depression. On the completion of acknowledging all monitor events, the Monitor Queue Led illuminates steady.
2) A secondary means to view the monitor events shall be available via the up and down arrows. The Monitor Queue button shall return the display to the last acknowledged event.
3) The FACP shall be capable of reset, alarm silence, and trouble silence by the Operator free of the need for 100 percent operator acknowledgement of prior events.
D. Circuits
1. Signaling Line Circuits: NFPA 72, Class B, Style 4.
a. System Layout: Install no more than 50 percent capacity addressable devices on each signaling line circuit (not to exceed 60 devices per loop maximum).
2. Notification-Appliance Circuits: NFPA 72, Class B, Style Y.
a. Audible/Speaker Circuit: No more than 50 percent capacity.
b. Visual Circuit: No more than 50 percent capacity.
3. Actuation of alarm notification appliances, emergency voice communications, annunciation, smoke control, and actuation of suppression systems shall occur within 10 seconds after the activation of an initiating device.
4. Electrical monitoring for the integrity of wiring external to the FACP for mechanical equipment shutdown providing a break in the circuit will cause mechanical equipment to shut down.
E. Notification-Appliance Circuit: Operation shall sound in a three pulse temporal pattern.
1. A pre-recorded digital voice message, complying with ANSI S3.41 shall be provided but not activated.
2. Amplifier output voltage shall be 70 volts with speakers connected at 70 volts.
F. Alarm Silencing, Trouble, and Supervisory Alarm Reset: Manual reset at the FACP after initiating devices are restored to normal.
1. Silencing-switch operation halts alarm operation of audible notification appliances and activates an "alarm silence" light. Display of identity of the alarm zone or device is retained. The visual notification appliances shall continue to operate.
2. Subsequent alarm signals from other devices or zones reactivate notification appliances until silencing switch is operated again.
3. When alarm-initiating devices return to normal and system reset switch is operated, notification appliances operate again until alarm silence switch is reset.
G. Walk Test: A test mode to allow one person to test alarm and supervisory features of initiating devices. Enabling of this mode shall require the entry of a password. The FACP and annunciators shall display a test indication while the test is underway. If testing ceases while in walk-test mode, after a preset delay, the system shall automatically return to normal.
H. Remote Smoke-Detector Sensitivity Adjustment: Controls shall select specific addressable smoke detectors for adjustment, display their current status and sensitivity settings, and control of changes in those settings. Allow controls to be used to program repetitive, time-scheduled, and automated changes in sensitivity of specific detector groups. Record sensitivity adjustments and sensitivity-adjustment schedule changes in system memory, and make a print-out of the final adjusted values on the system printer.
I. Transmission to Remote Alarm Receiving Station: Automatically transmit alarm, trouble and water flow through auxiliary contacts connected to the existing security system panel and through existing central control building energy management panel.
J. Voice/Alarm Signaling Service: A central emergency communication system with microphone, preamplifier, amplifier, and tone generator located in the FACP.
1. System shall be capable of indicating number of alarm channels for automatic, simultaneous transmission of different announcements to different zones, or for manual transmission of announcements by use of the central-control microphone. Amplifiers shall be BS listed.
a. Allow the application of and evacuation signal to indicated number of zones and, at the same time, allow voice paging to the other zones selectively or in any combination.
b. Programmable tone and message sequence selection.
c. Standard digitally recorded messages for "Evacuation" and "All Clear”.
d. Generate tones to be sequenced with audio messages of the type recommended by NFPA 72 and that are compatible with tone patterns of the notification-appliance circuits of the FACP.
2. Status Annunciator: Indicate the status of various voice/alarm speaker zones.
K. Portable Printer: Ports shall be RS-232 for system printer.
1. Provide printer interface card for unsupervised interface with printer.
2. Provide printer in nearest mechanical or communication room closest to FACP.
L. Printout of Events: On receipt of signal, when printer is installed, print alarm, supervisory, and trouble events. Identify zone, device, and function. Include type of signal (alarm, supervisory, or trouble), and date and time of occurrence. Differentiate alarm signals from all other printed indications. Also print system reset event, including the same information for device, location, date, and time. Commands initiate the printing of a list of existing alarm, supervisory, and trouble conditions in the system and a historical log of events.
M. Primary Power: 24-V dc obtained from 220Vac service and a power-supply module. Initiating devices, notification appliances, signaling lines, trouble signal, supervisory signal shall be powered by the 24Vdc source.
1. The alarm current draw of the entire fire alarm system shall not exceed 80 percent of the power-supply module rating.
N. Secondary Power: Provide standby batteries with charger for operation of the system in the supervisory mode for up to 24 hours followed by a minimum of 15 minutes of an alarm condition in the event of power failure.
1. Batteries: Sealed lead calcium.
2. Battery and Charger Capacity: Comply with NFPA 72.
3. Submit substantiating battery calculations for supervisory and alarm power requirements.
4. Include power (Watts) requirements for each system component and each panel component, and the battery-recharging period.
O. Surge Protection:
1. Install surge protection on normal ac power for the FACP and its accessories.
2. Install surge protectors recommended by FACP manufacturer. Install on all system wiring external to the building housing the FACP.
P. Event History Log: Minimum 300-event history log of alarm, trouble and sprinkler supervisory alarm conditions and shall be complete with one-man system walk test.
Q. Provide FACP or remote panels sized to accommodate a minimum of two additional initiation, two speakers and four strobe circuits.
R. Provide minimum of fourteen sets of normally open and normally closed auxiliary contacts (two for alarm, two for trouble, two for waterflow, two for first smoke, and six spare).
2.5 ABORT PUSH BUTTON
A. Abort push button (APB) shall be white in color with a red, momentary pushbutton.
B. Abort push button should be lockable. Turn to release abort push button.
C. Installed at 1.5m from floor level
D. Similar to Telemecanique XB4-BS542 and fitted on metallic box similar to Telemecanique XAP-M1201.
2.6 PRESSURE SWITCH
A. Pressure switch rating: 250 bar
B. The pressure switch is mounted either in the distribution pipework or on the manifold and may be used to provide an electrical indication of the release of CO2, to perform ventilation shut-downs or to initiate indication of gas trapped in manifold where there are stop valves in the distribution pipework.
C. Sends signal to FACP when CO2 gas is released
D. The pressure switch requires to be manually reset following operation
E. A minimum pressure of 3 bar is required to ensure satisfactory operation.
F. Connection to the pressure switch may be either 1/2″ NPT (male) or 1/4″ NPT (female).
2.7 MANUAL FIRE ALARM STATIONS
A. Manual fire alarm stations shall conform to the applicable requirements of BS.
B. Connect manual stations into signal line circuits. Stations shall be installed on surface mounted outlet boxes at 1400 mm.
C. Stations shall be double action type.
D. Stations shall be finished in red, with raised letter operating instructions of contrasting color.
E. Stations requiring the breaking of glass or plastic panels for operation are not acceptable. Stations employing glass rods are not acceptable.
F. The use of a key shall be required to reset the station.
G. Gravity or mercury switches are not acceptable. Switches and contacts shall be rated for the voltage and current upon which they operate.
H. Stations shall have a separate screw terminal for each conductor. Surface mounted boxes shall be matched and painted the same color as the mounting surface.
2.8 PHOTOELECTRIC SMOKE DETECTOR
A. Smoke detectors shall be designed for detection of abnormal smoke densities.
B. Detectors shall be four-wire type.
C. Integral Addressable Module: Arranged to communicate detector status (normal, alarm, or trouble) to fire-alarm control unit.
D. Base Mounting: Detector and associated electronic components shall be mounted in a twist-lock module that connects to a fixed base. Provide terminals in the fixed base for making wiring connections.
E. Self-Restoring: Detectors do not require resetting or readjustment after actuation to restore them to normal operation.
F. EN54 approved by LPCB
G. Detectors shall contain a visible indicator LED that shows when the unit is in alarm condition.
H. Detector address shall be accessible from fire-alarm control unit and shall be able to identify the detector's location within the system and its sensitivity setting.
I. An operator at fire-alarm control unit, having the designated access level, shall be able to manually access the following for each detector:
1. Primary status.
2. Device type.
3. Present average value.
4. Present sensitivity selected.
5. Sensor range (normal, dirty, etc.).
J. Detectors shall not be adversely affected by vibration or pressure.
K. Detectors that are to be installed in concealed (above false ceilings, etc.) locations shall be provided with a remote indicator LED suitable for mounting in a finished, visible location.
L. Optical detectors shall be used
M. Detectors shall operate on a light scattering concept using an LED light source.
N. Failure of the LED shall not cause an alarm condition. Detectors shall be factory set for sensitivity and shall require no field adjustments of any kind.
O. Diode base allowing the monitoring of a removed detector with BS 5839.
2.9 FIXED TEMPERATURE DETECTOR
A. Heat detectors shall be designed for detection of fire by fixed temperature.
B. Detectors shall be four-wire type.
C. Integral Addressable Module: Arranged to communicate detector status (normal, alarm, or trouble) to fire-alarm control unit.
D. Base Mounting: Detector and associated electronic components shall be mounted in a twist-lock module that connects to a fixed base. Provide terminals in the fixed base for making wiring connections.
E. Self-Restoring: Detectors do not require resetting or readjustment after actuation to restore them to normal operation.
F. EN54 approved by LPCB
G. Integral Addressable Module: Arranged to communicate detector status (normal, alarm, or trouble) to fire-alarm control unit.
H. Detectors shall be designed for surface outlet box mounting and supported independently of wiring connections.
I. Detectors shall be designed to detect high heat.
J. The detectors shall have a specific temperature setting of 57.2°C
K. Diode base allowing the monitoring of a removed detector with BS 5839.
A. Detectors located in areas subject to moisture, exterior atmospheric conditions, or hazardous locations as defined by NFPA 70 and as shown on drawings, shall be types approved for such locations.
2.10 RATE COMPENSATION DETECTOR
A. Heat detectors shall be designed for detection of fire by rate-compensating principle.
B. Detectors shall be four-wire type.
C. Integral Addressable Module: Arranged to communicate detector status (normal, alarm, or trouble) to fire-alarm control unit.
D. Base Mounting: Detector and associated electronic components shall be mounted in a twist-lock module that connects to a fixed base. Provide terminals in the fixed base for making wiring connections.
E. Self-Restoring: Detectors do not require resetting or readjustment after actuation to restore them to normal operation.
F. EN54 approved by LPCB
G. Detectors shall be surface mounted horizontal and vertical type, with outlet box supported independently of wiring connections.
H. Detectors shall be hermetically sealed and automatically resetting.
I. Rate Compensated detectors shall be rated for 15 by 15m.
J. Diode base allowing the monitoring of a removed detector with BS 5839.
K. Detectors located in areas subject to moisture, exterior atmospheric conditions, or hazardous locations as defined by NFPA 70 and as shown on drawings, shall be types approved for such locations.
2.11 COMBINATION FIXED-TEMPERATURE AND RATE OF RISE DETECTOR
A. Heat detectors shall be designed for detection of fire by combination fixed temperature and rate-of-rise principle.
B. Detectors shall be four-wire type.
C. Integral Addressable Module: Arranged to communicate detector status (normal, alarm, or trouble) to fire-alarm control unit.
D. Base Mounting: Detector and associated electronic components shall be mounted in a twist-lock module that connects to a fixed base. Provide terminals in the fixed base for making wiring connections.
E. Self-Restoring: Detectors do not require resetting or readjustment after actuation to restore them to normal operation.
F. Detectors shall be designed for surface outlet box mounting and supported independently of wiring connections.
G. Contacts shall be self-resetting after response to rate-of-rise principle.
H. Under fixed temperature actuation, the detector shall have a permanent external indication which is readily visible.
I. Detector units located in boiler rooms, showers, or other areas subject to abnormal temperature changes shall operate on fixed temperature principle only.
J. The rating for the fixed temperature portion shall be 57.2°C.
K. The rating for the Rate-of-Rise detectors shall be rated for 15 by 15m.
L. Diode base allowing the monitoring of a removed detector with BS 5839.
2.12 REMOTE LED INDICATOR
A. Remote Indicator is used where a detector LED is not visible i.e., when the detector is mounted in a roof void, lift shaft etc.
2.13 FLAME DETECTOR
A. The detectors shall be sensitive to the micron range best suited for their intended use.
B. Detectors shall be four-wire type.
C. Integral Addressable Module: Arranged to communicate detector status (normal, alarm, or trouble) to fire-alarm control unit.
D. Base Mounting: Detector and associated electronic components shall be mounted in a twist-lock module that connects to a fixed base. Provide terminals in the fixed base for making wiring connections.
E. Self-Restoring: Detectors do not require resetting or readjustment after actuation to restore them to normal operation.
F. The detectors shall operate over electrically supervised wiring circuits and the loss of power to the detector shall result in a trouble signal.
G. A self-test feature shall be provided for each detector to be individually tested.
2.14 INFRARED (IR) SINGLE FREQUENCY FLAME DETECTOR
A. The detector shall comply with BS guide.
B. Detectors shall be four-wire type.
C. Integral Addressable Module: Arranged to communicate detector status (normal, alarm, or trouble) to fire-alarm control unit.
D. Base Mounting: Detector and associated electronic components shall be mounted in a twist-lock module that connects to a fixed base. Provide terminals in the fixed base for making wiring connections.
E. Self-Restoring: Detectors do not require resetting or readjustment after actuation to restore them to normal operation.
F. The detector shall operate over electrically supervised wiring circuits and the loss of power to the detector shall result in a trouble signal.
G. The detector shall be sensitive in the range of 4.4 to 4.6 μm only.
H. A self-test feature shall be provided for each detector to be individually tested.
2.15 ULTRAVIOLET (UV) FLAME DETECTOR
A. The detector shall comply with BS guide.
B. Detectors shall be four-wire type.
C. Integral Addressable Module: Arranged to communicate detector status (normal, alarm, or trouble) to fire-alarm control unit.
D. Base Mounting: Detector and associated electronic components shall be mounted in a twist-lock module that connects to a fixed base. Provide terminals in the fixed base for making wiring connections.
E. Self-Restoring: Detectors do not require resetting or readjustment after actuation to restore them to normal operation.
F. The detector shall operate over electrically supervised wiring circuits and the loss of power to the detector shall result in a trouble signal.
G. UV flame detector shall be of the narrow band response type which operates on radiated ultraviolet energy and shall be sensitive in the range of 0.185 - 0.260 μm only.
H. The detector shall be sensitive in the range of 185 to 260nm.
I. The cone of vision shall be 120 degrees.
J. Each detector shall be completely insensitive to light sources in the visible frequency range.
K. A self-test feature shall be provided for each detector to be individually tested.
2.16 COMBINATION UV/IR FLAME DETECTOR
A. The detector shall comply with BS guide.
B. Detectors shall be four-wire type.
C. Integral Addressable Module: Arranged to communicate detector status (normal, alarm, or trouble) to fire-alarm control unit.
D. Base Mounting: Detector and associated electronic components shall be mounted in a twist-lock module that connects to a fixed base. Provide terminals in the fixed base for making wiring connections.
E. Self-Restoring: Detectors do not require resetting or readjustment after actuation to restore them to normal operation.
F. The detector shall operate over electrically supervised wiring circuits and the loss of power to the detector shall result in a trouble signal.
G. The UV/IR detector shall provide discrimination against false alarms by requiring both UV and IR flame detection before an alarm is sent.
H. The UV sensor shall be sensitive in the range of 0.185 to 0.265 micrometers only.
I. The IR sensor shall be sensitive in the range of 0.185 - 0.260 μm only.
J. Detectors shall be completely insensitive to light sources in the visible frequency range.
K. A self-test feature shall be provided for each detector to be individually tested.
2.17 HORN
A. Horn shall have a separate screw terminal for each conductor.
B. Individually addressed, connected to a signaling line circuit, equipped for mounting as indicated and with screw terminals for system connections.
C. Horn shall be painted red.
D. Horns shall be surface mounted, with the matching mounting back box surface mounted vibrating type suitable for use in an electrically supervised circuit.
E. Horn to be fitted to its original surface mounting box.
F. Horns shall produce a sound rating of at least 92 dBA at 3m.
G. Horn should offer two (2) distinct prioritized audible signals from two isolated inputs.
H. Priority one (1) will override all other commands upon activation.
I. Horns used in exterior locations shall be specifically listed or approved for outdoor use and be provided with metal housing.
2.18 STROBE
A. Strobe shall have clear high intensity optic lens, xenon flash tubes, and output white light.
B. Individually addressed, connected to a signaling line circuit, equipped for mounting as indicated and with screw terminals for system connections.
C. Strobe flash rate shall be between 1 to 3 flashes per second and a minimum of 75 candela.
D. Strobe shall be surface mounted with engraved letters “FIRE”, 25mm text height.
E. Strobe light is activated in case of agent release
F. Strobe to be fitted to its original surface mounting box
G. Strobe used in exterior locations shall be specifically listed or approved for outdoor use and be provided with metal housing.
2.19 COMBINED HORN/STROBE
A. Combined horn/strobe shall provide the same requirements as individual units, except that they shall mount as a unit in standard back boxes.
B. Individually addressed, connected to a signaling line circuit, equipped for mounting as indicated and with screw terminals for system connections.
C. Units shall be factory assembled.
2.20 MAGNETIC DOOR HOLDERS
A. Magnetic door holder units are equipped for wall or floor mounting as indicated and are complete with matching doorplate.
B. Requires no more than 3W to develop 111-N holding force.
C. Flush mounted unless otherwise indicated.
D. Rating: 24-V ac or dc.
E. Material and Finish: Match door hardware.
2.21 ADDRESSABLE CONTROL MODULE
A. Microelectronic monitor module for use in providing a system address for alarm-initiating devices for wired applications with normally open/closed contacts.
B. Integral Relay: NO/NC contact pairs rated at 1A 220Vac or 24Vdc for fan shut down and smoke damper closure.
2.22 LUMINOUS EVACUATE SIGN
A. Internal luminous warning sign, 10cd, with red letterings: “CO2 Release – Evacuate Immediately” or “FIRE ALARM”.
B. Lighting with high luminosity LED - IP55
C. Internal luminous warning sign is activated on the second stage.
2.23 REMOTE ANNUNCIATOR
A. Description: Annunciator functions shall match those of fire-alarm control unit for alarm, supervisory, and trouble indications. Manual switching functions shall match those of fire alarm control unit, including acknowledging, silencing, resetting, and testing.
1. Mounting: Flush or surface cabinet, NEMA 250, Type 1 (flush where possible).
B. Display Type and Functional Performance: Alphanumeric display and LED indicating lights shall match those of fire-alarm control unit. Provide controls to acknowledge, silence, reset, and test functions for alarm, supervisory, and trouble signals.
2.24 WARNING PLATES
A. Door Caution Plate
1. The door caution plate provides instructions to personnel who may enter a CO2 protected area.
2. Door caution plate shall be affixed on the external side of doors in every protected space where it is determined that carbon dioxide could migrate, creating a hazard to personnel and at each entrance to Carbon dioxide storage rooms.
3. Door caution plate text should be: “CO2 – CAUTION! – Do not enter unless CO2 system is isolated (locked off) – When alarm sounds evacuate hazard area – After CO2 discharge do NOT re-enter until thoroughly ventilated”
4. Warning sign dimensions: 210x210mm
B. Manual Release Caution Plate
1. The manual release caution plate provides instructions to personnel on the use of manual controls.
2. One plate is to be fixed adjacent to all positions from where CO2 can be released manually.
3. Warning sign text should be: “CO2 – RELEASE – Manual Control Point – CO2 – CAUTION – Ensure all personnel are evacuated before releasing CO2”
2.25 WIRING
A. Wiring shall conform to NFPA 70.
B. Fire resistant and flame retardant control cables, BS6387, shall be utilized to connect the different devices of the fire detection system
C. Power cable 3x1.5mm² shall be used to connect the FACP to the electrical distribution panel (220Vac)
D. Wiring for fire alarm circuits shall be 1.5mm² cross-section, solid copper, five conductors, color coded, with red colored jacket
E. Wiring code color shall remain uniform throughout the circuit.
F. Conductors used for the same functions shall be similarly color coded.
G. Voltages shall not be mixed in any junction box, housing, or device, except those containing power supplies and control relays.
H. System field wiring shall be solid copper and installed in rigid fire retarded plastic conduit. Electrical metallic tubing will be used where indicated on drawings or where cables run in hazardous area.
I. Pigtail or T-tap connections to initiating device circuits, supervisory alarm circuits, and notification appliance circuits are prohibited.
2.26 LABELS
A. FACP shall be clearly labeled identifying:
1. Manufacturer
2. Model
3. Origin of manufacturer
4. Date of manufacturing
B. FACP electrical wiring diagram should be provided inside the FACP
C. All wires inside the FACP should be numbered
D. Additional components inside the FACP should be labeled
E. Abort push button and smoke detectors should be labeled
2.27 SPARE PARTS
A. Furnish the following spare parts:
1. Two of each type detector installed.
4. One of each type of audible and visual alarm device installed.
5. Five of each type of fuse required by the system.
6. Three complete sets of system keys
2.28 ACCESSORIES
1. All accessories necessary for the installation and proper operation of the system should be delivered with the system free of charge.
2.29 DEVICES LIST
A. The device list should be filled in and submitted with the technical offer. A soft copy is provided.
3 EXECUTION
3.1 INSTALLATION
A. All work shall be installed as shown, and in accordance with NFPA 70 and NFPA 72, and in accordance with the manufacturer's diagrams and recommendations, unless otherwise specified.
B. Smoke detectors shall not be installed until construction is essentially complete and the building has been thoroughly cleaned.
C. Power Supply for the System
1. A single dedicated circuit connection for supplying power from a branch circuit to each fire alarm system shall be provided.
2. The power shall be supplied as shown on the drawings.
3. The power supply shall be marked in red with the words "FIRE ALARM”.
D. Wiring
1. Conduit size for wiring shall be in accordance with NFPA 70.
2. Wiring for the fire alarm system shall not be installed in conduits, junction boxes, or outlet boxes with conductors of lighting and power systems.
3. Not more than two conductors shall be installed under any device screw terminal.
4. The wires under the screw terminal shall be straight when placed under the terminal then clamped in place under the screw terminal.
5. The wires shall be broken and not twisted around the terminal.
6. Circuit conductors entering or leaving any mounting box, outlet box enclosure, or cabinet shall be connected to screw terminals with each terminal and conductor marked in accordance with the wiring diagram.
7. Connections and splices shall be made using screw terminal blocks.
8. The use of wire nut type connectors in the system is prohibited.
9. Wiring within any control equipment shall be readily accessible without removing any component parts.
10. The fire alarm equipment manufacturer's representative shall be present for the connection of wiring to the control panel.
E. Control Panel
1. The control panel and its assorted components shall be mounted so that no part of the enclosing cabinet is less than 1600 mm nor more than 1800 mm above the finished floor.
2. Manually operable controls, such as abort push button, shall be at 1500mm above the finished floor.
F. Detectors
1. Detectors shall be located and installed in accordance with NFPA 72.
2. Detectors shall be connected into signal line circuits or initiating device circuits as indicated on the drawings.
3. Detectors shall be at least 300 mm from any part of any lighting fixture.
4. Detectors shall be located at least 900 mm from diffusers of air handling systems.
5. Each detector shall be provided with appropriate mounting hardware as required by its mounting location.
6. Detectors which mount in open space shall be mounted directly to the end of the stubbed down rigid conduit drop.
7. Conduit drops shall be firmly secured to minimize detector sway.
8. Where length of conduit drops from ceiling or wall surface exceeds 900 mm, sway bracing shall be provided.
9. Detectors installed in concealed locations (above ceiling, raised floors, etc.) shall have a remote visible indicator LED/LCD as indicated.
G. Notification Appliances
1. Notification appliances shall be mounted 2000 mm above the finished floor or 150 mm below the ceiling, whichever is lower.
H. Alarm Contacts
1. Alarm contacts, 1st stage, 2nd stage, and trouble, should be connected to existing alarm distribution frame.
2. Alarm contacts should be voltage free and normally closed.
I. GROUNDING
1. Provide grounding by connecting to existing ground system.
3.2 TRAINING
A. Provide training course for the operations and maintenance staff.
B. Conduct the course in the building where the system is installed or as designated by the MIC1 engineer.
C. Submit lesson plans, operating instructions, maintenance procedures, and training data, furnished in manual format, for the training courses.
D. The operations training shall familiarize designated personnel with proper operation of the fire alarm system.
E. The training period for systems operation shall consist of 1 training day and shall start after the system is functionally completed but prior to final acceptance tests.
3.3 TESTING
A. Notify the MIC1 engineer at least 2 days before the preliminary and acceptance tests are to be conducted.
B. Perform the tests in accordance with the approved test procedures in the presence of the MIC1 engineer.
C. The control panel manufacturer's representative shall be present to supervise tests.
D. Furnish instruments and personnel required for the tests.
1. Submit detailed test procedures, prepared and signed by a Registered Professional Engineer, for the fire detection and alarm system 1 day prior to performing system tests.
2. Submit test reports, in booklet form, showing field tests performed to prove compliance with the specified performance criteria, upon completion and testing of the installed system.
3. Each test report shall document readings, test results and indicate the final position of controls.
4. Include the NFPA 72 Certificate of Completion and NFPA 72 Inspection and Testing Form, with the appropriate test reports.
E. Preliminary Tests
1. Upon completion of the installation, subject the system to functional and operational performance tests including tests of each installed initiating and notification appliance, when required.
2. Tests shall include the meggering of system conductors to determine that the system is free from grounded, shorted, or open circuits. Conduct the megger test prior to the installation of fire alarm equipment. If deficiencies are found, corrections shall be made and the system shall be retested to assure that it is functional.
3. After completing the preliminary testing complete and submit the NFPA 72, Certificate of Completion.
F. Acceptance Test
1. Do not perform acceptance testing until the Contractor has completed and submitted the Certificate of Completion.
2. Testing shall be in accordance with NFPA 72.
3. The recommended tests in NFPA 72 shall be considered mandatory and shall verify that previous deficiencies have been corrected.
4. Complete and submit the NFPA 72, Inspection and Testing Form.
5. The test shall include all requirements of NFPA 72 and the following:
a. Test of each function of the control panel.
b. Test of each circuit in both trouble and normal modes.
c. Tests of each alarm initiating devices in both normal and trouble conditions.
d. Tests of each control circuit and device.
e. Tests of each alarm notification appliance.
f. Tests of the battery charger and batteries.
g. Complete operational tests under emergency power supply.
h. Visual inspection of wiring connections.
i. Opening the circuit at each alarm initiating device and notification appliance to test the wiring supervisory feature.
j. Ground fault.
k. Short circuit faults.
l. Stray voltage.
m. Loop resistance.
3.4 SITE DOCUMENT
A. A wiring drawing of the FACP (3 copies)
B. Devices List
C. Battery size calculations
D. AS BUILT plans
E. FACP technical and operating manual
F. Certificate of testing and commissioning
END OF SECTION

## Grade of Compliancy
| RFT Compliance Matrix | Reference Number | SF-CF-25
|  | Owner | PRO
|  | Revision Code | 3.0
|  | Implementation Date | 2024-03-01
Grade of Compliance range from 0 to 15 with a step of 1 unit:
15 : Compliant with additional value, not initially included in the requirements
10 : Fully compliant
4 - 5 - 6: Partially compliant
0 : Not compliant
K : Disqualification