## General Requirements
| RFT Compliance Matrix |  |  |  | Reference Number | SF-CF-25
[5 empty] | Owner | PRO
[5 empty] | Revision Code | 3.0
[5 empty] | Implementation Date | 2024-03-01
Project Name:
Reference Number:
RFT Article (Part Number or Title) | Requirements (Description) | Killer | Fully Compliant | Partially Compliant | Non-Compliant | Reference (Specify document & page nb)
Article 4 | Conditions for the Participation of the Eligible Bidders
4.1 | 1- Bidders shall meet the following conditions, declared in accordance with the required documents in the First section of this Article mentioned below as (First: Envelope No. (1) Administrative Documents and Transactions):
a- That there is no proven violation, by the bidders, of professional ethics generally accepted and stipulated in the relevant provisions, if any;
b- Bidders have the legal capacity to enter into the procurement contract;
c- Bidders have fulfilled their obligations to pay taxes and social security contributions;
d- Bidders have not been convicted, neither their directors nor employees involved with the procurement process, by a court decision of any criminal offence - even if the verdict can still be appealed - related to their professional conduct or the making of false statements or misrepresentations as to their qualifications to enter into a procurement contract, or corrupting a public procurement or a contract awarding process, or have not been otherwise disqualified pursuant to administrative suspension or debarment proceedings, or have been in a situation of exclusion from participation in public procurements;
e- Bidders are not the subject of legal proceedings for insolvency or bankruptcy, or were declared bankrupt by a court of law;
f- Bidders have not been convicted by a court decision - even if the verdict can still be appealed - of usury or money laundering;
g- Bidders have not participated in the decision-making process of the contracting authority or have any conflict of interest, or any material interest linking them to any of the decision makers;
h- Any other conditions set forth by the contracting authority in the tender documents that are commensurate with the required works;
i- Certificate from the Ministry of Economy proving compliance with the provisions of the Law on Boycott of Israel for foreign companies (added by Law No. 309, dated April 19, 2023).
j- Declaration of the economic beneficiaries (according to Law No. 309, dated April 19, 2023).
4.2 | 2- The bid must be submitted clearly and unequivocally without any deletion, alteration, or modification.
4.3 | 3- The bidders state in their offer that they have reviewed the Tender document and its complementary documents and have obtained a copy. They accept and undertake to adhere to all the conditions outlined therein without any reservations or exceptions. The bidder submits their offer on this basis and affixes financial stamps worth fifty thousand Lebanese pounds covering all the documents.
4.4 | 4- Any bid containing reservations or exceptions is rejected.
4.5 | 5- The bidder mentions in their offer a clear address and place of residence for prompt communication.
Administrative Documents and Transactions | First: Envelope No. (1) Administrative Documents and Transactions
A- General Conditions:
1- Undertaking Letter (Declaration), according to the attached form, signed and stamped by the bidder, this Undertaking includes the bidder's confirmation of their commitment to the price and the validity of the offer. A financial stamp of 50,000 L.L. is affixed.
2- Commercial Circular specifying the authorized signatory of the bidder and a sample of their signature.
3- Legal Authorization: If the offer is signed by someone other than the person authorized to sign according to the commercial circular, it must be notarized by a notary public.
4- Police Record of the Authorized Signatory or his “legal representative”, not exceeding three months from the bid opening date.
5- Partnership Contract legalized by a notary public if required.
6- Registration Certificate before the Directorate of Value Added Tax, if applicable, or a certificate of non-registration if not subject to it. In the latter case, the bidder commits to their bid price even if they become registered for VAT during the execution period.
7- Registration Certificate issued by the Ministry of Finance – Department of Revenue.
8- Certificate issued by the Ministry of Finance proving the bidder's compliance with tax obligations.
9- Clearance Certificate from the National Social Security Fund “comprehensive or valid for participation in public tenders and bids” valid on the date of the bid opening session, stating that the bidder has paid all his subscriptions (the bidder must be registered before the National Social Security Fund and any statement mentioning the phrase “unregistered institution” will be rejected).
10- Certificate issued by the Municipality, proving full payment of municipal fees by the bidder, issued by the municipality within its jurisdiction based on the commercial registration certificate.
11- Comprehensive Certificate issued by the Commercial Register showing founders, members, contributors, or partners, authorized signatories, the manager, capital, the bidder's activity, and ongoing liabilities.
12- Certificate issued by the relevant authorities proving that the bidder is not in a state of bankruptcy.
13- Certificate issued by the relevant authorities proving that the bidder is not in a state of judicial liquidation.
14- Bid bond as required in the specific Tender document of the procurement project, in accordance with Articles 34 and 36 of the Public Procurement Law.
15- Declaration from the Bidder identifying the economic beneficiary/beneficiaries according to Form M18 issued by the Ministry of Finance (any natural person who owns or effectively controls the ultimate outcome of the activity practiced by the bidder, either directly or indirectly, whether the bidder is a natural person or a legal entity.)
16- Copies of Identification Cards (ID/Passport) for the economic beneficiary/beneficiaries.
17- Copies of Identification Cards (ID/Passport) for each person representing the bidder (those acting on behalf of the bidder in their relationship with the contracting authority: legal representative, representative of the legal entity, or authorized signatory).
18- Integrity Declaration Document signed by the bidder in accordance with the prescribed format
Miscellaneous | The bidder shall declare any relative relations with any Alfa employee up to the 4th degree under Clause 30 of the PPL, for MIC1 to be able to assess the existing of any potential conflict of interests which may lead to deprive the bidder from participating to the tender under the risk of disqualification.
The bidder or any of his employees, partners, agents, contributors, consultants, or their relatives shall declare any relationships that may lead to a conflict of interest in the subject of this contract.
Special Conditions | B- Special Conditions Regarding the Subject of the Contract:
Financial Qualifications | 1- Financial Qualifications (To be determined based on the size and nature of the contract).
Technical/Professional Qualifications | 2- Technical/Professional Qualifications (To be determined based on the nature of the contract):
1- Certificate from the Chamber of Commerce, Industry, and Agriculture confirming that the bidder is engaged in the activities related to the subject of the contract, valid as of the date of the bidding session and valid for participation in public tenders.
2- Clearance certificate from the Order of Engineers…
3- Clearance certificate from the Contractors Syndicate…
4- ISO certificate.
5- Five Certificates of good execution and completion for similar projects in terms of size and type.
6- Technical proposal according to the required specifications in the appendix (1) of the RFT.
7- Declaration of site inspection by the bidder, denying any unfamiliarity, according to the attached model.
Participation of a foreign bidder | C- In case of the participation of a foreign bidder, the bidder must comply with one of the following conditions:
1- is part of a coalition that includes at least one Lebanese company that meets the conditions required by the specific Tender document of the procurement project.
2- The personal presence of the legal representative of the company to participate in the procurement proceedings (not mandatory).
3- Has an authorized agent or representative in Lebanon responsible for signing the contract on its behalf.
In addition to the above conditions, the foreign bidder must submit the following:
1- Certificate registration of the company or certificate of establishment issued by the relevant authorities in their country.
2- Certificate from the Lebanese Ministry of Economy and Trade confirming compliance with the provisions of the Law on Israel Boycott.
3- The required certificates according to paragraph (First) above, according to the laws of the country where the bidder is located, provided that these certificates are authenticated according to the regulations of the competent authorities.
For certificates issued without an expiration date, the validity date of each certificate is determined according to its nature, not exceeding six months from the date of the bid opening session.
Information Security Specifications | Information Security Specifications Issuing Department to determine whether all or part of this Article is applicable to their specific RFT
The Bidder shall commit to refrain from offering any product / equipment which can cause security threat or information leakage that jeopardizes MIC1 network security. (K)
The Bidder shall accept that MIC1 runs a vulnerability scan on the proposed solution prior to issuing the acceptance and in case any vulnerability is found, the Bidder undertakes to take the necessary actions to remedy such vulnerability within _____________________ days from its notification.
The Bidder shall mention the security standards adopted/followed in designing the proposed solution.
The Bidder should specify if it has acquired the ISO27001 certification or any other equivalent security certification and submit with the Offer a copy of such certificate.
The Bidder shall not hard code passwords in the proposed solution.
The provided application should run without the need of root (unix) and / or admin (win) privileges.
Source code of proposed application should be owned by MIC1.
System shall allow generation of user, operator as well as alarms logs.
Solution and storage shall be sized to host history logs for at least 1 year back.
The Bidder should submit a data flow diagram and schema of the solution architecture.
In case of online payment, the Bidder shall use encryption. (K)
The Bidder shall harden systems servers / storage before being published online, and describe hardening aspects applied on each type.
The Bidder shall describe security checking and audits performed on the designed solution prior to putting it on the market.
The Bidder shall change default errors / messages and configuration.
Application should support role-based access, specific privileges per user (i.e specific access to application modules and reports)
Database should support restricted access per user or groups to data (i.e access per field or per table, …)
Encryption shall be used in all communications / interactions between systems, especially if the communication is through web access. Web based access shall always be used through HTTP+SSL.
Each user shall have only one account / profile to access data.
Least-privileges should always be specified on nodes / applications.
Pseudocode flow chart shall be provided by the Bidders.
The Bidder should commit to improve solution / systems information security weaknesses whenever needed or highlighted by MIC1 information security team.
Health, Safety and Environmental Specifications | To ensure that the proposed products and services bidders are compliant with HSE culture, bidders should state basic HSE specifications and compliance information:
Bidder shall provide the product’s specifications that have an environmental impact (power consumption, gas emissions, etc…)
Bidder shall provide the product specifications that contribute into preserving the environment (made of recycled material, ozone friendly, low volatile organic compounds, etc…)
Bidder shall provide the product’s specifications that contribute towards the health and safety of the users (ergonomic design, safety features, etc)
Bidder shall state the safety measures being followed by personnel performing the work on Alfa’s sites (ISO45001 certification, specific best practices, etc…).
Bidder shall provide the product’s life cycle data if available.

## Technical Requirements
| RFT Compliance Matrix |  |  |  | Reference Number | SF-CF-25
[5 empty] | Owner | PRO
[5 empty] | Revision Code | 3.0
[5 empty] | Implementation Date | 2024-03-01
Project Name: | JDEIDET DATA CENTER
Reference Number: | 28 31 12.00.F01 - Zoned (DC Loop) Fire-Alarm Systems - 10.2023
RFT Article (Part Number or Title) | Requirements (Description) | Killer | Fully Compliant | Partially Compliant | Non-Compliant | Reference (Specify document & page nb)
1 GENERAL
1.1 SUMMARY
A. This section of the specifications includes the furnishing, installation, and connection of the fire alarm equipment to form a complete coordinated system ready for operation. It shall include, but not be limited to, alarm initiating devices, alarm notification appliances, control units, fire safety control devices, annunciators, power supplies, and wiring as shown on the drawings and specified.
B. The fire protection system shall comprise the following components:
1. CO2 or FM200 total flooding system
2. Fire Detection System
3. Portable fire extinguisher
C. The firefighting method used shall be Automatic Total Flooding complete with fire alarm and detection system.
D. Shall utilize fixed nozzle agent distribution network.
E. Shall be capable of automatic detection and manual actuation.
F. Additional equipment shall be available for fuel shut-off and generator shut-off where required.
G. Shall be capable of extinguishing fire in Class A, B, and C hazards.
H. Detection system shall be tested to applicable NFPA & BS Standards and Regulations.
1.2 REFERENCES
A. Compliancy with international standards:
1. National Fire Protection Association (NFPA):
a. NFPA 12 – Standard on Carbon Dioxide Extinguishing Systems.
b. NFPA 2001 – Standard on Clean Agent Fire Extinguishing Systems.
c. NFPA 70 – National Electrical Code.
d. NFPA 72 – Standard for Protective Signaling Systems.
2. British Standards
a. BS 5839 – Part 1 (Fire detection and alarm systems for buildings. Code of practice for system design, installation and servicing.
b. BS 6266 – Code of practice for fire protection for electronic data processing installations
c. BS 7273-1 – Code of practice for the operation of fire protection measures
B. Laboratory approvals
1. Loss Prevention Certification Board (LPCB)
Underwriter Laboratories (UL)
1.3 SUBMITTALS
A. Two (2) complete set of documentations shall be provided by the supplier. Documents should include:
B. Manuals
1. FACP technical and operational manual
2. Technical data sheets of all submitted products and accessories data with manual of installation and operation.
3. Devices list (filled in)
4. Manufacturer’s instruction for system maintenance and recharge.
C. Drawings and Calculation Notes
1. Detailed installation drawings of the complete detection and suppression system.
2. Include manufacturer's name(s), model numbers, ratings, power requirements, equipment layout, device arrangement, complete wiring point-to-point diagrams, and conduit layouts.
3. Sufficient information, clearly presented, shall be included to determine compliance with drawings and specifications.
4. AS-BUILT drawings after system commission
5. Wiring diagram of the FACP and all connected devices
6. Battery sizing calculation notes
D. Certificates
1. Product certificate of all components including:
a. FACP
b. Detectors
c. Abort push button
d. Siren
e. Strobe
f. Pressure switch
2. Site commissioning certificate – Signed
1.4 QUALITY ASSURANCE
A. Manufacturer: The manufacturer of the system components shall have minimum of 10 years’ experience in the manufacture and design of fire detection systems and control equipment.
B. Installer: The installer shall be authorized and trained by manufacturer to design, install, and maintain fire detection systems.
C. All system components must be approved by Loss Prevention Certification Board (LPCB) or Underwriter Laboratory (UL).
1.5 WARRANTY
A. Equipment
1. The supplied products shall be covered by full supplier warranty for a minimum period of one (1) year from commissioning date at a full repair and replacement service.
2. Warranty shall include all defected spare parts and workmanship.
B. Services
1. Installation and dismantling
a. The supplier is responsible for the dismantling, hoisting, transportation and re-installation for parts that cannot be repaired or replaced on site
2. Part replacement/repair
a. For any part replacement or repair service the warranty for the repaired or new part shall be a minimum of 6 (six) months from the date of receipt of the repaired or new part. In case a part was repaired twice already under this warranty and the equipment becomes faulty again within up to six months the Operator on its discretion may request replacement of the complete equipment
3. Major defect
a. In case of major defect in the supplied products, the Operator reserves the right to reject the equipment. The supplier shall replace the defected system/parts under no cost from the Operator, including dismantling, hoisting, transportation and re-installation
2 PRODUCTS
2.1 MANUFACTURERS
1. The FACP and peripheral devices shall be manufactured 100% by a single manufacturer (or division thereof).
2. The fire alarm system shall be manufactured by an ISO 9001 certified company and meet the requirements of BS EN9001: ANSI/ASQC Q9001:2015.
2.2 GENERAL
A. System includes detectors, sound and visual alarms manual release/abort stations and control panel. The detectors to be as shown on drawings and shall conform to the relevant electrical specifications sections.
B. Used to operate a single or multiple fire suppression or alarm system based on inputs received from fire detection devices.
C. Circuits to be configured using cross, counting and independent or priority-zone concepts.
D. Provision should be made to alert plant staff that the extinguishant (CO2 or FM200) has been dis-charged.
2.3 FIRE ALARM CONTROL PANEL (FACP)
A. Functional Description
1. The Single Area Conventional Fire Alarm Control Panel (FACP) shall be the central processing unit of the system, receiving and analyzing signals from fire detectors or manual releasing devices, providing audible and visual information to the user, initiating automatic alarm response sequences and providing the means by which the user interacts with the system. It shall also have the capability to electronically activate and release extinguishant by means of control of a solenoid valve.
2. FACP shall comply and should be certified to BS/LPCB or UL/FM.
3. The FACP shall be certified as meeting the requirements of EN 12094-1, (Environmental Class A) by a suitable, notified body. A certificate and test report shall be made available for inspection as evidence of certification.
4. The FACP shall have the capability to support two (2) zones of conventional detection all of which configured to contribute to the release of the extinguishant.
5. Each conventional detection zone shall be capable of supporting up to 20 conventional fire detectors. The detection zones shall be capable of supporting intrinsically safe detection devices using appropriate intrinsically safe (IS) barriers.
6. The FACP shall have the capability to operate in either manual mode or automatic and manual (combined) mode. The mode of the system shall be selectable by means of a key operated switch. In manual mode the extinguishant will not be released by automatic detection.
7. The FACP shall incorporate a display on the control panel and on all status indicator units, which in the activated condition shall show the time remaining in seconds until the extinguishant will be discharged.
8. Time delay before extinguishant release should be 30 seconds.
9. In addition to the activation of the extinguishant output, the FACP shall be capable of halting the release of the extinguishant by the operation of a "hold-off" input.
10. The FACP shall have a facility for connecting door interlock switches to change the mode of the system from "automatic and manual" to "manual only".
11. The FACP shall have the facility to monitor a pressure switch connected to the extinguishant cylinder and indicate loss of pressure in the cylinder.
12. The FACP shall have the facility to monitor a pressure switch connected to the extinguishant cylinder, which indicates release of extinguishant from the cylinder.
13. The FACP shall contain a manual control to provide a clean contact relay output to operate an extractor fan after the extinguishant has been released.
14. The FACP shall provide 2 sounder outputs, which operate when any alarm is detected (first stage alarm). It shall be possible to program a delay from 30 seconds or 1 minute to 10 minutes (in 1 minute steps) before the first stage alarm outputs activate.
15. The FACP shall contain one sounder output, which operates when the FACP is in the activated condition (second stage alarm).
16. The FACP shall provide a volt free changeover contact, which operates when first stage alarm is detected (1st fire alarm relay). This relay shall de-activate only when the FACP is reset.
17. The FACP shall provide a volt free changeover contact, which operates when second fire alarm is detected (2nd fire alarm relay). This relay shall de-activate when FACP is reset.
18. The FACP shall provide a volt free changeover contact, which operates when any fault or power loss is detected (fault relay). This relay shall de-activate only when the FACP is reset.
19. FACP chassis should be grounded to nearest metallic equipment.
20. Sequence of Operation: System operation shall be such that when a smoke detector detects fire in a zone, it shall send a signal to the FACP which sends it in turn to the alarm distribution frame (ADF) for tele-reporting and starts a first stage alarm status (Preliminary Alarm). This first stage includes an intermittent sound alarm from an electronic siren and a visual alarm from a light strobe. Then, if the alarm condition is confirmed by a second smoke detector, the fire alarm panel shall trigger a second alarm status (2nd stage fire alarm) where the siren shall send a continuous sound and a luminous warning sign inside the room shall be lit. Also, an alarm signal shall be sent to the alarm distribution frame (ADF) and an outdoor warning strobe shall be lit for the attention of the personnel not to enter the protected zone. The audio/visual alarm conditions shall remain for 30 seconds before agent discharge. During this period, personnel should evacuate the premises prior to discharge.
B. Enclosure
1. The housing containing the FACP shall be of metal construction and shall be capable of being surface mounted. It shall be complete with cable knocks-outs in sufficient quantity to accommodate all likely cabling requirements.
2. The housing shall afford a minimum ingress protection to IP30 and it shall not be possible to open the FACP without the use of a key.
C. Front panel controls
1. The FACP shall have the following front panel controls:
a. Silence/sound alarm (first stage)
b. Alarm/fault warning silence (buzzer)
c. Reset
d. Lamp test
e. Mode • Select • Enter
f. Enable controls (Key operated switch)
g. Manual only or Automatic and manual (Key operated switch)
h. Manual release (Lift flap, push button) / Output Disable
D. Front panel indications
1. The FACP shall have the following front panel indications:
a. Power on
b. Test mode
c. Power fault
d. General fault
e. System fault
f. Alarm/Fault warning silenced
g. Sounder fault/disabled
h. Fire zone 1 & Fire zone 2
i. Fault zone 1 & Fault zone 2
j. Extinguishant disabled
k. Manual release disabled
l. 1st stage contact disabled
m. 2nd stage contact disabled
n. Extract fan disabled
o. Extinguishant released
p. Release imminent
q. 1st stage activated
r. Hold activated
s. Flooding zone fault
t. Low pressure
u. Manual only mode
v. Automatic and manual mode
E. Internal controls
1. The FACP shall have the following internal controls:
a. Terminate extinguishant release
b. Watchdog reset
c. Processor reset
d. Adjust extinguishant monitor circuit
e. Write enable
F. Internal indications
1. The FACP shall have the following internal indications:
a. Mains fail
b. Battery fail
c. CPU fault
d. Aux 24V fault
e. Battery low
f. Common fault
g. Earth fault
h. System fuse fault
i. First stage sounders 1 fault (S1)
j. First stage sounders 2 fault (S2)
k. Extinguishant fault
l. Hold off fault
m. Manual release fault
n. Mode select fault
o. Released pressure switch fault
p. Low pressure switch fault
q. Manual release operated tell tale
G. Circuit Connections
1. Connect circuit conductors entering or leaving the panel to screw-type terminals with each conductor and terminal marked for identification.
2.4 BATTERY
A. General
1. Battery backup power shall be through use of rechargeable, sealed-type storage batteries and battery charger.
B. Capacity
1. Provide storage batteries that are 24 Vdc sealed, lead-calcium type requiring no additional water with ample capacity, with primary power disconnected, to operate the fire alarm system.
2. Battery capacity should be capable to operate the fire alarm system for 24 hours in supervisory (standby) mode.
3. Following this period of standby battery operation, the batteries shall have ample capacity to operate all components of the system, including all alarm signaling devices in the total alarm mode for a minimum period of 1 hour.
4. Submit substantiating battery calculations for supervisory and alarm power requirements.
5. Include power (Watts) requirements for each system component and each panel component, and the battery recharging period.
C. Placement
1. Locate batteries at the bottom of the panel.
2. Provide batteries with overcurrent protection in accordance with NFPA 72.
2.5 BATTERY CHARGER
A. Battery charger shall be completely automatic, 24 Vdc with high/low charging rate, capable of restoring the batteries from full discharge (18 Vdc) to full charge within 48 hours.
B. A pilot light indicating when batteries are manually placed on a high rate of charge shall be provided as part of the unit assembly, if a high-rate switch is provided.
C. Locate charger in control panel cabinet.
2.6 ABORT PUSH BUTTON
A. Abort push button (APB) shall be white in color with a red, momentary pushbutton.
B. Abort push button should be lockable. Turn to release abort push button.
C. Installed at 1.5m from floor level
D. Similar to Telemecanique XB4-BS542 and fitted on metallic box similar to Telemecanique XAP-M1201
2.7 PRESSURE SWITCH
A. Pressure switch should be provided for CO2 extinguishant only.
B. Pressure switch rating: 250 bar
C. The pressure switch is mounted either in the distribution pipework or on the manifold and may be used to provide an electrical indication of the release of CO2, to perform ventilation shut-downs or to initiate indication of gas trapped in manifold where there are stop valves in the distribution pipework.
D. Sends signal to FACP when CO2 gas is released
E. The pressure switch requires to be manually reset following operation
F. A minimum pressure of 3 bar is required to ensure satisfactory operation.
G. Connection to the pressure switch may be either 1/2″ NPT (male) or 1/4″ NPT (female).
2.8 MANUAL FIRE ALARM STATIONS
A. Manual fire alarm stations shall conform to the applicable requirements of BS.
B. Connect manual stations into signal line circuits. Stations shall be installed on surface mounted outlet boxes at 1400 mm.
C. Stations shall be double action type.
D. Stations shall be finished in red, with raised letter operating instructions of contrasting color.
E. Stations requiring the breaking of glass or plastic panels for operation are not acceptable. Stations employing glass rods are not acceptable.
F. The use of a key shall be required to reset the station.
G. Gravity or mercury switches are not acceptable. Switches and contacts shall be rated for the voltage and current upon which they operate.
H. Stations shall have a separate screw terminal for each conductor. Surface mounted boxes shall be matched and painted the same color as the mounting surface.
2.9 PHOTOELECTRIC SMOKE DETECTOR
A. Smoke detectors shall be designed for detection of abnormal smoke densities.
B. EN54 approved by LPCB
C. Detectors shall contain a visible indicator LED that shows when the unit is in alarm condition.
D. Detectors shall not be adversely affected by vibration or pressure.
E. Detectors shall be the plug-in type in which the detector base contains terminals for making wiring connections.
F. Detectors that are to be installed in concealed (above false ceilings, etc.) locations shall be provided with a remote indicator LED suitable for mounting in a finished, visible location.
G. Optical detectors shall be used
H. Detectors shall operate on a light scattering concept using an LED light source.
I. Failure of the LED shall not cause an alarm condition. Detectors shall be factory set for sensitivity and shall require no field adjustments of any kind.
J. Diode base allowing the monitoring of a removed detector with BS 5839.
2.10 FIXED TEMPERATURE DETECTOR
A. Heat detectors shall be designed for detection of fire by fixed temperature.
B. EN54 approved by LPCB
C. Detectors shall be designed for surface outlet box mounting and supported independently of wiring connections.
D. Detectors shall be designed to detect high heat.
E. The detectors shall have a specific temperature setting of 57.2°C
F. Diode base allowing the monitoring of a removed detector with BS 5839.
A. Detectors located in areas subject to moisture, exterior atmospheric conditions, or hazardous locations as defined by NFPA 70 and as shown on drawings, shall be types approved for such locations.
2.11 RATE COMPENSATION DETECTOR
A. Heat detectors shall be designed for detection of fire by rate-compensating principle.
B. EN54 approved by LPCB
C. Detectors shall be surface mounted horizontal and vertical type, with outlet box supported independently of wiring connections.
D. Detectors shall be hermetically sealed and automatically resetting.
E. Rate Compensated detectors shall be rated for 15 by 15m.
F. Diode base allowing the monitoring of a removed detector with BS 5839.
G. Detectors located in areas subject to moisture, exterior atmospheric conditions, or hazardous locations as defined by NFPA 70 and as shown on drawings, shall be types approved for such locations.
2.12 COMBINATION FIXED-TEMPERATURE AND RATE OF RISE DETECTOR
A. Heat detectors shall be designed for detection of fire by combination fixed temperature and rate-of-rise principle.
B. Detectors shall be designed for surface outlet box mounting and supported independently of wiring connections.
C. Contacts shall be self-resetting after response to rate-of-rise principle.
D. Under fixed temperature actuation, the detector shall have a permanent external indication which is readily visible.
E. Detector units located in boiler rooms, showers, or other areas subject to abnormal temperature changes shall operate on fixed temperature principle only.
F. The rating for the fixed temperature portion shall be 57.2°C.
G. The rating for the Rate-of-Rise detectors shall be rated for 15 by 15m.
H. Diode base allowing the monitoring of a removed detector with BS 5839.
2.13 REMOTE LED INDICATOR
A. Remote Indicator is used where a detector LED is not visible i.e., when the detector is mounted in a roof void, lift shaft etc.
2.14 FLAME DETECTOR
A. The detectors shall be sensitive to the micron range best suited for their intended use.
B. The detectors shall operate over electrically supervised wiring circuits and the loss of power to the detector shall result in a trouble signal.
C. A self-test feature shall be provided for each detector to be individually tested.
2.15 INFRARED (IR) SINGLE FREQUENCY FLAME DETECTOR
A. The detector shall comply with BS guide.
B. The detector shall operate over electrically supervised wiring circuits and the loss of power to the detector shall result in a trouble signal.
C. The detector shall be sensitive in the range of 4.4 to 4.6 μm only.
D. A self-test feature shall be provided for each detector to be individually tested.
2.16 ULTRAVIOLET (UV) FLAME DETECTOR
A. The detector shall comply with BS guide.
B. The detector shall operate over electrically supervised wiring circuits and the loss of power to the detector shall result in a trouble signal.
C. UV flame detector shall be of the narrow band response type which operates on radiated ultraviolet energy and shall be sensitive in the range of 0.185 - 0.260 μm only.
D. The detector shall be sensitive in the range of 185 to 260nm.
E. The cone of vision shall be 120 degrees.
F. Each detector shall be completely insensitive to light sources in the visible frequency range.
G. A self-test feature shall be provided for each detector to be individually tested.
2.17 COMBINATION UV/IR FLAME DETECTOR
A. The detector shall comply with BS guide.
B. The detector shall operate over electrically supervised wiring circuits and the loss of power to the detector shall result in a trouble signal.
C. The UV/IR detector shall provide discrimination against false alarms by requiring both UV and IR flame detection before an alarm is sent.
D. The UV sensor shall be sensitive in the range of 0.185 to 0.265 micrometers only.
E. The IR sensor shall be sensitive in the range of 0.185 - 0.260 μm only.
F. Detectors shall be completely insensitive to light sources in the visible frequency range.
G. A self-test feature shall be provided for each detector to be individually tested.
2.18 HORN
A. Horn shall have a separate screw terminal for each conductor.
B. Horn shall be painted red.
C. Horns shall be surface mounted, with the matching mounting back box surface mounted vibrating type suitable for use in an electrically supervised circuit.
D. Horn to be fitted to its original surface mounting box.
E. Horns shall produce a sound rating of at least 92 dBA at 3m.
F. Horn should offer two (2) distinct prioritized audible signals from two isolated inputs.
G. Priority one (1) will override all other commands upon activation.
H. Horns used in exterior locations shall be specifically listed or approved for outdoor use and be provided with metal housing.
2.19 STROBE
A. Strobe shall have clear high intensity optic lens, xenon flash tubes, and output white light.
B. Strobe flash rate shall be between 1 to 3 flashes per second and a minimum of 75 candela.
C. Strobe shall be surface mounted with engraved letters “FIRE”, 25mm text height.
D. Strobe light is activated in case of agent release
E. Strobe to be fitted to its original surface mounting box
F. Strobe used in exterior locations shall be specifically listed or approved for outdoor use and be provided with metal housing.
2.20 COMBINED HORN/STROBE
A. Combined horn/strobe shall provide the same requirements as individual units, except that they shall mount as a unit in standard back boxes.
B. Units shall be factory assembled.
2.21 LUMINOUS EVACUATE SIGN
A. Internal luminous warning sign, 10cd, with red letterings:
1. “CO2 Release – Evacuate Immediately”
2. or “FM200 Release – Evacuate Immediately”
3. or “FIRE ALARM”.
B. Lighting with high luminosity LED - IP55
C. Internal luminous warning sign is activated on the second stage.
2.22 WARNING PLATES
A. Door Caution Plate
1. The door caution plate provides instructions to personnel who may enter a CO2 or FM200 protected area.
2. Door caution plate shall be affixed on the external side of doors in every protected space where it is determined that the extinguishing gas (CO2 or FM200) could migrate, creating a hazard to personnel and at each entrance to extinguishing gas (CO2 or FM200) storage rooms.
3. Door caution plate text should be:
a. CO2 protected area: “CO2 – CAUTION! – Do not enter unless CO2 automatic release system is locked off (isolated) – When alarm sounds evacuate hazard area – After CO2 discharge do NOT re-enter until thoroughly ventilated”
b. FM200 protected area: “FM-200 – CAUTION! – This area is protected by a gaseous fire extinguishing system – When alarm sounds or upon gas discharge evacuate hazard area immediately – After discharge do NOT re-enter until thoroughly ventilated”
4. Warning sign dimensions: 210x210mm
B. Manual Release Caution Plate
1. The manual release caution plate provides instructions to personnel on the use of manual controls.
2. One plate is to be fixed adjacent to all positions from where the extinguishant (CO2 or FM200) can be released manually.
3. Warning sign text should be:
a. “CO2 – RELEASE – Manual Control Point – CO2 – CAUTION – Ensure all personnel are evacuated before releasing CO2”
b. “FM-200 – RELEASE – Manual Control Point – FM-200 – CAUTION – Ensure all personnel are evacuated before releasing FM-200”
2.23 WIRING
A. Wiring shall conform to NFPA 70.
B. Fire resistant and flame retardant control cables, BS6387, shall be utilized to connect the different devices of the fire detection system
C. Power cable 3x1.5mm² shall be used to connect the FACP to the electrical distribution panel (220Vac)
D. Wiring for fire alarm circuits shall be 1.5mm² cross-section, solid copper, three conductors, color coded, with red colored jacket
E. Wiring code color shall remain uniform throughout the circuit.
F. Conductors used for the same functions shall be similarly color coded.
G. Voltages shall not be mixed in any junction box, housing, or device, except those containing power supplies and control relays.
H. System field wiring shall be solid copper and installed in rigid fire retarded plastic conduit. Electrical metallic tubing will be used where indicated on drawings or where cables run in hazardous area.
I. Pigtail or T-tap connections to initiating device circuits, supervisory alarm circuits, and notification appliance circuits are prohibited.
2.24 LABELS
A. FACP shall be clearly labeled identifying:
1. Manufacturer
2. Model
3. Origin of manufacturer
4. Date of manufacturing
B. FACP electrical wiring diagram should be provided inside the FACP
C. All wires inside the FACP should be numbered
D. Additional components inside the FACP should be labeled
E. Abort push button and smoke detectors should be labeled
2.25 SPARE PARTS
A. Furnish the following spare parts:
1. Two of each type detector installed.
4. One of each type of audible and visual alarm device installed.
5. Five of each type of fuse required by the system.
6. Three complete sets of system keys
2.26 ACCESSORIES
1. All accessories necessary for the installation and proper operation of the system should be delivered with the system free of charge.
2.27 DEVICES LIST
A. The device list should be filled in and submitted with the technical offer. A soft copy should be provided.
1 EXECUTION
1.1 INSTALLATION
A. All work shall be installed as shown, and in accordance with NFPA 70 and NFPA 72, and in accordance with the manufacturer's diagrams and recommendations, unless otherwise specified.
B. Smoke detectors shall not be installed until construction is essentially complete and the building has been thoroughly cleaned.
C. Verification of Conditions: The Contractor shall verify that area being protected by carbon dioxide system meets requirements of NFPA 12.
D. Power Supply for the System
1. A single dedicated circuit connection for supplying power from a branch circuit to each fire alarm system shall be provided.
2. The power shall be supplied as shown on the drawings.
3. The power supply shall be marked in red with the words "FIRE ALARM”.
E. Wiring
1. Conduit size for wiring shall be in accordance with NFPA 70.
2. Wiring for the fire alarm system shall not be installed in conduits, junction boxes, or outlet boxes with conductors of lighting and power systems.
3. Not more than two conductors shall be installed under any device screw terminal.
4. The wires under the screw terminal shall be straight when placed under the terminal then clamped in place under the screw terminal.
5. The wires shall be broken and not twisted around the terminal.
6. Circuit conductors entering or leaving any mounting box, outlet box enclosure, or cabinet shall be connected to screw terminals with each terminal and conductor marked in accordance with the wiring diagram.
7. Connections and splices shall be made using screw terminal blocks.
8. The use of wire nut type connectors in the system is prohibited.
9. Wiring within any control equipment shall be readily accessible without removing any component parts.
10. The fire alarm equipment manufacturer's representative shall be present for the connection of wiring to the control panel.
F. Control Panel
1. The control panel and its assorted components shall be mounted so that no part of the enclosing cabinet is less than 1600 mm nor more than 1800 mm above the finished floor.
2. Manually operable controls, such as abort push button, shall be at 1500mm above the finished floor.
G. Detectors
1. Detectors shall be located and installed in accordance with NFPA 72.
2. Detectors shall be connected into signal line circuits or initiating device circuits as indicated on the drawings.
3. Detectors shall be at least 300 mm from any part of any lighting fixture.
4. Detectors shall be located at least 900 mm from diffusers of air handling systems.
5. Each detector shall be provided with appropriate mounting hardware as required by its mounting location.
6. Detectors which mount in open space shall be mounted directly to the end of the stubbed down rigid conduit drop.
7. Conduit drops shall be firmly secured to minimize detector sway.
8. Where length of conduit drops from ceiling or wall surface exceeds 900 mm, sway bracing shall be provided.
9. Detectors installed in concealed locations (above ceiling, raised floors, etc.) shall have a remote visible indicator LED/LCD as indicated.
H. Notification Appliances
1. Notification appliances shall be mounted 2000 mm above the finished floor or 150 mm below the ceiling, whichever is lower.
I. Alarm Contacts
1. Alarm contacts, 1st stage, 2nd stage, and trouble, should be connected to existing alarm distribution frame.
2. Alarm contacts should be voltage free and normally closed.
J. GROUNDING
1. Provide grounding by connecting to existing ground system.
1.2 TRAINING
A. Provide training course for the operations and maintenance staff.
B. Conduct the course in the building where the system is installed or as designated by the MIC1 engineer.
C. Submit lesson plans, operating instructions, maintenance procedures, and training data, furnished in manual format, for the training courses.
D. The operations training shall familiarize designated personnel with proper operation of the fire alarm system.
E. The training period for systems operation shall consist of 1 training day and shall start after the system is functionally completed but prior to final acceptance tests.
1.3 TESTING
A. Notify the MIC1 engineer at least 2 days before the preliminary and acceptance tests are to be conducted.
B. Perform the tests in accordance with the approved test procedures in the presence of the MIC1 engineer.
C. The control panel manufacturer's representative shall be present to supervise tests.
D. Furnish instruments and personnel required for the tests.
1. Submit detailed test procedures, prepared and signed by a Registered Professional Engineer, for the fire detection and alarm system 1 day prior to performing system tests.
2. Submit test reports, in booklet form, showing field tests performed to prove compliance with the specified performance criteria, upon completion and testing of the installed system.
3. Each test report shall document readings, test results and indicate the final position of controls.
4. Include the NFPA 72 Certificate of Completion and NFPA 72 Inspection and Testing Form, with the appropriate test reports.
E. Preliminary Tests
1. Upon completion of the installation, subject the system to functional and operational performance tests including tests of each installed initiating and notification appliance, when required.
2. Tests shall include the meggering of system conductors to determine that the system is free from grounded, shorted, or open circuits. Conduct the megger test prior to the installation of fire alarm equipment. If deficiencies are found, corrections shall be made, and the system shall be retested to assure that it is functional.
3. After completing the preliminary testing complete and submit the NFPA 72, Certificate of Completion.
F. Acceptance Test
1. Do not perform acceptance testing until the Contractor has completed and submitted the Certificate of Completion.
2. Testing shall be in accordance with NFPA 72.
3. The recommended tests in NFPA 72 shall be considered mandatory and shall verify that previous deficiencies have been corrected.
4. Complete and submit the NFPA 72, Inspection and Testing Form.
5. The test shall include all requirements of NFPA 72 and the following:
a. Test of each function of the control panel.
b. Test of each circuit in both trouble and normal modes.
c. Tests of each alarm initiating devices in both normal and trouble conditions.
d. Tests of each control circuit and device.
e. Tests of each alarm notification appliance.
f. Tests of the battery charger and batteries.
g. Complete operational tests under emergency power supply.
h. Visual inspection of wiring connections.
i. Opening the circuit at each alarm initiating device and notification appliance to test the wiring supervisory feature.
j. Ground fault.
k. Short circuit faults.
l. Stray voltage.
m. Loop resistance.
1.4 SITE DOCUMENT
A. A wiring drawing of the FACP (3 copies)
B. Devices List
C. Battery size calculations
D. AS BUILT plans
E. CO2 / FM200 quantity calculations
F. CO2 / FM200 hydraulic flow calculations
G. FACP technical and operating manual
H. Certificate of testing and commissioning
END OF SECTION

## Grade of Compliancy
| RFT Compliance Matrix | Reference Number | SF-CF-25
|  | Owner | PRO
|  | Revision Code | 3.0
|  | Implementation Date | 2024-03-01
Grade of Compliance range from 0 to 15 with a step of 1 unit:
15 : Compliant with additional value, not initially included in the requirements
10 : Fully compliant
4 - 5 - 6: Partially compliant
0 : Not compliant
K : Disqualification