## TOTAL
JDEIDET MOT - CORE SITE Fire Protection
BILL OF QUANTITIES - GRAND TOTAL
ITEM | DESCRIPTION | TOTAL (USD)
1 | Firefighting System | 0
| GRAND TOTAL | 0

## FireProtection
BILL OF QUANTITIES - FIRE PROTECTION SYSTEM
ITEM | DESCRIPTION | QTY | UNIT | UNIT PRICE | TOTAL US$
Drawings of fire protection system installation supplied with this schedule are design drawings necessary for the establishment of tender documents only. The contractor is responsible to verify the design, make the necessary calculations (hydraulic and other) and shall be responsible for the performance of the system and its compliance with the specified standards. Contractor shall submit to the client a copy of the calculations and isometric drawings for approval. the fire alarm and fire fighting system shall cover the data center expansion
FM200 FIRE SUPPRESSION SYSTEM
21 22 00.00.FM - Clean-Agent Fire-Extinguishing Systems - FM200
Complete FM-200 Fire supression system, including FM-200 cylinders, cylinder heads, solenoide valves, manifolds, all as specified and based on calculations to be submitted based on NFPA requirements.
1 | FM-200 System serving the data center room area (Total of 616Kg of FM-200) Void #1 (raised flr to ceiling) Area: 264m², height = 3.45m Void #2 (FFL to raised flr) Area: 264m², height = 0.50m Void #3 (Delivery area): Area: 12.6m², heigh = 4m | LS | 1 |  | 0
2 | FM-200 System serving the UPS and DC systems room (Total of 102Kg of FM-200) Void (FFL to ceiling): Area = 55m², height = 3.3m | LS | 1 |  | 0
3 | FM-200 System serving the Electrical room (Total of 48Kg of FM-200) Void (FFL to ceiling) Area: 16m², height = 3m | LS | 1 |  | 0
FIRE SUPPRESSION PIPES
4 | Pipe for FM-200 fire suppression system, galvanized seamless steel pipe with welded or threaded fittings and accessories, installed exposed or in shafts, including all kind of supports and hangers all as per specifications. Contractor is responsible for design calculations and for evaluating the proper pipe diameters and quantities. * Data Center Room * UPS and DC Systems Room * Electrical Room | LS | 1 |  | 0
5 | Nozzles for FM200 fire suppression system brass or bronze, all as per specifications. * Data Center Room * UPS and DC Systems Room * Electrical Room | LS | 1 |  | 0
6 | Installation of mechanical system * Data Center Room * UPS and DC Systems Room * Electrical Room | U | 1 |  | 0
PORTABLE FIRE EXTINGUISHER
SECTION 10 44 16.13 - Portable Fire Extinguishers
Portable fire extinguisher with discharge hose and nozzle, complete with wall support and accessories, all as per specifications
7 | 6-kg CO2 Extinguisher | U | 12 |  | 0
8 | 5-kg Powder ABC | U | 3 |  | 0
ADDRESSABLE FIRE DETECTION / ALARM CONTROL SYSTEM
SECTION 28 31 11.00.FA01 Digital Addressable Fire-Alarm Systems
Supply, install and connect complete fire alarm and suppression system including conduits, wires, cables, pull and junction boxes with all necessary accessories for a complete and perfect operation of the system. The fire alarm system shall include but not limited to: FACP, smoke detectors, combined smoke/rate of rise detector, sounders, light strobes, warning signs, dead man's switch, wiring & cabling, junction boxes, etc... The fire alarm and detection shall cover the Data Center expansion area
Fire alarm shall be of addressable type with a double knock configuration for under the raised floor and the room void
All inputs, outputs and detection lines shall be monitored by the panel.
Wiring shall be by fire resistant cables.
The system shall include at least, but not limited to the following:
9 | FACP Addressable type with mimic panel with floor layout; The FACP shall be able to discharge the FM200 cylinders in the data center area | U | 1 |  | 0
10 | Intelligent smoke detector | U | 34 |  | 0
11 | Hold push button | U | 2 |  | 0
12 | Horn | U | 3 |  | 0
13 | Light strobe | U | 3 |  | 0
14 | Luminous evacuate sign | U | 2 |  | 0
15 | Warning sign | U | 2 |  | 0
16 | Manual release point with cover protection | U | 1 |  | 0
17 | Smart auxilliary contact relay to release door lock upon fire event | U | 2 |  | 0
CONVENTIONAL FIRE DETECTION / ALARM CONTROL SYSTEM
SECTION 28 31 12.00.F01 Zoned (DC Loop) Fire-Alarm Systems
Supply, install and connect complete fire alarm and suppression system including conduits, wires, cables, pull and junction boxes with all necessary accessories for a complete and perfect operation of the system. The fire alarm system shall include but not limited to: FACP, smoke detectors, combined smoke/rate of rise detector, sounders, light strobes, warning signs, dead man's switch, wiring & cabling, junction boxes, etc... The fire alarm and detection shall cover the UPS and DC Systems Room, the Utility UPS Room, and the Electrical Room.
Fire alarm shall be of conventional type with a double knock configuration for the room void
18 | Conventional Fire detection system for FM200 cylinders discharge including: (For Electrical Room) | U | 1 |  | 0
FACP - Qty = 1
Smoke detector - Qty = 6
Abort Push Button - Qty = 1
Horn - Qty = 1
Strobe - Indoor - Qty = 1
Strobe - Outdoor - Qty = 1
Luminous Evacuate Sign - Qty = 1
Pressure Switch - Qty = 1
Fire rated cables - Qty = LS
Warning signs - Qty = 1
19 | Conventional Fire detection system for FM200 cylinders discharge including: (UPS and DC Systems room) | U | 1 |  | 0
FACP - Qty = 1
Smoke detector - Qty = 8
Abort Push Button - Qty = 1
Horn - Qty = 1
Strobe - Indoor - Qty = 1
Strobe - Outdoor - Qty = 1
Luminous Evacuate Sign - Qty = 1
Pressure Switch - Qty = 1
Fire rated cables - Qty = LS
Warning signs - Qty = 1
Total |  |  |  |  | 0