## grade of compliance range
| RFT Scoring Sheet | Reference Number | SF-CF-87
|  | Owner | PRO/PMO
|  | Revision Code | 2.0
|  | Implementation Date | 2021-09-01
Grade of Compliance range from 0 to 15 with a step of 1 unit:
15 : Compliant with additional value, not initially included in the requirements
10 : Fully compliant
4 - 5 - 6: Partially compliant
0 : Not compliant
K : Disqualification

## weight
| RFT Scoring Sheet | [11 empty] | Reference Number |  | SF-CF-87
[13 empty] | Owner |  | PRO/PMO
[13 empty] | Revision Code |  | 2.0
[13 empty] | Implementation Date |  | 2021-09-01
Project Name | JDEIDET DATA CENTER
Weight Distribution | 50% Technical 50% Commercial
Article | Requirements | Weight | Responsible Entity | Supplier 1 | Supplier 2 | Supplier 3 | Supplier 4 | Supplier 5 | Supplier 6 | Remarks | Supplier 1 Final | Supplier 2 Final | Supplier 3 Final | Supplier 4 Final | Supplier 5 Final | Supplier 6 Final
| 1 GENERAL | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1.1 SUMMARY | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Batteries for core sites | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1.2 REFERENCES | 5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Compliancy with international standards: | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. BS 6290-4:1997 - Lead-acid stationary cells and batteries. Specification for classifying valve regulated types | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. IEC 60896-21:2004 - Stationary lead-acid batteries - Valve regulated types – Methods of test | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. IEC 60896-22:2004 - Stationary lead-acid batteries - Valve regulated types – Requirements | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 4. DIN 40742 – Valve regulated OPzV single cells | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5. DIN 43534 – Lead storage batteries; MAINTENANCE-FREE, SEALED, IMMOBILIZED ELECTROLYTE; RATED CAPACITIES, VOLTAGES, MAIN DIMENSIONS, CONSTRUCTION-DETAILS, REQUIREMENTS | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 6. DIN 43539 Part 5 - Proof against deep discharge | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 7. UL 94-V0 – Standard for Tests for Flammability of Plastic Materials for Parts in Devices and Appliances | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 8. EUROBAT guide 1999 – Classified as “long life” | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 9. Manufactured in ISO 9001:2000 and ISO 14001:2004 certified production facilities | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Laboratory approvals | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. The bidder should submit a test report certificate from one of the below laboratories: | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| a. Underwriters Laboratory (UL) | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| b. Germanisher Lloyd (GL) | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| c. Deutche Bahn | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| d. TUV | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| e. SGS | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1.3 SUBMITTALS | 5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Manuals | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Two (2) complete set of documentations shall be provided by the supplier. Documents should include: | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| a. Technical specifications | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| b. Installation guide | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| c. Maintenance procedure | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| d. Manufacturer recommendations | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| e. Warranty Certificate | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. The supplier shall supply a completed Battery Discharge Table for all offered batteries. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1.4 WARRANTY | 5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Equipment | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. The supplied products shall be covered by full supplier warranty for a minimum period of one (1) year from delivery to site at a full repair and replacement service. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Warranty shall include all defected spare parts and workmanship. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Services | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Installation and dismantling | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| a. The supplier is responsible for the dismantling, hoisting, transportation and re-installation for parts that cannot be repaired or replaced on site | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Part replacement/repair | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| a. For any part replacement or repair service the warranty for the repaired or new part shall be a minimum of 6 (six) months from the date of receipt of the repaired or new part. In case a part was repaired twice already under this warranty and the equipment becomes faulty again within up to six months the Operator on its discretion may request replacement of the complete equipment | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. Major defect | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| a. In case of major defect in the supplied products, the Operator reserves the right to reject the equipment. The supplier shall replace the defected system/parts under no cost from the Operator, including dismantling, hoisting, transportation and re-installation | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2 PRODUCTS | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.1 MANUFACTURERS | 5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Products manufacturer should be ISO 9001:2015 certified. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Batteries manufacturing date should not be older than six (6) months. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.2 BATTERY CHARACTERISTICS | 15 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. General | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Application: Telecommunication | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Type: Absorbent Glass Mat (AGM) or GEL – VRLA (valve regulated lead acid) | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. Reliability and robustness: | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| a. Positive tubular plates die-cast for longer life duration | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| b. Low self-discharge rate with optimized number of cycles for a long life expectancy | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 4. Design life: greater than 10 years at 60% depth of discharge @ 20°C ambient temperature; Eurobat 1999 – classified as long life | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Battery Specifications | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Design life: 15 years @ 20°C ambient temperature floating voltage | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Cycle life: Minimum 1500 cycles @ 60% depth of discharge (DoD) @ 20°C (or 1200 cycles @ 80% DoD @ 20°C). The bidder should submit support test documentation. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. Nominal Block Voltage: 2Vdc | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| a. Capacity: Rated 10 hours to 1.80Vpc @ 20°C | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 4. Size: | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| a. 600AH, C10, 1.80Vpc @ 25°C | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| b. 1200AH, C10, 1.80Vpc @ 25°C | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| c. 1500AH, C10, 1.80Vpc @ 25°C | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| d. 2000AH, C10, 1.80Vpc @ 25°C | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| e. 3000AH, C10, 1.80Vpc @ 25°C | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5. System Voltage (string): -48Vdc | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 6. End (cut-off) voltage: 1.8Vdc per cell | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 7. Charging current: That can be applied to the battery during recharging under the specified float conditions and under any refresher charge conditions must be stated by the supplier. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 8. Float voltage: Shall be in between 2.2 and 2.7Vdc per cell @ 20°C and shall remain stable (±0.05Vdc) throughout the battery life. Since the charging voltage differ due to acid Ph and metallurgy between the various battery manufacturers and is also related to the working temperature, hence charging voltages shall be adjusted according to the graph supplied with each battery type; Supplier should deliver the charge voltages graph per cell (charging and floating) | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 9. Self-discharge rate: The self-discharge rate of the battery shall be less than 0.5% per week. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 10. Recharge rate: Recharge rate of 90% shall be within 12hours. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 11. Efficiency of Recharging – AH: greater than 90% | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 12. Recombination efficiency: Shall not be less than 97% @ 25°C after ten (10) discharge cycles or twelve (12) months on float operation. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 13. Operating temperature: is from -10°C to 45°C and Humidity <90%. Battery should withstand hard freezing without damage of the alloy, plates, or cell container assembly. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 14. Ventilation: No special needs shall be required | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.3 BATTERY STORAGE | 5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Storage: Temperature range of -10°C to +45°C, Humidity <90% | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Shelf life: one (1) year at 20°C without recharge. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. Batteries storage time shall not exceed 2 years. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.4 BATTERY REFRSHING CHARGE | 5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Batteries must be given a refreshing charge: | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| a. When maximum storage time is reached, or | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| b. When the OCV (Open Charge Voltage) approaches 2.10Volts/cell whichever occurs first | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Refreshing charge: The refresh charge should be conducted using constant voltage (adjusted to the temperature) eg. 2.23Vpc at 20-25°C with 0.1 C10 Amps current limit for a minimum period of 96hrs. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 BATTERY CONSTRUCTION | 5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. AGM | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| a. Positive plates: tubular plates consisting of Lead-Calcium alloy with high corrosion resistance | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| b. Negative plates: grid plate consisting of Lead-Calcium alloy | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| c. Separators: low resistance microporous material | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. GEL | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| a. Lead/calcium alloys in both positive and negative electrodes. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| b. Thick plates with mechanical strengthening of the positive mass. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. Case material: container and lid in ABS (Acrylanitrile Butadiene Styrene) according to UL94-V0 (V-0: burning stops within 10 seconds on a vertical specimen; drips of particles allowed as long as they are not inflamed.) | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 4. Installation: Horizontal installation inside rack | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5. Terminals: terminals with brass insert and M10/M8 stainless steel bolts. Colored washers to be provided for easy polarity recognition. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 6. Terminals: should be protected during transport | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 7. Connectors: | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| a. Insulated solid copper connector (30 x 3mm) for vertical installations or insulated flexible cable connectors (70-90mm²) for horizontal installations. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| b. Each connector design is of the bolt-on type | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| c. Each connector allows for voltage measurements | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 8. Pressure relief valve: one way gas release valve in case of excess pressure with integral flame arrestor and protects cell against atmosphere. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.6 BATTERY INSTALLATION | 5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Physical arrangement shall ensure access to each battery block terminals. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Must be easy to install and virtually maintenance free | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. Mixing of different capacity rating is not permitted | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.7 LABELS | 5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Each cell shall be clearly and permanently labeled identifying: | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Manufacturer | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Model | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. Origin of manufacturer | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 4. Date of manufacture (year and month) | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5. Nominal voltage | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 6. Nominal AH capacity at 10hrs to 1.8V/cell @ 25°C | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Each cell shall be consequently numbered at the positive (GND) terminal. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| C. Each string shall be labeled with a clear string identification number. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.8 ACCESSORIES | 5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Connectors, bolts, nuts, buss bars, lugs, insulation covers, labels, jumpers to connect the batteries strings in parallel, lifting straps, etc. necessary for the installation of the batteries should be delivered with the batteries. Note that inter-cell connectors shall be lead plated copper. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.9 METALLIC RACKS | 5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Metallic racks should be supplied so that batteries are installed horizontally. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Metallic racks should be capable of carrying 3,000Kg | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. Batteries, on racks, should be provided with protective insulation cover | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3 EXECUTION | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3.1 STORAGE | 5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. All products including batteries should be stored at the supplier warehouse till the date of installation on site. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. The supplier is responsible to perform one refreshing charge to stored batteries at his warehouse free of charge during the first year of storage. If the supplied batteries need more than one refreshing charge per year, the supplier shall bear the expenses of the additional refreshing charges. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3.2 COMMISSIONING | 5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Safety, installation & ventilation | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. The battery room should be well ventilated in order to remove gases produced during charging. The gases (mixture of oxygen and hydrogen) liberated by the cells when on charge may cause an explosion, and therefore, care must be taken not to produce SPARKS. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. NAKED LIGHTS must be not allowed, and remember NO SMOKING. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Following precautions must also be taken: | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Do not wear clothing likely to create static electricity (nylon) during maintenance operations | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Do not use a portable apparatus linked to an electric plug | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| C. The electrical protective measures and the accommodation and ventilation of the battery installation must be in accordance with the applicable “local” national standards, rules and regulations. Specifically EN 50272-2 standard applies. Low ventilation requirement according to EN 50272-2: Safety Requirements for Secondary Batteries and Battery Installations Part 2: Stationary Batteries. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| D. The battery should be installed in a clean, dry area. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| E. Avoid placing the battery in a hot place or in front of a window (no direct sunlight). Battery racks are recommended for proper installation. Place the cells on the rack and arrange the positive and the negative terminals for connection according the wiring diagram. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| F. Check that all contact surfaces are clean. Tighten terminal screws, taking care to use the correct torque loading. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| G. Follow the polarity to avoid short circuiting of cell groups. A loose connector can cause trouble in adjusting the system, erratic battery performance, and possible damage to the battery and/or personal injury. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| H. Commissioning: The initial charge is extremely important as it will condition the battery service life. So, the battery must be fully recharged to ensure that it is in an optimum state of charge. The recommended float charge voltage is 2.25Vpc (20°C). | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| I. End-of-charge | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. End-of-charge is when all cell voltages and electrolyte specific gravities (corrected to 25°C) cease to rise for three consecutive hourly readings. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Continue charging until the specific gravity of electrolyte for all cells rise to nominal specific gravity at maximum level. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| J. Electrolyte specific gravities: | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Measure the specific gravity with a hydrometer | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. After reading, squirt the solution back into the cell from which it was drawn | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. The nominal specific gravity at the end of the charge at the specified level is for a temperature of 25ºC | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 4. If temperature is above or below 25ºC, specific gravity reading must be adjusted using the table provided by supplier. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| K. Nominal electrolyte specific gravity of cells at maximum level = 1.240 at 25°C | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3.3 INSTALLATION ON SITE | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. All batteries transported to site should be fully charged at the supplier warehouse to prevent overload on the site mains power supply, EDL & generator. | 5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3.4 DISCHARGE TESTS | 10 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. The supplier shall perform a discharge test to confirm the quoted capacity of the battery. This test will be performed after the installation and will be conducted at the nominal 10hrs discharge rate to 1.92V/cell. The battery shall then be fully recharged before being placed into service. The contractor shall submit the following records prior to issuance of an Acceptance Certificate. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Initial charge records | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Discharge test records | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. Recharge records | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 4. Test forms | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Discharging (low voltage urgent and non-urgent alarm) | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. As a rule, installations will be equipped with LVD whose voltage threshold values will protect against deep discharge: | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3.5 DISPOSAL | 5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Batteries are recyclable. End of life batteries must be packaged and transported according to prevailing transportation rules and regulations. End of life batteries must be disposed of in compliance with local and national laws by a licensed battery recycler. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| END OF SECTION | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 | 0
[11 empty] | SUPPLIER 1 SCORE | SUPPLIER 2 SCORE | SUPPLIER 3 SCORE | SUPPLIER 4 SCORE | SUPPLIER 5 SCORE | SUPPLIER 6 SCORE
* For Requirements defined as ''Killer'', a ‘’Fully Compliant’’ score should be the sole acceptable outcome. Failing to obtain a ‘’Fully Compliant’’ score on the requirements defined as Killers, will mandate immediate disqualification for bidders.
Note on D9: Entity (Department/ Unit) that identified the requirement and that will be responsible for its evaluation.
Note on E9: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on F9: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on G9: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on H9: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on I9: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on J9: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on E11: Evaluators Comments
Note on F11: Evaluators Comments
Note on G11: Evaluators Comments
Note on H11: Evaluators Comments
Note on I11: Evaluators Comments
Note on J11: Evaluators Comments
Note on E12: Evaluators Comments
Note on F12: Evaluators Comments
Note on G12: Evaluators Comments
Note on H12: Evaluators Comments
Note on I12: Evaluators Comments
Note on J12: Evaluators Comments
Note on E13: Evaluators Comments
Note on F13: Evaluators Comments
Note on G13: Evaluators Comments
Note on H13: Evaluators Comments
Note on I13: Evaluators Comments
Note on J13: Evaluators Comments
Note on E14: Evaluators Comments
Note on F14: Evaluators Comments
Note on G14: Evaluators Comments
Note on H14: Evaluators Comments
Note on I14: Evaluators Comments
Note on J14: Evaluators Comments
Note on E15: Evaluators Comments
Note on F15: Evaluators Comments
Note on G15: Evaluators Comments
Note on H15: Evaluators Comments
Note on I15: Evaluators Comments
Note on J15: Evaluators Comments
Note on E16: Evaluators Comments
Note on F16: Evaluators Comments
Note on G16: Evaluators Comments
Note on H16: Evaluators Comments
Note on I16: Evaluators Comments
Note on J16: Evaluators Comments
Note on E17: Evaluators Comments
Note on F17: Evaluators Comments
Note on G17: Evaluators Comments
Note on H17: Evaluators Comments
Note on I17: Evaluators Comments
Note on J17: Evaluators Comments
Note on E18: Evaluators Comments
Note on F18: Evaluators Comments
Note on G18: Evaluators Comments
Note on H18: Evaluators Comments
Note on I18: Evaluators Comments
Note on J18: Evaluators Comments
Note on E19: Evaluators Comments
Note on F19: Evaluators Comments
Note on G19: Evaluators Comments
Note on H19: Evaluators Comments
Note on I19: Evaluators Comments
Note on J19: Evaluators Comments
Note on E20: Evaluators Comments
Note on F20: Evaluators Comments
Note on G20: Evaluators Comments
Note on H20: Evaluators Comments
Note on I20: Evaluators Comments
Note on J20: Evaluators Comments
Note on E21: Evaluators Comments
Note on F21: Evaluators Comments
Note on G21: Evaluators Comments
Note on H21: Evaluators Comments
Note on I21: Evaluators Comments
Note on J21: Evaluators Comments
Note on E22: Evaluators Comments
Note on F22: Evaluators Comments
Note on G22: Evaluators Comments
Note on H22: Evaluators Comments
Note on I22: Evaluators Comments
Note on J22: Evaluators Comments
Note on E23: Evaluators Comments
Note on F23: Evaluators Comments
Note on G23: Evaluators Comments
Note on H23: Evaluators Comments
Note on I23: Evaluators Comments
Note on J23: Evaluators Comments
Note on E24: Evaluators Comments
Note on F24: Evaluators Comments
Note on G24: Evaluators Comments
Note on H24: Evaluators Comments
Note on I24: Evaluators Comments
Note on J24: Evaluators Comments
Note on E25: Evaluators Comments
Note on F25: Evaluators Comments
Note on G25: Evaluators Comments
Note on H25: Evaluators Comments
Note on I25: Evaluators Comments
Note on J25: Evaluators Comments
Note on E26: Evaluators Comments
Note on F26: Evaluators Comments
Note on G26: Evaluators Comments
Note on H26: Evaluators Comments
Note on I26: Evaluators Comments
Note on J26: Evaluators Comments
Note on E27: Evaluators Comments
Note on F27: Evaluators Comments
Note on G27: Evaluators Comments
Note on H27: Evaluators Comments
Note on I27: Evaluators Comments
Note on J27: Evaluators Comments
Note on E28: Evaluators Comments
Note on F28: Evaluators Comments
Note on G28: Evaluators Comments
Note on H28: Evaluators Comments
Note on I28: Evaluators Comments
Note on J28: Evaluators Comments
Note on E29: Evaluators Comments
Note on F29: Evaluators Comments
Note on G29: Evaluators Comments
Note on H29: Evaluators Comments
Note on I29: Evaluators Comments
Note on J29: Evaluators Comments
Note on E30: Evaluators Comments
Note on F30: Evaluators Comments
Note on G30: Evaluators Comments
Note on H30: Evaluators Comments
Note on I30: Evaluators Comments
Note on J30: Evaluators Comments
Note on E31: Evaluators Comments
Note on F31: Evaluators Comments
Note on G31: Evaluators Comments
Note on H31: Evaluators Comments
Note on I31: Evaluators Comments
Note on J31: Evaluators Comments
Note on E32: Evaluators Comments
Note on F32: Evaluators Comments
Note on G32: Evaluators Comments
Note on H32: Evaluators Comments
Note on I32: Evaluators Comments
Note on J32: Evaluators Comments
Note on E33: Evaluators Comments
Note on F33: Evaluators Comments
Note on G33: Evaluators Comments
Note on H33: Evaluators Comments
Note on I33: Evaluators Comments
Note on J33: Evaluators Comments
Note on E34: Evaluators Comments
Note on F34: Evaluators Comments
Note on G34: Evaluators Comments
Note on H34: Evaluators Comments
Note on I34: Evaluators Comments
Note on J34: Evaluators Comments
Note on E35: Evaluators Comments
Note on F35: Evaluators Comments
Note on G35: Evaluators Comments
Note on H35: Evaluators Comments
Note on I35: Evaluators Comments
Note on J35: Evaluators Comments
Note on E36: Evaluators Comments
Note on F36: Evaluators Comments
Note on G36: Evaluators Comments
Note on H36: Evaluators Comments
Note on I36: Evaluators Comments
Note on J36: Evaluators Comments
Note on E37: Evaluators Comments
Note on F37: Evaluators Comments
Note on G37: Evaluators Comments
Note on H37: Evaluators Comments
Note on I37: Evaluators Comments
Note on J37: Evaluators Comments
Note on E38: Evaluators Comments
Note on F38: Evaluators Comments
Note on G38: Evaluators Comments
Note on H38: Evaluators Comments
Note on I38: Evaluators Comments
Note on J38: Evaluators Comments
Note on E39: Evaluators Comments
Note on F39: Evaluators Comments
Note on G39: Evaluators Comments
Note on H39: Evaluators Comments
Note on I39: Evaluators Comments
Note on J39: Evaluators Comments
Note on E40: Evaluators Comments
Note on F40: Evaluators Comments
Note on G40: Evaluators Comments
Note on H40: Evaluators Comments
Note on I40: Evaluators Comments
Note on J40: Evaluators Comments
Note on E41: Evaluators Comments
Note on F41: Evaluators Comments
Note on G41: Evaluators Comments
Note on H41: Evaluators Comments
Note on I41: Evaluators Comments
Note on J41: Evaluators Comments
Note on E42: Evaluators Comments
Note on F42: Evaluators Comments
Note on G42: Evaluators Comments
Note on H42: Evaluators Comments
Note on I42: Evaluators Comments
Note on J42: Evaluators Comments
Note on E43: Evaluators Comments
Note on F43: Evaluators Comments
Note on G43: Evaluators Comments
Note on H43: Evaluators Comments
Note on I43: Evaluators Comments
Note on J43: Evaluators Comments
Note on E44: Evaluators Comments
Note on F44: Evaluators Comments
Note on G44: Evaluators Comments
Note on H44: Evaluators Comments
Note on I44: Evaluators Comments
Note on J44: Evaluators Comments
Note on E45: Evaluators Comments
Note on F45: Evaluators Comments
Note on G45: Evaluators Comments
Note on H45: Evaluators Comments
Note on I45: Evaluators Comments
Note on J45: Evaluators Comments
Note on E46: Evaluators Comments
Note on F46: Evaluators Comments
Note on G46: Evaluators Comments
Note on H46: Evaluators Comments
Note on I46: Evaluators Comments
Note on J46: Evaluators Comments
Note on E47: Evaluators Comments
Note on F47: Evaluators Comments
Note on G47: Evaluators Comments
Note on H47: Evaluators Comments
Note on I47: Evaluators Comments
Note on J47: Evaluators Comments
Note on E48: Evaluators Comments
Note on F48: Evaluators Comments
Note on G48: Evaluators Comments
Note on H48: Evaluators Comments
Note on I48: Evaluators Comments
Note on J48: Evaluators Comments
Note on E49: Evaluators Comments
Note on F49: Evaluators Comments
Note on G49: Evaluators Comments
Note on H49: Evaluators Comments
Note on I49: Evaluators Comments
Note on J49: Evaluators Comments
Note on E50: Evaluators Comments
Note on F50: Evaluators Comments
Note on G50: Evaluators Comments
Note on H50: Evaluators Comments
Note on I50: Evaluators Comments
Note on J50: Evaluators Comments
Note on E51: Evaluators Comments
Note on F51: Evaluators Comments
Note on G51: Evaluators Comments
Note on H51: Evaluators Comments
Note on I51: Evaluators Comments
Note on J51: Evaluators Comments
Note on E52: Evaluators Comments
Note on F52: Evaluators Comments
Note on G52: Evaluators Comments
Note on H52: Evaluators Comments
Note on I52: Evaluators Comments
Note on J52: Evaluators Comments
Note on E53: Evaluators Comments
Note on F53: Evaluators Comments
Note on G53: Evaluators Comments
Note on H53: Evaluators Comments
Note on I53: Evaluators Comments
Note on J53: Evaluators Comments
Note on E54: Evaluators Comments
Note on F54: Evaluators Comments
Note on G54: Evaluators Comments
Note on H54: Evaluators Comments
Note on I54: Evaluators Comments
Note on J54: Evaluators Comments
Note on E55: Evaluators Comments
Note on F55: Evaluators Comments
Note on G55: Evaluators Comments
Note on H55: Evaluators Comments
Note on I55: Evaluators Comments
Note on J55: Evaluators Comments
Note on E56: Evaluators Comments
Note on F56: Evaluators Comments
Note on G56: Evaluators Comments
Note on H56: Evaluators Comments
Note on I56: Evaluators Comments
Note on J56: Evaluators Comments
Note on E57: Evaluators Comments
Note on F57: Evaluators Comments
Note on G57: Evaluators Comments
Note on H57: Evaluators Comments
Note on I57: Evaluators Comments
Note on J57: Evaluators Comments
Note on E58: Evaluators Comments
Note on F58: Evaluators Comments
Note on G58: Evaluators Comments
Note on H58: Evaluators Comments
Note on I58: Evaluators Comments
Note on J58: Evaluators Comments
Note on E59: Evaluators Comments
Note on F59: Evaluators Comments
Note on G59: Evaluators Comments
Note on H59: Evaluators Comments
Note on I59: Evaluators Comments
Note on J59: Evaluators Comments
Note on E60: Evaluators Comments
Note on F60: Evaluators Comments
Note on G60: Evaluators Comments
Note on H60: Evaluators Comments
Note on I60: Evaluators Comments
Note on J60: Evaluators Comments
Note on E61: Evaluators Comments
Note on F61: Evaluators Comments
Note on G61: Evaluators Comments
Note on H61: Evaluators Comments
Note on I61: Evaluators Comments
Note on J61: Evaluators Comments
Note on E62: Evaluators Comments
Note on F62: Evaluators Comments
Note on G62: Evaluators Comments
Note on H62: Evaluators Comments
Note on I62: Evaluators Comments
Note on J62: Evaluators Comments
Note on E63: Evaluators Comments
Note on F63: Evaluators Comments
Note on G63: Evaluators Comments
Note on H63: Evaluators Comments
Note on I63: Evaluators Comments
Note on J63: Evaluators Comments
Note on E64: Evaluators Comments
Note on F64: Evaluators Comments
Note on G64: Evaluators Comments
Note on H64: Evaluators Comments
Note on I64: Evaluators Comments
Note on J64: Evaluators Comments
Note on E65: Evaluators Comments
Note on F65: Evaluators Comments
Note on G65: Evaluators Comments
Note on H65: Evaluators Comments
Note on I65: Evaluators Comments
Note on J65: Evaluators Comments
Note on E66: Evaluators Comments
Note on F66: Evaluators Comments
Note on G66: Evaluators Comments
Note on H66: Evaluators Comments
Note on I66: Evaluators Comments
Note on J66: Evaluators Comments
Note on E67: Evaluators Comments
Note on F67: Evaluators Comments
Note on G67: Evaluators Comments
Note on H67: Evaluators Comments
Note on I67: Evaluators Comments
Note on J67: Evaluators Comments
Note on E68: Evaluators Comments
Note on F68: Evaluators Comments
Note on G68: Evaluators Comments
Note on H68: Evaluators Comments
Note on I68: Evaluators Comments
Note on J68: Evaluators Comments
Note on E69: Evaluators Comments
Note on F69: Evaluators Comments
Note on G69: Evaluators Comments
Note on H69: Evaluators Comments
Note on I69: Evaluators Comments
Note on J69: Evaluators Comments
Note on E70: Evaluators Comments
Note on F70: Evaluators Comments
Note on G70: Evaluators Comments
Note on H70: Evaluators Comments
Note on I70: Evaluators Comments
Note on J70: Evaluators Comments
Note on E71: Evaluators Comments
Note on F71: Evaluators Comments
Note on G71: Evaluators Comments
Note on H71: Evaluators Comments
Note on I71: Evaluators Comments
Note on J71: Evaluators Comments
Note on E72: Evaluators Comments
Note on F72: Evaluators Comments
Note on G72: Evaluators Comments
Note on H72: Evaluators Comments
Note on I72: Evaluators Comments
Note on J72: Evaluators Comments
Note on E73: Evaluators Comments
Note on F73: Evaluators Comments
Note on G73: Evaluators Comments
Note on H73: Evaluators Comments
Note on I73: Evaluators Comments
Note on J73: Evaluators Comments
Note on E74: Evaluators Comments
Note on F74: Evaluators Comments
Note on G74: Evaluators Comments
Note on H74: Evaluators Comments
Note on I74: Evaluators Comments
Note on J74: Evaluators Comments
Note on E75: Evaluators Comments
Note on F75: Evaluators Comments
Note on G75: Evaluators Comments
Note on H75: Evaluators Comments
Note on I75: Evaluators Comments
Note on J75: Evaluators Comments
Note on E76: Evaluators Comments
Note on F76: Evaluators Comments
Note on G76: Evaluators Comments
Note on H76: Evaluators Comments
Note on I76: Evaluators Comments
Note on J76: Evaluators Comments
Note on E77: Evaluators Comments
Note on F77: Evaluators Comments
Note on G77: Evaluators Comments
Note on H77: Evaluators Comments
Note on I77: Evaluators Comments
Note on J77: Evaluators Comments
Note on E78: Evaluators Comments
Note on F78: Evaluators Comments
Note on G78: Evaluators Comments
Note on H78: Evaluators Comments
Note on I78: Evaluators Comments
Note on J78: Evaluators Comments
Note on E79: Evaluators Comments
Note on F79: Evaluators Comments
Note on G79: Evaluators Comments
Note on H79: Evaluators Comments
Note on I79: Evaluators Comments
Note on J79: Evaluators Comments
Note on E80: Evaluators Comments
Note on F80: Evaluators Comments
Note on G80: Evaluators Comments
Note on H80: Evaluators Comments
Note on I80: Evaluators Comments
Note on J80: Evaluators Comments
Note on E81: Evaluators Comments
Note on F81: Evaluators Comments
Note on G81: Evaluators Comments
Note on H81: Evaluators Comments
Note on I81: Evaluators Comments
Note on J81: Evaluators Comments
Note on E82: Evaluators Comments
Note on F82: Evaluators Comments
Note on G82: Evaluators Comments
Note on H82: Evaluators Comments
Note on I82: Evaluators Comments
Note on J82: Evaluators Comments
Note on E83: Evaluators Comments
Note on F83: Evaluators Comments
Note on G83: Evaluators Comments
Note on H83: Evaluators Comments
Note on I83: Evaluators Comments
Note on J83: Evaluators Comments
Note on E84: Evaluators Comments
Note on F84: Evaluators Comments
Note on G84: Evaluators Comments
Note on H84: Evaluators Comments
Note on I84: Evaluators Comments
Note on J84: Evaluators Comments
Note on E85: Evaluators Comments
Note on F85: Evaluators Comments
Note on G85: Evaluators Comments
Note on H85: Evaluators Comments
Note on I85: Evaluators Comments
Note on J85: Evaluators Comments
Note on E86: Evaluators Comments
Note on F86: Evaluators Comments
Note on G86: Evaluators Comments
Note on H86: Evaluators Comments
Note on I86: Evaluators Comments
Note on J86: Evaluators Comments
Note on E87: Evaluators Comments
Note on F87: Evaluators Comments
Note on G87: Evaluators Comments
Note on H87: Evaluators Comments
Note on I87: Evaluators Comments
Note on J87: Evaluators Comments
Note on E88: Evaluators Comments
Note on F88: Evaluators Comments
Note on G88: Evaluators Comments
Note on H88: Evaluators Comments
Note on I88: Evaluators Comments
Note on J88: Evaluators Comments
Note on E89: Evaluators Comments
Note on F89: Evaluators Comments
Note on G89: Evaluators Comments
Note on H89: Evaluators Comments
Note on I89: Evaluators Comments
Note on J89: Evaluators Comments
Note on E90: Evaluators Comments
Note on F90: Evaluators Comments
Note on G90: Evaluators Comments
Note on H90: Evaluators Comments
Note on I90: Evaluators Comments
Note on J90: Evaluators Comments
Note on E91: Evaluators Comments
Note on F91: Evaluators Comments
Note on G91: Evaluators Comments
Note on H91: Evaluators Comments
Note on I91: Evaluators Comments
Note on J91: Evaluators Comments
Note on E92: Evaluators Comments
Note on F92: Evaluators Comments
Note on G92: Evaluators Comments
Note on H92: Evaluators Comments
Note on I92: Evaluators Comments
Note on J92: Evaluators Comments
Note on E93: Evaluators Comments
Note on F93: Evaluators Comments
Note on G93: Evaluators Comments
Note on H93: Evaluators Comments
Note on I93: Evaluators Comments
Note on J93: Evaluators Comments
Note on E94: Evaluators Comments
Note on F94: Evaluators Comments
Note on G94: Evaluators Comments
Note on H94: Evaluators Comments
Note on I94: Evaluators Comments
Note on J94: Evaluators Comments
Note on E95: Evaluators Comments
Note on F95: Evaluators Comments
Note on G95: Evaluators Comments
Note on H95: Evaluators Comments
Note on I95: Evaluators Comments
Note on J95: Evaluators Comments
Note on E96: Evaluators Comments
Note on F96: Evaluators Comments
Note on G96: Evaluators Comments
Note on H96: Evaluators Comments
Note on I96: Evaluators Comments
Note on J96: Evaluators Comments
Note on E97: Evaluators Comments
Note on F97: Evaluators Comments
Note on G97: Evaluators Comments
Note on H97: Evaluators Comments
Note on I97: Evaluators Comments
Note on J97: Evaluators Comments
Note on E98: Evaluators Comments
Note on F98: Evaluators Comments
Note on G98: Evaluators Comments
Note on H98: Evaluators Comments
Note on I98: Evaluators Comments
Note on J98: Evaluators Comments
Note on E99: Evaluators Comments
Note on F99: Evaluators Comments
Note on G99: Evaluators Comments
Note on H99: Evaluators Comments
Note on I99: Evaluators Comments
Note on J99: Evaluators Comments
Note on E100: Evaluators Comments
Note on F100: Evaluators Comments
Note on G100: Evaluators Comments
Note on H100: Evaluators Comments
Note on I100: Evaluators Comments
Note on J100: Evaluators Comments
Note on E101: Evaluators Comments
Note on F101: Evaluators Comments
Note on G101: Evaluators Comments
Note on H101: Evaluators Comments
Note on I101: Evaluators Comments
Note on J101: Evaluators Comments
Note on E102: Evaluators Comments
Note on F102: Evaluators Comments
Note on G102: Evaluators Comments
Note on H102: Evaluators Comments
Note on I102: Evaluators Comments
Note on J102: Evaluators Comments
Note on E103: Evaluators Comments
Note on F103: Evaluators Comments
Note on G103: Evaluators Comments
Note on H103: Evaluators Comments
Note on I103: Evaluators Comments
Note on J103: Evaluators Comments
Note on E104: Evaluators Comments
Note on F104: Evaluators Comments
Note on G104: Evaluators Comments
Note on H104: Evaluators Comments
Note on I104: Evaluators Comments
Note on J104: Evaluators Comments
Note on E105: Evaluators Comments
Note on F105: Evaluators Comments
Note on G105: Evaluators Comments
Note on H105: Evaluators Comments
Note on I105: Evaluators Comments
Note on J105: Evaluators Comments
Note on E106: Evaluators Comments
Note on F106: Evaluators Comments
Note on G106: Evaluators Comments
Note on H106: Evaluators Comments
Note on I106: Evaluators Comments
Note on J106: Evaluators Comments
Note on E107: Evaluators Comments
Note on F107: Evaluators Comments
Note on G107: Evaluators Comments
Note on H107: Evaluators Comments
Note on I107: Evaluators Comments
Note on J107: Evaluators Comments
Note on E108: Evaluators Comments
Note on F108: Evaluators Comments
Note on G108: Evaluators Comments
Note on H108: Evaluators Comments
Note on I108: Evaluators Comments
Note on J108: Evaluators Comments
Note on E109: Evaluators Comments
Note on F109: Evaluators Comments
Note on G109: Evaluators Comments
Note on H109: Evaluators Comments
Note on I109: Evaluators Comments
Note on J109: Evaluators Comments
Note on E110: Evaluators Comments
Note on F110: Evaluators Comments
Note on G110: Evaluators Comments
Note on H110: Evaluators Comments
Note on I110: Evaluators Comments
Note on J110: Evaluators Comments
Note on E111: Evaluators Comments
Note on F111: Evaluators Comments
Note on G111: Evaluators Comments
Note on H111: Evaluators Comments
Note on I111: Evaluators Comments
Note on J111: Evaluators Comments
Note on E112: Evaluators Comments
Note on F112: Evaluators Comments
Note on G112: Evaluators Comments
Note on H112: Evaluators Comments
Note on I112: Evaluators Comments
Note on J112: Evaluators Comments
Note on E113: Evaluators Comments
Note on F113: Evaluators Comments
Note on G113: Evaluators Comments
Note on H113: Evaluators Comments
Note on I113: Evaluators Comments
Note on J113: Evaluators Comments
Note on E114: Evaluators Comments
Note on F114: Evaluators Comments
Note on G114: Evaluators Comments
Note on H114: Evaluators Comments
Note on I114: Evaluators Comments
Note on J114: Evaluators Comments
Note on E115: Evaluators Comments
Note on F115: Evaluators Comments
Note on G115: Evaluators Comments
Note on H115: Evaluators Comments
Note on I115: Evaluators Comments
Note on J115: Evaluators Comments
Note on E116: Evaluators Comments
Note on F116: Evaluators Comments
Note on G116: Evaluators Comments
Note on H116: Evaluators Comments
Note on I116: Evaluators Comments
Note on J116: Evaluators Comments
Note on E117: Evaluators Comments
Note on F117: Evaluators Comments
Note on G117: Evaluators Comments
Note on H117: Evaluators Comments
Note on I117: Evaluators Comments
Note on J117: Evaluators Comments
Note on E118: Evaluators Comments
Note on F118: Evaluators Comments
Note on G118: Evaluators Comments
Note on H118: Evaluators Comments
Note on I118: Evaluators Comments
Note on J118: Evaluators Comments
Note on E119: Evaluators Comments
Note on F119: Evaluators Comments
Note on G119: Evaluators Comments
Note on H119: Evaluators Comments
Note on I119: Evaluators Comments
Note on J119: Evaluators Comments
Note on E120: Evaluators Comments
Note on F120: Evaluators Comments
Note on G120: Evaluators Comments
Note on H120: Evaluators Comments
Note on I120: Evaluators Comments
Note on J120: Evaluators Comments
Note on E121: Evaluators Comments
Note on F121: Evaluators Comments
Note on G121: Evaluators Comments
Note on H121: Evaluators Comments
Note on I121: Evaluators Comments
Note on J121: Evaluators Comments
Note on E122: Evaluators Comments
Note on F122: Evaluators Comments
Note on G122: Evaluators Comments
Note on H122: Evaluators Comments
Note on I122: Evaluators Comments
Note on J122: Evaluators Comments
Note on E123: Evaluators Comments
Note on F123: Evaluators Comments
Note on G123: Evaluators Comments
Note on H123: Evaluators Comments
Note on I123: Evaluators Comments
Note on J123: Evaluators Comments
Note on E124: Evaluators Comments
Note on F124: Evaluators Comments
Note on G124: Evaluators Comments
Note on H124: Evaluators Comments
Note on I124: Evaluators Comments
Note on J124: Evaluators Comments
Note on E125: Evaluators Comments
Note on F125: Evaluators Comments
Note on G125: Evaluators Comments
Note on H125: Evaluators Comments
Note on I125: Evaluators Comments
Note on J125: Evaluators Comments
Note on E126: Evaluators Comments
Note on F126: Evaluators Comments
Note on G126: Evaluators Comments
Note on H126: Evaluators Comments
Note on I126: Evaluators Comments
Note on J126: Evaluators Comments
Note on E127: Evaluators Comments
Note on F127: Evaluators Comments
Note on G127: Evaluators Comments
Note on H127: Evaluators Comments
Note on I127: Evaluators Comments
Note on J127: Evaluators Comments
Note on E128: Evaluators Comments
Note on F128: Evaluators Comments
Note on G128: Evaluators Comments
Note on H128: Evaluators Comments
Note on I128: Evaluators Comments
Note on J128: Evaluators Comments
Note on E129: Evaluators Comments
Note on F129: Evaluators Comments
Note on G129: Evaluators Comments
Note on H129: Evaluators Comments
Note on I129: Evaluators Comments
Note on J129: Evaluators Comments
Note on E130: Evaluators Comments
Note on F130: Evaluators Comments
Note on G130: Evaluators Comments
Note on H130: Evaluators Comments
Note on I130: Evaluators Comments
Note on J130: Evaluators Comments
Note on E131: Evaluators Comments
Note on F131: Evaluators Comments
Note on G131: Evaluators Comments
Note on H131: Evaluators Comments
Note on I131: Evaluators Comments
Note on J131: Evaluators Comments
Note on E132: Evaluators Comments
Note on F132: Evaluators Comments
Note on G132: Evaluators Comments
Note on H132: Evaluators Comments
Note on I132: Evaluators Comments
Note on J132: Evaluators Comments
Note on E133: Evaluators Comments
Note on F133: Evaluators Comments
Note on G133: Evaluators Comments
Note on H133: Evaluators Comments
Note on I133: Evaluators Comments
Note on J133: Evaluators Comments
Note on E134: Evaluators Comments
Note on F134: Evaluators Comments
Note on G134: Evaluators Comments
Note on H134: Evaluators Comments
Note on I134: Evaluators Comments
Note on J134: Evaluators Comments
Note on E135: Evaluators Comments
Note on F135: Evaluators Comments
Note on G135: Evaluators Comments
Note on H135: Evaluators Comments
Note on I135: Evaluators Comments
Note on J135: Evaluators Comments
Note on E136: Evaluators Comments
Note on F136: Evaluators Comments
Note on G136: Evaluators Comments
Note on H136: Evaluators Comments
Note on I136: Evaluators Comments
Note on J136: Evaluators Comments
Note on E137: Evaluators Comments
Note on F137: Evaluators Comments
Note on G137: Evaluators Comments
Note on H137: Evaluators Comments
Note on I137: Evaluators Comments
Note on J137: Evaluators Comments
Note on E138: Evaluators Comments
Note on F138: Evaluators Comments
Note on G138: Evaluators Comments
Note on H138: Evaluators Comments
Note on I138: Evaluators Comments
Note on J138: Evaluators Comments
Note on E139: Evaluators Comments
Note on F139: Evaluators Comments
Note on G139: Evaluators Comments
Note on H139: Evaluators Comments
Note on I139: Evaluators Comments
Note on J139: Evaluators Comments
Note on E140: Evaluators Comments
Note on F140: Evaluators Comments
Note on G140: Evaluators Comments
Note on H140: Evaluators Comments
Note on I140: Evaluators Comments
Note on J140: Evaluators Comments
Note on E141: Evaluators Comments
Note on F141: Evaluators Comments
Note on G141: Evaluators Comments
Note on H141: Evaluators Comments
Note on I141: Evaluators Comments
Note on J141: Evaluators Comments
Note on E142: Evaluators Comments
Note on F142: Evaluators Comments
Note on G142: Evaluators Comments
Note on H142: Evaluators Comments
Note on I142: Evaluators Comments
Note on J142: Evaluators Comments
Note on E143: Evaluators Comments
Note on F143: Evaluators Comments
Note on G143: Evaluators Comments
Note on H143: Evaluators Comments
Note on I143: Evaluators Comments
Note on J143: Evaluators Comments
Note on E144: Evaluators Comments
Note on F144: Evaluators Comments
Note on G144: Evaluators Comments
Note on H144: Evaluators Comments
Note on I144: Evaluators Comments
Note on J144: Evaluators Comments
Note on E145: Evaluators Comments
Note on F145: Evaluators Comments
Note on G145: Evaluators Comments
Note on H145: Evaluators Comments
Note on I145: Evaluators Comments
Note on J145: Evaluators Comments
Note on E146: Evaluators Comments
Note on F146: Evaluators Comments
Note on G146: Evaluators Comments
Note on H146: Evaluators Comments
Note on I146: Evaluators Comments
Note on J146: Evaluators Comments
Note on E147: Evaluators Comments
Note on F147: Evaluators Comments
Note on G147: Evaluators Comments
Note on H147: Evaluators Comments
Note on I147: Evaluators Comments
Note on J147: Evaluators Comments
Note on E148: Evaluators Comments
Note on F148: Evaluators Comments
Note on G148: Evaluators Comments
Note on H148: Evaluators Comments
Note on I148: Evaluators Comments
Note on J148: Evaluators Comments
Note on E149: Evaluators Comments
Note on F149: Evaluators Comments
Note on G149: Evaluators Comments
Note on H149: Evaluators Comments
Note on I149: Evaluators Comments
Note on J149: Evaluators Comments
Note on E150: Evaluators Comments
Note on F150: Evaluators Comments
Note on G150: Evaluators Comments
Note on H150: Evaluators Comments
Note on I150: Evaluators Comments
Note on J150: Evaluators Comments
Note on E151: Evaluators Comments
Note on F151: Evaluators Comments
Note on G151: Evaluators Comments
Note on H151: Evaluators Comments
Note on I151: Evaluators Comments
Note on J151: Evaluators Comments
Note on E152: Evaluators Comments
Note on F152: Evaluators Comments
Note on G152: Evaluators Comments
Note on H152: Evaluators Comments
Note on I152: Evaluators Comments
Note on J152: Evaluators Comments
Note on E153: Evaluators Comments
Note on F153: Evaluators Comments
Note on G153: Evaluators Comments
Note on H153: Evaluators Comments
Note on I153: Evaluators Comments
Note on J153: Evaluators Comments
Note on E154: Evaluators Comments
Note on F154: Evaluators Comments
Note on G154: Evaluators Comments
Note on H154: Evaluators Comments
Note on I154: Evaluators Comments
Note on J154: Evaluators Comments
Note on E155: Evaluators Comments
Note on F155: Evaluators Comments
Note on G155: Evaluators Comments
Note on H155: Evaluators Comments
Note on I155: Evaluators Comments
Note on J155: Evaluators Comments
Note on E156: Evaluators Comments
Note on F156: Evaluators Comments
Note on G156: Evaluators Comments
Note on H156: Evaluators Comments
Note on I156: Evaluators Comments
Note on J156: Evaluators Comments
Note on E157: Evaluators Comments
Note on F157: Evaluators Comments
Note on G157: Evaluators Comments
Note on H157: Evaluators Comments
Note on I157: Evaluators Comments
Note on J157: Evaluators Comments
Note on E158: Evaluators Comments
Note on F158: Evaluators Comments
Note on G158: Evaluators Comments
Note on H158: Evaluators Comments
Note on I158: Evaluators Comments
Note on J158: Evaluators Comments
Note on E159: Evaluators Comments
Note on F159: Evaluators Comments
Note on G159: Evaluators Comments
Note on H159: Evaluators Comments
Note on I159: Evaluators Comments
Note on J159: Evaluators Comments
Note on E160: Evaluators Comments
Note on F160: Evaluators Comments
Note on G160: Evaluators Comments
Note on H160: Evaluators Comments
Note on I160: Evaluators Comments
Note on J160: Evaluators Comments
Note on E161: Evaluators Comments
Note on F161: Evaluators Comments
Note on G161: Evaluators Comments
Note on H161: Evaluators Comments
Note on I161: Evaluators Comments
Note on J161: Evaluators Comments
Note on E162: Evaluators Comments
Note on F162: Evaluators Comments
Note on G162: Evaluators Comments
Note on H162: Evaluators Comments
Note on I162: Evaluators Comments
Note on J162: Evaluators Comments
Note on E163: Evaluators Comments
Note on F163: Evaluators Comments
Note on G163: Evaluators Comments
Note on H163: Evaluators Comments
Note on I163: Evaluators Comments
Note on J163: Evaluators Comments
Note on E164: Evaluators Comments
Note on F164: Evaluators Comments
Note on G164: Evaluators Comments
Note on H164: Evaluators Comments
Note on I164: Evaluators Comments
Note on J164: Evaluators Comments
Note on E165: Evaluators Comments
Note on F165: Evaluators Comments
Note on G165: Evaluators Comments
Note on H165: Evaluators Comments
Note on I165: Evaluators Comments
Note on J165: Evaluators Comments
Note on E166: Evaluators Comments
Note on F166: Evaluators Comments
Note on G166: Evaluators Comments
Note on H166: Evaluators Comments
Note on I166: Evaluators Comments
Note on J166: Evaluators Comments
Note on E167: Evaluators Comments
Note on F167: Evaluators Comments
Note on G167: Evaluators Comments
Note on H167: Evaluators Comments
Note on I167: Evaluators Comments
Note on J167: Evaluators Comments
Note on E168: Evaluators Comments
Note on F168: Evaluators Comments
Note on G168: Evaluators Comments
Note on H168: Evaluators Comments
Note on I168: Evaluators Comments
Note on J168: Evaluators Comments
Note on E169: Evaluators Comments
Note on F169: Evaluators Comments
Note on G169: Evaluators Comments
Note on H169: Evaluators Comments
Note on I169: Evaluators Comments
Note on J169: Evaluators Comments