## General Requirements
| RFT Compliance Matrix |  |  |  | Reference Number | SF-CF-25
[5 empty] | Owner | PRO
[5 empty] | Revision Code | 3.0
[5 empty] | Implementation Date | 2024-03-01
Project Name:
Reference Number:
RFT Article (Part Number or Title) | Requirements (Description) | Killer | Fully Compliant | Partially Compliant | Non-Compliant | Reference (Specify document & page nb)
Article 4 | Conditions for the Participation of the Eligible Bidders
4.1 | 1- Bidders shall meet the following conditions, declared in accordance with the required documents in the First section of this Article mentioned below as (First: Envelope No. (1) Administrative Documents and Transactions):
a- That there is no proven violation, by the bidders, of professional ethics generally accepted and stipulated in the relevant provisions, if any;
b- Bidders have the legal capacity to enter into the procurement contract;
c- Bidders have fulfilled their obligations to pay taxes and social security contributions;
d- Bidders have not been convicted, neither their directors nor employees involved with the procurement process, by a court decision of any criminal offence - even if the verdict can still be appealed - related to their professional conduct or the making of false statements or misrepresentations as to their qualifications to enter into a procurement contract, or corrupting a public procurement or a contract awarding process, or have not been otherwise disqualified pursuant to administrative suspension or debarment proceedings, or have been in a situation of exclusion from participation in public procurements;
e- Bidders are not the subject of legal proceedings for insolvency or bankruptcy, or were declared bankrupt by a court of law;
f- Bidders have not been convicted by a court decision - even if the verdict can still be appealed - of usury or money laundering;
g- Bidders have not participated in the decision-making process of the contracting authority or have any conflict of interest, or any material interest linking them to any of the decision makers;
h- Any other conditions set forth by the contracting authority in the tender documents that are commensurate with the required works;
i- Certificate from the Ministry of Economy proving compliance with the provisions of the Law on Boycott of Israel for foreign companies (added by Law No. 309, dated April 19, 2023).
j- Declaration of the economic beneficiaries (according to Law No. 309, dated April 19, 2023).
4.2 | 2- The bid must be submitted clearly and unequivocally without any deletion, alteration, or modification.
4.3 | 3- The bidders state in their offer that they have reviewed the Tender document and its complementary documents and have obtained a copy. They accept and undertake to adhere to all the conditions outlined therein without any reservations or exceptions. The bidder submits their offer on this basis and affixes financial stamps worth fifty thousand Lebanese pounds covering all the documents.
4.4 | 4- Any bid containing reservations or exceptions is rejected.
4.5 | 5- The bidder mentions in their offer a clear address and place of residence for prompt communication.
Administrative Documents and Transactions | First: Envelope No. (1) Administrative Documents and Transactions
A- General Conditions:
1- Undertaking Letter (Declaration), according to the attached form, signed and stamped by the bidder, this Undertaking includes the bidder's confirmation of their commitment to the price and the validity of the offer. A financial stamp of 50,000 L.L. is affixed.
2- Commercial Circular specifying the authorized signatory of the bidder and a sample of their signature.
3- Legal Authorization: If the offer is signed by someone other than the person authorized to sign according to the commercial circular, it must be notarized by a notary public.
4- Police Record of the Authorized Signatory or his “legal representative”, not exceeding three months from the bid opening date.
5- Partnership Contract legalized by a notary public if required.
6- Registration Certificate before the Directorate of Value Added Tax, if applicable, or a certificate of non-registration if not subject to it. In the latter case, the bidder commits to their bid price even if they become registered for VAT during the execution period.
7- Registration Certificate issued by the Ministry of Finance – Department of Revenue.
8- Certificate issued by the Ministry of Finance proving the bidder's compliance with tax obligations.
9- Clearance Certificate from the National Social Security Fund “comprehensive or valid for participation in public tenders and bids” valid on the date of the bid opening session, stating that the bidder has paid all his subscriptions (the bidder must be registered before the National Social Security Fund and any statement mentioning the phrase “unregistered institution” will be rejected).
10- Certificate issued by the Municipality, proving full payment of municipal fees by the bidder, issued by the municipality within its jurisdiction based on the commercial registration certificate.
11- Comprehensive Certificate issued by the Commercial Register showing founders, members, contributors, or partners, authorized signatories, the manager, capital, the bidder's activity, and ongoing liabilities.
12- Certificate issued by the relevant authorities proving that the bidder is not in a state of bankruptcy.
13- Certificate issued by the relevant authorities proving that the bidder is not in a state of judicial liquidation.
14- Bid bond as required in the specific Tender document of the procurement project, in accordance with Articles 34 and 36 of the Public Procurement Law.
15- Declaration from the Bidder identifying the economic beneficiary/beneficiaries according to Form M18 issued by the Ministry of Finance (any natural person who owns or effectively controls the ultimate outcome of the activity practiced by the bidder, either directly or indirectly, whether the bidder is a natural person or a legal entity.)
16- Copies of Identification Cards (ID/Passport) for the economic beneficiary/beneficiaries.
17- Copies of Identification Cards (ID/Passport) for each person representing the bidder (those acting on behalf of the bidder in their relationship with the contracting authority: legal representative, representative of the legal entity, or authorized signatory).
18- Integrity Declaration Document signed by the bidder in accordance with the prescribed format
Miscellaneous | The bidder shall declare any relative relations with any Alfa employee up to the 4th degree under Clause 30 of the PPL, for MIC1 to be able to assess the existing of any potential conflict of interests which may lead to deprive the bidder from participating to the tender under the risk of disqualification.
The bidder or any of his employees, partners, agents, contributors, consultants, or their relatives shall declare any relationships that may lead to a conflict of interest in the subject of this contract.
Special Conditions | B- Special Conditions Regarding the Subject of the Contract:
Financial Qualifications | 1- Financial Qualifications (To be determined based on the size and nature of the contract).
Technical/Professional Qualifications | 2- Technical/Professional Qualifications (To be determined based on the nature of the contract):
1- Certificate from the Chamber of Commerce, Industry, and Agriculture confirming that the bidder is engaged in the activities related to the subject of the contract, valid as of the date of the bidding session and valid for participation in public tenders.
2- Clearance certificate from the Order of Engineers…
3- Clearance certificate from the Contractors Syndicate…
4- ISO certificate.
5- Five Certificates of good execution and completion for similar projects in terms of size and type.
6- Technical proposal according to the required specifications in the appendix (1) of the RFT.
7- Declaration of site inspection by the bidder, denying any unfamiliarity, according to the attached model.
Participation of a foreign bidder | C- In case of the participation of a foreign bidder, the bidder must comply with one of the following conditions:
1- is part of a coalition that includes at least one Lebanese company that meets the conditions required by the specific Tender document of the procurement project.
2- The personal presence of the legal representative of the company to participate in the procurement proceedings (not mandatory).
3- Has an authorized agent or representative in Lebanon responsible for signing the contract on its behalf.
In addition to the above conditions, the foreign bidder must submit the following:
1- Certificate registration of the company or certificate of establishment issued by the relevant authorities in their country.
2- Certificate from the Lebanese Ministry of Economy and Trade confirming compliance with the provisions of the Law on Israel Boycott.
3- The required certificates according to paragraph (First) above, according to the laws of the country where the bidder is located, provided that these certificates are authenticated according to the regulations of the competent authorities.
For certificates issued without an expiration date, the validity date of each certificate is determined according to its nature, not exceeding six months from the date of the bid opening session.
Information Security Specifications | Information Security Specifications Issuing Department to determine whether all or part of this Article is applicable to their specific RFT
The Bidder shall commit to refrain from offering any product / equipment which can cause security threat or information leakage that jeopardizes MIC1 network security. (K)
The Bidder shall accept that MIC1 runs a vulnerability scan on the proposed solution prior to issuing the acceptance and in case any vulnerability is found, the Bidder undertakes to take the necessary actions to remedy such vulnerability within _____________________ days from its notification.
The Bidder shall mention the security standards adopted/followed in designing the proposed solution.
The Bidder should specify if it has acquired the ISO27001 certification or any other equivalent security certification and submit with the Offer a copy of such certificate.
The Bidder shall not hard code passwords in the proposed solution.
The provided application should run without the need of root (unix) and / or admin (win) privileges.
Source code of proposed application should be owned by MIC1.
System shall allow generation of user, operator as well as alarms logs.
Solution and storage shall be sized to host history logs for at least 1 year back.
The Bidder should submit a data flow diagram and schema of the solution architecture.
In case of online payment, the Bidder shall use encryption. (K)
The Bidder shall harden systems servers / storage before being published online, and describe hardening aspects applied on each type.
The Bidder shall describe security checking and audits performed on the designed solution prior to putting it on the market.
The Bidder shall change default errors / messages and configuration.
Application should support role-based access, specific privileges per user (i.e specific access to application modules and reports)
Database should support restricted access per user or groups to data (i.e access per field or per table, …)
Encryption shall be used in all communications / interactions between systems, especially if the communication is through web access. Web based access shall always be used through HTTP+SSL.
Each user shall have only one account / profile to access data.
Least-privileges should always be specified on nodes / applications.
Pseudocode flow chart shall be provided by the Bidders.
The Bidder should commit to improve solution / systems information security weaknesses whenever needed or highlighted by MIC1 information security team.
Health, Safety and Environmental Specifications | To ensure that the proposed products and services bidders are compliant with HSE culture, bidders should state basic HSE specifications and compliance information:
Bidder shall provide the product’s specifications that have an environmental impact (power consumption, gas emissions, etc…)
Bidder shall provide the product specifications that contribute into preserving the environment (made of recycled material, ozone friendly, low volatile organic compounds, etc…)
Bidder shall provide the product’s specifications that contribute towards the health and safety of the users (ergonomic design, safety features, etc)
Bidder shall state the safety measures being followed by personnel performing the work on Alfa’s sites (ISO45001 certification, specific best practices, etc…).
Bidder shall provide the product’s life cycle data if available.

## Technical Requirements
| RFT Compliance Matrix |  |  |  | Reference Number | SF-CF-25
[5 empty] | Owner | PRO
[5 empty] | Revision Code | 3.0
[5 empty] | Implementation Date | 2024-03-01
Project Name: | JDEIDET DATA CENTER
Reference Number: | 26 33 43.00.BCC01 - Battery Chargers - Core 5.8-70KW - 10.2023
RFT Article (Part Number or Title) | Requirements (Description) | Killer | Fully Compliant | Partially Compliant | Non-Compliant | Reference (Specify document & page nb)
1 GENERAL
1.1 SUMMARY
A. Charger for core Telco sites
1.2 REFERENCES
A. Compliancy with international standards:
1. Electrical safety: UL 60950-1, EN 60950-1, CSA 22.2
2. EMC:
a. EN 61000-6-1 (immunity, light industry)
b. EN 61000-6-2 (immunity, industry)
c. EN 61000-6-3 (emission, light industry)
d. EN 61000-6-4 (emission, industry)
e. EN 61000-3-2
f. ETSI EN 300 386 V.1.3.2 (telecommunication network)
g. ETSI EN 300 386 V.1.4.1
h. Telcordia NEBS GR1089 CORE
3. Environment:
a. ETSI EN 300 019: 2-1 (Class 1.2), 2-2 (Class 2.3) & 2-3 (Class 3.2)
b. ETSI EN 300 132-2
c. Telcordia NEBS GR63 CORE Zone 4
d. RoHS (2011/65/EU) compliant
B. Laboratory approvals
1. The bidder should submit a test report certificate from one of the below laboratories:
a. UL (US and Canada)
b. FCC (Class B) Verification
c. IEC -60950
d. EMC
1.3 SUBMITTALS
A. Manuals
1. Two (2) complete set of documentations shall be provided by the supplier. Documents should include:
a. Technical specifications
b. Installation guide
c. Maintenance procedure
d. Manufacturer recommendations
e. Warranty Certificate
1.4 WARRANTY
A. Equipment
1. The supplied products shall be covered by full supplier warranty for a minimum period of one (1) year from delivery to site at a full repair and replacement service.
2. Warranty shall include all defected spare parts and workmanship.
B. Services
1. Installation and dismantling
a. The supplier is responsible for the dismantling, hoisting, transportation and re-installation for parts that cannot be repaired or replaced on site
2. Part replacement/repair
a. For any part replacement or repair service the warranty for the repaired or new part shall be a minimum of 6 (six) months from the date of receipt of the repaired or new part. In case a part was repaired twice already under this warranty and the equipment becomes faulty again within up to six months the Operator on its discretion may request replacement of the complete equipment
3. Major defect
a. In case of major defect in the supplied products, the Operator reserves the right to reject the equipment. The supplier shall replace the defected system/parts under no cost from the Operator, including dismantling, hoisting, transportation and re-installation
2 PRODUCTS
2.1 MANUFACTURERS
A. Manufacturing:
1. Manufacturer should be ISO 9001:2015 certified.
2.2 RECTIFIER MODULE
A. Input (AC Supply)
1. Input nominal voltage: 380 Vac, 3 Phase
2. Operating voltage range: 323 Vac to 437 Vac
3. Permitted Input voltage variation: 260 Vac to 456 Vac
4. Connectivity: 3 phases with neutral
5. Frequency: 45 to 66 Hz
6. Power factor > 0.99 (50% to 100% output current)
7. Total harmonic distortion: < 5% from 50% to 100% load
B. Output (DC Supply)
1. Nominal Voltage: 48 Vdc
2. DC output adjustment range: - 42 Vdc to – 58 Vdc
3. Nominal output power: 5800 W @ Vout 48Vdc
4. Efficiency > 96% peak
5. Current limitation: 0 to 120 Adc
6. Over-voltage protection
7. Under-voltage protection (system shutdown)
C. Other Specifications
1. Hot-pluggable
2. DSP (Digital Signalling Processor) switch mode technology
3. Rectifier Alarm and Signaling: Alarm and status reported via CAN bus to system Controller
4. Visual Indications:
a. Green LED = Normal operation
b. Yellow LED = Alarm
c. Red LED = Failure
d. Flashing Red LED = Fan failure
D. Rectifier Module Environmental
1. Operating temperature range: -40°C to +65°C
2. Relative humidity: 0 to 95%
3. EMC: ETSI EN 300 386 class B
4. Safety: IEC 60950, EN 60950, UL 60950
2.3 CONTROLLER MODULE
A. Controller Module Features
1. Input voltage: 19 Vdc to 60 Vdc
2. Operating temperature: - 40°C to + 75°c
3. Relative humidity: 0 to 95%
4. Hot pluggable in stand-alone or embedded power plants
5. Fail proof: in case the controller fails to operate, the rectifiers/system continue to supply power without power interruption.
6. EMC: EN 300 386:2001 class B
7. Safety: IEC 60950-1, EN 60950-1, UL 60950-1
8. Approvals: CE, UL
9. Battery Management
B. Controller Module Battery Management
1. Battery Charge Temperature Compensation
5. Battery Equalize Charge
6. Battery Charge Current Limit
7. High and Low Battery Temperature Alarms
8. Battery Thermal Runaway Management (BTRM) Feature (Reduces Voltage during a High Battery Temperature Condition)
9. Battery Discharge Tests
10. Battery Test Logs
11. Battery LVD (Low Voltage Disconnect)
12. Battery Capacity Prediction
C. Controller Module Display & Communication
1. Display: LCD with 8 x 16 characters
2. External Communication: RS232, RS485, Ethernet, USB
3. Protocol: HTTP, SNMP, EEM, SocTpe, RSoc
4. Unattended battery test: advanced scheduled test /constant test / fast test
D. Controller Module Alarms
1. Digital inputs: 1 input for status of SPD auxiliary contacts, 10 load fuses, 4 battery fuses, bi-stable contactor status
2. Analogue inputs: 2 battery currents, 1 load current, 1 bus voltage, 2 battery voltages, 3 temperatures, 3 AC voltages
3. Low voltage disconnects: 2 (mono & bi-stable contactor)
4. Module alarms (not limited to):
a. AC mains failure
b. Rectifier failure
c. DC/DC converter failure
d. High voltage shut-down
e. Fan failure
f. Thermal derating (of rectifier output due to high temperature)
g. Circuit breaker trip alarm
h. Over-temperature
i. Under-voltage
5. Alarm History Log: records 600 latest alarms
E. WEB Interface Access
Via the WEB Interface, a User (with proper access level) can:
1. View real-time operating information (rectifiers, converters, AC, DC, Batteries, etc)
2. View and download information recorded in logs.
3. Send control commands.
4. Set programmable parameters.
5. Download and upload configuration files.
6. Download firmware to the Controller.
F. Rectifier Redundancy Function
1. The controller turns off a number of the rectifiers in order to increase the load per rectifier. By having the rectifiers operate at their peak, system efficiency is optimized.
2. The controller rotates the rectifiers on standby with the active rectifiers, thereby balancing the exposure.
2.4 DC POWER CABINET
A. General Features
1. The system should be of modular type
2. DC power cabinet should be of modular type and easily interconnected in parallel with similar dc power cabinets.
3. Hot-pluggable rectifier modules
4. Plug-n-play rectifiers: add rectifiers without changing the settings and making adjustments; no system interruption
5. The total system capacity should be divided into several parallel rectifiers’ modules.
6. The rectifier modules should be controlled and monitored by 2 controller modules connected in parallel; one master and the second is redundant
7. Each rectifier module should be protected with one dedicated circuit breaker
8. Low Voltage Battery Disconnect (LVBD): the system should be able to disconnect the batteries at adjustable battery voltage
9. Low Voltage Load Disconnect (LLBD): the system should be able to disconnect the load at adjustable battery voltage
10. Alarm dry contact for each fuse/circuit breaker to be also provided for remote alarm monitoring.
B. Electrical System Specifications
1. Nominal system voltage: - 48 V DC
2. Adjustable range for operating voltage: - 42V DC to -58 V DC
3. Output power, system: 69.6KW per cabinet (12x 5800W) and expandable up to 278.4KW (4 cabinets)
4. Input voltage, nominal: 480 Vac, 3 phase
5. Input voltage, permitted variation: 260 Vac to 456 Vac
6. Line frequency: 45 Hz – 65 Hz
C. Mechanical System Specifications
1. Recommended dimensions (HxWxD): 2000 x 600 x 600 mm
2. Recommended weight: < 280 Kg (fully equipped)
3. Cabling configuration: bottom
4. Access: front
5. Equipped with lockable door
D. Cabinet System Units
1. Fuses:
a. Battery Connection Unit: 4x NH3 sized fuses and LVD (630A)
b. Distribution Fuse Unit: 6x NH2 sized fuses with fuse size 500 A
2. AC distribution system with circuit breaker for each rectifier module
3. Rectifier modules: 12 rectifiers per cabinet
4. Controllers: Two controllers (main and redundant)
5. Temperature sensor with cable
6. Surge protection device
2.5 DC DISTRIBUTION CABINET
A. General Features
1. Modular design: initial and field installed interchangeable fuse and circuit breaker distribution modules
2. Fuse protection: utilizing TPS, TLS and TPL fuses protects circuits ranging from 3 to 250A
3. Circuit breaker protection: plug-in bullet nose breakers available in current ratings of 1 to 250A
4. Cable access: to be provided on left and right of the cabinet in order to simplify installation
5. Feeders entry: bottom
6. Current rating: up to 2100A
7. Each cabinet should house 6 distribution panels consisting of fuse holders or circuit breakers
8. Internal Ground/Return Bar: two full cabinet length internal ground/return bars (one per side).
9. Equipped with Distribution Panel Paralleling Bar to parallel distribution panels
10. Equipped with Ground/Return Input Assembly
11. Auxiliary Fuse Circuit Card: This circuit card provides four fuses for auxiliary equipment loads. Terminal blocks are also provided on the circuit card.
B. Distribution Panel
1. Current rating: 600A per panel
2. Shall house ten (10) TPL fuse holders
3. Shall house twenty-eight (28) toggle-handle bullet nose circuit breaker and/or TLS/TPS fuse (with bullet nose fuse holder)
C. High Ohmic Distribution Panel
1. Equipped with high ohmic toggle-handle bullet nose circuit breaker
2. MCB Ratings High Ohmic (30mΩ): 15A, 20A, 25A, 30A
3. MCB Current Breaking Capacity: 10kA
4. Voltage Range: 18 - 60Vdc
5. Alarms: MCB tripped detection (electronic)
6. Approved brand: Emerson or equivalent
D. High Ohmic Distribution Cabinet
1. Consists of 6 distribution panels distributed as follows:
2. Distribution panel No.1: 28x 15A CB
3. Distribution panel No.2: 28x 15A CB
4. Distribution panel No.3: 28x 15A CB
5. Distribution panel No.4: 28x 30A CB
6. Distribution panel No.5: 28x 30A CB
7. Distribution panel No.6: 28x 30A CB
E. High Ohmic Spare Circuit Breakers
1. Spare circuit breakers should be provided as follows:
a. 15A circuit breaker: Qty= 100
b. 30A circuit breaker: Qty= 100
F. Low Ohmic Distribution Panel
1. Equipped with twenty-eight (28) TLS fuse (with bullet nose fuse holder)
2. TLS rating: 1 to 125A
3. TLS current Breaking Capacity: 100kA
4. TLS voltage rating: 170Vdc
5. TLS fuses similar to Littelfuse
G. Low Ohmic Distribution Cabinet
1. Consists of 6 distribution panels distributed as follows:
2. Distribution panel No.1: 28x TLS 15A Fuse
3. Distribution panel No.2: 28x TLS 15A Fuse
4. Distribution panel No.3: 28x TLS 30A Fuse
5. Distribution panel No.4: 28x TLS 30A Fuse
6. Distribution panel No.5: 28x TLS 30A Fuse
7. Distribution panel No.6: 14x TLS 40A Fuse + 14x TLS 60A Fuse
H. Low Ohmic Spare Fuse Links
1. Spare fuse links should be provided as follows:
a. 15A fuse link: Qty= 100
b. 30A fuse link: Qty= 100
c. 40A fuse link: Qty= 100
d. 60A fuse link: Qty= 50
e. 80A fuse link: Qty= 50
f. 100A fuse link: Qty= 50
2.6 DC CABINET ALARMS, METERING, & REMOTE ACCESS
1. Alarm dry contact for each fuse/circuit breaker to be also provided for remote alarm monitoring.
2. External Alarm Circuits: Four (4) relays each provide three (3) sets of Form-C contacts for external alarms. Various available alarms can be mapped to each of the relays. Contact rating is 2A at 30 VDC.
3. Digital Metering:
a. A digital meter is furnished for load voltage and distribution panel current monitoring.
b. The Meter/Alarm Panel provides digital metering of load voltage and current individually for each distribution panel. Also displays system alarm messages and adjustment information.
c. Meter Accuracy: Current: ±1.0%; Voltage: ±0.1%
4. Local Indicators:
a. A status indicator at the top of the bay front panel indicates system status.
b. Each distribution panel has a green indicator which illuminates when power is being supplied to the panel, and a red indicator which illuminates if a fuse or circuit breaker within the panel opens.
c. Each fuse/circuit breaker has a a local alarm indicator on it.
5. Remote Access: Via Web Interface
a. Description: The Web Interface provides remote access to the system monitoring and control functions that are available locally at the Meter/Control Panel.
b. Connection: Ethernet, RJ 45 10BaseT jack.
c. Security: Password Protection & Page Access Levels
2.7 DC VOLTAGE, CURRENT, ENVIRONMENT, & SAFETY SPECIFICATIONS
1. DC nominal voltage: -48Vdc.
2. DC voltage range: -42Vdc to -60Vdc
3. Output Ratings
a. Distribution Panel: 600A, maximum.
b. Distribution Cabinet: 2100A, maximum
4. Operating Ambient Temperature: 0°C to +40°C
5. Operating relative humidity: 0% to 95%, non-condensing
6. Safety Compliance: UL Listed as a DC Power Distribution Center for Communications Equipment
7. NEBS (Network Equipment Building Systems) Compliance: Nationally Recognized Testing Laboratory (NRTL) per GR-1089-CORE and GR-63-CORE.
8. Remote Supervision Software
2.8 ACCESSORIES
A. All necessary accessories required for the proper installation and operation should be included and delivered with the system.
2.9 CONSTRUCTION
A. Identification label
1. Shall be self-adhering identifying:
a. Manufacturer
b. Model
c. Origin of manufacturer
d. Nominal power
2.10 SPARE PARTS
A. Recommended Spare Parts
1. A detailed list of the recommended spare parts for 10 years should be submitted. The exhaustive list of all required spare parts must be provided with pricing information (USD) about each item. The calculation methodology must be described in a separate document based on preventive maintenance procedure and the MTBF for each part.
B. Spare Parts Availability
1. Specify delivery time of spare parts which are in stock and that which are ex-stock. Spare parts should be available for at least 10 years from the PO date.
3 EXECUTION
3.1 INSTALLATION
A. System Installation
1. Shall include:
a. Transportation to site
b. Hoisting to rooftop or green-field
c. Installation and assembly
d. And power connection of system
B. Startup and Commissioning
1. Including startup, commissioning and power system evaluation
2. Commissioning process should be methodical, and documented to ensure that systems and equipment meet established design requirements and expectations.
3. The commissioning process should verify the following:
a. System installed as per specifications
b. System functions properly
c. System is successfully turned over to the user
3.2 TEST & TURN-UP
1. The installation and full test of the equipment on site after delivery should assure future trouble-free operation
2. Installation will comply with MIC1 requirements as well as the standards and practices of the Telco codes:
a. AC Power and Grounding
b. DC Power and Grounding to Telco Standards - Grounding, Bonding, & Surge Protection
c. Cabinet Installations and Outside Plant Services including Cable Rack
d. Primary Cabling, Secondary distribution wiring and ladder rack
3.3 LOAD TESTS
1. Load test should be performed as per manufacturer recommendation.
3.4 TRAININGS
1. Proper and adequate trainings should be provided to staff who will operate the system
2. The training should cover the detailed Operation and Maintenance requirements of the purchased products/systems.
3. The training will be tailored toward the day to day operation, maintenance, and troubleshooting of the purchased system components.
4. Number of trainees: 15
5. Training location: at vendor workshop
END OF SECTION

## Grade of Compliancy
| RFT Compliance Matrix | Reference Number | SF-CF-25
|  | Owner | PRO
|  | Revision Code | 3.0
|  | Implementation Date | 2024-03-01
Grade of Compliance range from 0 to 15 with a step of 1 unit:
15 : Compliant with additional value, not initially included in the requirements
10 : Fully compliant
4 - 5 - 6: Partially compliant
0 : Not compliant
K : Disqualification