## grade of compliance range
| RFT Scoring Sheet | Reference Number | SF-CF-87
|  | Owner | PRO/PMO
|  | Revision Code | 2.0
|  | Implementation Date | 2021-09-01
Grade of Compliance range from 0 to 15 with a step of 1 unit:
15 : Compliant with additional value, not initially included in the requirements
10 : Fully compliant
4 - 5 - 6: Partially compliant
0 : Not compliant
K : Disqualification

## weight
| RFT Scoring Sheet | [11 empty] | Reference Number |  | SF-CF-87
[13 empty] | Owner |  | PRO/PMO
[13 empty] | Revision Code |  | 2.0
[13 empty] | Implementation Date |  | 2021-09-01
Project Name | JDEIDET DATA CENTER
Weight Distribution | 50% Technical 50% Commercial
Article | Requirements | Weight | Responsible Entity | Supplier 1 | Supplier 2 | Supplier 3 | Supplier 4 | Supplier 5 | Supplier 6 | Remarks | Supplier 1 Final | Supplier 2 Final | Supplier 3 Final | Supplier 4 Final | Supplier 5 Final | Supplier 6 Final
| 1 GENERAL | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1.1 SUMMARY | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Charger for core Telco sites | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1.2 REFERENCES | 5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Compliancy with international standards: | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Electrical safety: UL 60950-1, EN 60950-1, CSA 22.2 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. EMC: | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| a. EN 61000-6-1 (immunity, light industry) | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| b. EN 61000-6-2 (immunity, industry) | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| c. EN 61000-6-3 (emission, light industry) | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| d. EN 61000-6-4 (emission, industry) | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| e. EN 61000-3-2 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| f. ETSI EN 300 386 V.1.3.2 (telecommunication network) | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| g. ETSI EN 300 386 V.1.4.1 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| h. Telcordia NEBS GR1089 CORE | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. Environment: | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| a. ETSI EN 300 019: 2-1 (Class 1.2), 2-2 (Class 2.3) & 2-3 (Class 3.2) | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| b. ETSI EN 300 132-2 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| c. Telcordia NEBS GR63 CORE Zone 4 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| d. RoHS (2011/65/EU) compliant | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Laboratory approvals | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. The bidder should submit a test report certificate from one of the below laboratories: | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| a. UL (US and Canada) | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| b. FCC (Class B) Verification | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| c. IEC -60950 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| d. EMC | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1.3 SUBMITTALS | 5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Manuals | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Two (2) complete set of documentations shall be provided by the supplier. Documents should include: | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| a. Technical specifications | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| b. Installation guide | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| c. Maintenance procedure | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| d. Manufacturer recommendations | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| e. Warranty Certificate | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1.4 WARRANTY | 5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Equipment | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. The supplied products shall be covered by full supplier warranty for a minimum period of one (1) year from delivery to site at a full repair and replacement service. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Warranty shall include all defected spare parts and workmanship. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Services | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Installation and dismantling | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| a. The supplier is responsible for the dismantling, hoisting, transportation and re-installation for parts that cannot be repaired or replaced on site | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Part replacement/repair | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| a. For any part replacement or repair service the warranty for the repaired or new part shall be a minimum of 6 (six) months from the date of receipt of the repaired or new part. In case a part was repaired twice already under this warranty and the equipment becomes faulty again within up to six months the Operator on its discretion may request replacement of the complete equipment | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. Major defect | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| a. In case of major defect in the supplied products, the Operator reserves the right to reject the equipment. The supplier shall replace the defected system/parts under no cost from the Operator, including dismantling, hoisting, transportation and re-installation | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2 PRODUCTS | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.1 MANUFACTURERS | 5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Manufacturing: | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Manufacturer should be ISO 9001:2015 certified. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.2 RECTIFIER MODULE | 10 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Input (AC Supply) | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Input nominal voltage: 380 Vac, 3 Phase | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Operating voltage range: 323 Vac to 437 Vac | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. Permitted Input voltage variation: 260 Vac to 456 Vac | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 4. Connectivity: 3 phases with neutral | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5. Frequency: 45 to 66 Hz | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 6. Power factor > 0.99 (50% to 100% output current) | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 7. Total harmonic distortion: < 5% from 50% to 100% load | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Output (DC Supply) | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Nominal Voltage: 48 Vdc | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. DC output adjustment range: - 42 Vdc to – 58 Vdc | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. Nominal output power: 5800 W @ Vout 48Vdc | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 4. Efficiency > 96% peak | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5. Current limitation: 0 to 120 Adc | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 6. Over-voltage protection | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 7. Under-voltage protection (system shutdown) | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| C. Other Specifications | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Hot-pluggable | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. DSP (Digital Signalling Processor) switch mode technology | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. Rectifier Alarm and Signaling: Alarm and status reported via CAN bus to system Controller | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 4. Visual Indications: | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| a. Green LED = Normal operation | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| b. Yellow LED = Alarm | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| c. Red LED = Failure | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| d. Flashing Red LED = Fan failure | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| D. Rectifier Module Environmental | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Operating temperature range: -40°C to +65°C | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Relative humidity: 0 to 95% | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. EMC: ETSI EN 300 386 class B | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 4. Safety: IEC 60950, EN 60950, UL 60950 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.3 CONTROLLER MODULE | 10 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Controller Module Features | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Input voltage: 19 Vdc to 60 Vdc | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Operating temperature: - 40°C to + 75°c | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. Relative humidity: 0 to 95% | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 4. Hot pluggable in stand-alone or embedded power plants | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5. Fail proof: in case the controller fails to operate, the rectifiers/system continue to supply power without power interruption. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 6. EMC: EN 300 386:2001 class B | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 7. Safety: IEC 60950-1, EN 60950-1, UL 60950-1 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 8. Approvals: CE, UL | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 9. Battery Management | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Controller Module Battery Management | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Battery Charge Temperature Compensation | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5. Battery Equalize Charge | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 6. Battery Charge Current Limit | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 7. High and Low Battery Temperature Alarms | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 8. Battery Thermal Runaway Management (BTRM) Feature (Reduces Voltage during a High Battery Temperature Condition) | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 9. Battery Discharge Tests | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 10. Battery Test Logs | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 11. Battery LVD (Low Voltage Disconnect) | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 12. Battery Capacity Prediction | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| C. Controller Module Display & Communication | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Display: LCD with 8 x 16 characters | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. External Communication: RS232, RS485, Ethernet, USB | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. Protocol: HTTP, SNMP, EEM, SocTpe, RSoc | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 4. Unattended battery test: advanced scheduled test /constant test / fast test | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| D. Controller Module Alarms | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Digital inputs: 1 input for status of SPD auxiliary contacts, 10 load fuses, 4 battery fuses, bi-stable contactor status | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Analogue inputs: 2 battery currents, 1 load current, 1 bus voltage, 2 battery voltages, 3 temperatures, 3 AC voltages | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. Low voltage disconnects: 2 (mono & bi-stable contactor) | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 4. Module alarms (not limited to): | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| a. AC mains failure | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| b. Rectifier failure | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| c. DC/DC converter failure | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| d. High voltage shut-down | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| e. Fan failure | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| f. Thermal derating (of rectifier output due to high temperature) | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| g. Circuit breaker trip alarm | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| h. Over-temperature | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| i. Under-voltage | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5. Alarm History Log: records 600 latest alarms | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| E. WEB Interface Access | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Via the WEB Interface, a User (with proper access level) can: | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. View real-time operating information (rectifiers, converters, AC, DC, Batteries, etc) | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. View and download information recorded in logs. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. Send control commands. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 4. Set programmable parameters. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5. Download and upload configuration files. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 6. Download firmware to the Controller. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| F. Rectifier Redundancy Function | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. The controller turns off a number of the rectifiers in order to increase the load per rectifier. By having the rectifiers operate at their peak, system efficiency is optimized. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. The controller rotates the rectifiers on standby with the active rectifiers, thereby balancing the exposure. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.4 DC POWER CABINET | 10 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. General Features | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. The system should be of modular type | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. DC power cabinet should be of modular type and easily interconnected in parallel with similar dc power cabinets. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. Hot-pluggable rectifier modules | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 4. Plug-n-play rectifiers: add rectifiers without changing the settings and making adjustments; no system interruption | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5. The total system capacity should be divided into several parallel rectifiers’ modules. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 6. The rectifier modules should be controlled and monitored by 2 controller modules connected in parallel; one master and the second is redundant | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 7. Each rectifier module should be protected with one dedicated circuit breaker | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 8. Low Voltage Battery Disconnect (LVBD): the system should be able to disconnect the batteries at adjustable battery voltage | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 9. Low Voltage Load Disconnect (LLBD): the system should be able to disconnect the load at adjustable battery voltage | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 10. Alarm dry contact for each fuse/circuit breaker to be also provided for remote alarm monitoring. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Electrical System Specifications | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Nominal system voltage: - 48 V DC | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Adjustable range for operating voltage: - 42V DC to -58 V DC | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. Output power, system: 69.6KW per cabinet (12x 5800W) and expandable up to 278.4KW (4 cabinets) | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 4. Input voltage, nominal: 480 Vac, 3 phase | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5. Input voltage, permitted variation: 260 Vac to 456 Vac | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 6. Line frequency: 45 Hz – 65 Hz | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| C. Mechanical System Specifications | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Recommended dimensions (HxWxD): 2000 x 600 x 600 mm | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Recommended weight: < 280 Kg (fully equipped) | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. Cabling configuration: bottom | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 4. Access: front | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5. Equipped with lockable door | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| D. Cabinet System Units | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Fuses: | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| a. Battery Connection Unit: 4x NH3 sized fuses and LVD (630A) | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| b. Distribution Fuse Unit: 6x NH2 sized fuses with fuse size 500 A | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. AC distribution system with circuit breaker for each rectifier module | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. Rectifier modules: 12 rectifiers per cabinet | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 4. Controllers: Two controllers (main and redundant) | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5. Temperature sensor with cable | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 6. Surge protection device | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.5 DC DISTRIBUTION CABINET | 10 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. General Features | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Modular design: initial and field installed interchangeable fuse and circuit breaker distribution modules | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Fuse protection: utilizing TPS, TLS and TPL fuses protects circuits ranging from 3 to 250A | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. Circuit breaker protection: plug-in bullet nose breakers available in current ratings of 1 to 250A | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 4. Cable access: to be provided on left and right of the cabinet in order to simplify installation | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5. Feeders entry: bottom | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 6. Current rating: up to 2100A | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 7. Each cabinet should house 6 distribution panels consisting of fuse holders or circuit breakers | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 8. Internal Ground/Return Bar: two full cabinet length internal ground/return bars (one per side). | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 9. Equipped with Distribution Panel Paralleling Bar to parallel distribution panels | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 10. Equipped with Ground/Return Input Assembly | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 11. Auxiliary Fuse Circuit Card: This circuit card provides four fuses for auxiliary equipment loads. Terminal blocks are also provided on the circuit card. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Distribution Panel | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Current rating: 600A per panel | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Shall house ten (10) TPL fuse holders | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. Shall house twenty-eight (28) toggle-handle bullet nose circuit breaker and/or TLS/TPS fuse (with bullet nose fuse holder) | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| C. High Ohmic Distribution Panel | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Equipped with high ohmic toggle-handle bullet nose circuit breaker | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. MCB Ratings High Ohmic (30mΩ): 15A, 20A, 25A, 30A | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. MCB Current Breaking Capacity: 10kA | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 4. Voltage Range: 18 - 60Vdc | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5. Alarms: MCB tripped detection (electronic) | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 6. Approved brand: Emerson or equivalent | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| D. High Ohmic Distribution Cabinet | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Consists of 6 distribution panels distributed as follows: | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Distribution panel No.1: 28x 15A CB | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. Distribution panel No.2: 28x 15A CB | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 4. Distribution panel No.3: 28x 15A CB | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5. Distribution panel No.4: 28x 30A CB | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 6. Distribution panel No.5: 28x 30A CB | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 7. Distribution panel No.6: 28x 30A CB | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| E. High Ohmic Spare Circuit Breakers | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Spare circuit breakers should be provided as follows: | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| a. 15A circuit breaker: Qty= 100 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| b. 30A circuit breaker: Qty= 100 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| F. Low Ohmic Distribution Panel | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Equipped with twenty-eight (28) TLS fuse (with bullet nose fuse holder) | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. TLS rating: 1 to 125A | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. TLS current Breaking Capacity: 100kA | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 4. TLS voltage rating: 170Vdc | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5. TLS fuses similar to Littelfuse | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| G. Low Ohmic Distribution Cabinet | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Consists of 6 distribution panels distributed as follows: | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Distribution panel No.1: 28x TLS 15A Fuse | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. Distribution panel No.2: 28x TLS 15A Fuse | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 4. Distribution panel No.3: 28x TLS 30A Fuse | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5. Distribution panel No.4: 28x TLS 30A Fuse | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 6. Distribution panel No.5: 28x TLS 30A Fuse | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 7. Distribution panel No.6: 14x TLS 40A Fuse + 14x TLS 60A Fuse | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| H. Low Ohmic Spare Fuse Links | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Spare fuse links should be provided as follows: | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| a. 15A fuse link: Qty= 100 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| b. 30A fuse link: Qty= 100 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| c. 40A fuse link: Qty= 100 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| d. 60A fuse link: Qty= 50 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| e. 80A fuse link: Qty= 50 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| f. 100A fuse link: Qty= 50 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.6 DC CABINET ALARMS, METERING, & REMOTE ACCESS | 5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Alarm dry contact for each fuse/circuit breaker to be also provided for remote alarm monitoring. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. External Alarm Circuits: Four (4) relays each provide three (3) sets of Form-C contacts for external alarms. Various available alarms can be mapped to each of the relays. Contact rating is 2A at 30 VDC. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. Digital Metering: | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| a. A digital meter is furnished for load voltage and distribution panel current monitoring. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| b. The Meter/Alarm Panel provides digital metering of load voltage and current individually for each distribution panel. Also displays system alarm messages and adjustment information. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| c. Meter Accuracy: Current: ±1.0%; Voltage: ±0.1% | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 4. Local Indicators: | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| a. A status indicator at the top of the bay front panel indicates system status. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| b. Each distribution panel has a green indicator which illuminates when power is being supplied to the panel, and a red indicator which illuminates if a fuse or circuit breaker within the panel opens. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| c. Each fuse/circuit breaker has a a local alarm indicator on it. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5. Remote Access: Via Web Interface | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| a. Description: The Web Interface provides remote access to the system monitoring and control functions that are available locally at the Meter/Control Panel. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| b. Connection: Ethernet, RJ 45 10BaseT jack. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| c. Security: Password Protection & Page Access Levels | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.7 DC VOLTAGE, CURRENT, ENVIRONMENT, & SAFETY SPECIFICATIONS | 5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. DC nominal voltage: -48Vdc. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. DC voltage range: -42Vdc to -60Vdc | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. Output Ratings | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| a. Distribution Panel: 600A, maximum. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| b. Distribution Cabinet: 2100A, maximum | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 4. Operating Ambient Temperature: 0°C to +40°C | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5. Operating relative humidity: 0% to 95%, non-condensing | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 6. Safety Compliance: UL Listed as a DC Power Distribution Center for Communications Equipment | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 7. NEBS (Network Equipment Building Systems) Compliance: Nationally Recognized Testing Laboratory (NRTL) per GR-1089-CORE and GR-63-CORE. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 8. Remote Supervision Software | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.8 ACCESSORIES | 5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. All necessary accessories required for the proper installation and operation should be included and delivered with the system. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.9 CONSTRUCTION | 3 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Identification label | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Shall be self-adhering identifying: | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| a. Manufacturer | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| b. Model | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| c. Origin of manufacturer | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| d. Nominal power | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2.10 SPARE PARTS | 5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. Recommended Spare Parts | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. A detailed list of the recommended spare parts for 10 years should be submitted. The exhaustive list of all required spare parts must be provided with pricing information (USD) about each item. The calculation methodology must be described in a separate document based on preventive maintenance procedure and the MTBF for each part. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Spare Parts Availability | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Specify delivery time of spare parts which are in stock and that which are ex-stock. Spare parts should be available for at least 10 years from the PO date. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3 EXECUTION | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3.1 INSTALLATION | 5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| A. System Installation | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Shall include: | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| a. Transportation to site | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| b. Hoisting to rooftop or green-field | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| c. Installation and assembly | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| d. And power connection of system | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| B. Startup and Commissioning | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Including startup, commissioning and power system evaluation | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Commissioning process should be methodical, and documented to ensure that systems and equipment meet established design requirements and expectations. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. The commissioning process should verify the following: | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| a. System installed as per specifications | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| b. System functions properly | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| c. System is successfully turned over to the user | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3.2 TEST & TURN-UP | 5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. The installation and full test of the equipment on site after delivery should assure future trouble-free operation | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. Installation will comply with MIC1 requirements as well as the standards and practices of the Telco codes: | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| a. AC Power and Grounding | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| b. DC Power and Grounding to Telco Standards - Grounding, Bonding, & Surge Protection | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| c. Cabinet Installations and Outside Plant Services including Cable Rack | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| d. Primary Cabling, Secondary distribution wiring and ladder rack | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3.3 LOAD TESTS | 5 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Load test should be performed as per manufacturer recommendation. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3.4 TRAININGS | 2 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 1. Proper and adequate trainings should be provided to staff who will operate the system | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2. The training should cover the detailed Operation and Maintenance requirements of the purchased products/systems. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3. The training will be tailored toward the day to day operation, maintenance, and troubleshooting of the purchased system components. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 4. Number of trainees: 15 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5. Training location: at vendor workshop | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
| END OF SECTION | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 | 0
[11 empty] | SUPPLIER 1 SCORE | SUPPLIER 2 SCORE | SUPPLIER 3 SCORE | SUPPLIER 4 SCORE | SUPPLIER 5 SCORE | SUPPLIER 6 SCORE
* For Requirements defined as ''Killer'', a ‘’Fully Compliant’’ score should be the sole acceptable outcome. Failing to obtain a ‘’Fully Compliant’’ score on the requirements defined as Killers, will mandate immediate disqualification for bidders.
Note on D9: Entity (Department/ Unit) that identified the requirement and that will be responsible for its evaluation.
Note on E9: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on F9: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on G9: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on H9: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on I9: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on J9: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on E11: Evaluators Comments
Note on F11: Evaluators Comments
Note on G11: Evaluators Comments
Note on H11: Evaluators Comments
Note on I11: Evaluators Comments
Note on J11: Evaluators Comments
Note on E12: Evaluators Comments
Note on F12: Evaluators Comments
Note on G12: Evaluators Comments
Note on H12: Evaluators Comments
Note on I12: Evaluators Comments
Note on J12: Evaluators Comments
Note on E13: Evaluators Comments
Note on F13: Evaluators Comments
Note on G13: Evaluators Comments
Note on H13: Evaluators Comments
Note on I13: Evaluators Comments
Note on J13: Evaluators Comments
Note on E14: Evaluators Comments
Note on F14: Evaluators Comments
Note on G14: Evaluators Comments
Note on H14: Evaluators Comments
Note on I14: Evaluators Comments
Note on J14: Evaluators Comments
Note on E15: Evaluators Comments
Note on F15: Evaluators Comments
Note on G15: Evaluators Comments
Note on H15: Evaluators Comments
Note on I15: Evaluators Comments
Note on J15: Evaluators Comments
Note on E16: Evaluators Comments
Note on F16: Evaluators Comments
Note on G16: Evaluators Comments
Note on H16: Evaluators Comments
Note on I16: Evaluators Comments
Note on J16: Evaluators Comments
Note on E17: Evaluators Comments
Note on F17: Evaluators Comments
Note on G17: Evaluators Comments
Note on H17: Evaluators Comments
Note on I17: Evaluators Comments
Note on J17: Evaluators Comments
Note on E18: Evaluators Comments
Note on F18: Evaluators Comments
Note on G18: Evaluators Comments
Note on H18: Evaluators Comments
Note on I18: Evaluators Comments
Note on J18: Evaluators Comments
Note on E19: Evaluators Comments
Note on F19: Evaluators Comments
Note on G19: Evaluators Comments
Note on H19: Evaluators Comments
Note on I19: Evaluators Comments
Note on J19: Evaluators Comments
Note on E20: Evaluators Comments
Note on F20: Evaluators Comments
Note on G20: Evaluators Comments
Note on H20: Evaluators Comments
Note on I20: Evaluators Comments
Note on J20: Evaluators Comments
Note on E21: Evaluators Comments
Note on F21: Evaluators Comments
Note on G21: Evaluators Comments
Note on H21: Evaluators Comments
Note on I21: Evaluators Comments
Note on J21: Evaluators Comments
Note on E22: Evaluators Comments
Note on F22: Evaluators Comments
Note on G22: Evaluators Comments
Note on H22: Evaluators Comments
Note on I22: Evaluators Comments
Note on J22: Evaluators Comments
Note on E23: Evaluators Comments
Note on F23: Evaluators Comments
Note on G23: Evaluators Comments
Note on H23: Evaluators Comments
Note on I23: Evaluators Comments
Note on J23: Evaluators Comments
Note on E24: Evaluators Comments
Note on F24: Evaluators Comments
Note on G24: Evaluators Comments
Note on H24: Evaluators Comments
Note on I24: Evaluators Comments
Note on J24: Evaluators Comments
Note on E25: Evaluators Comments
Note on F25: Evaluators Comments
Note on G25: Evaluators Comments
Note on H25: Evaluators Comments
Note on I25: Evaluators Comments
Note on J25: Evaluators Comments
Note on E26: Evaluators Comments
Note on F26: Evaluators Comments
Note on G26: Evaluators Comments
Note on H26: Evaluators Comments
Note on I26: Evaluators Comments
Note on J26: Evaluators Comments
Note on E27: Evaluators Comments
Note on F27: Evaluators Comments
Note on G27: Evaluators Comments
Note on H27: Evaluators Comments
Note on I27: Evaluators Comments
Note on J27: Evaluators Comments
Note on E28: Evaluators Comments
Note on F28: Evaluators Comments
Note on G28: Evaluators Comments
Note on H28: Evaluators Comments
Note on I28: Evaluators Comments
Note on J28: Evaluators Comments
Note on E29: Evaluators Comments
Note on F29: Evaluators Comments
Note on G29: Evaluators Comments
Note on H29: Evaluators Comments
Note on I29: Evaluators Comments
Note on J29: Evaluators Comments
Note on E30: Evaluators Comments
Note on F30: Evaluators Comments
Note on G30: Evaluators Comments
Note on H30: Evaluators Comments
Note on I30: Evaluators Comments
Note on J30: Evaluators Comments
Note on E31: Evaluators Comments
Note on F31: Evaluators Comments
Note on G31: Evaluators Comments
Note on H31: Evaluators Comments
Note on I31: Evaluators Comments
Note on J31: Evaluators Comments
Note on E32: Evaluators Comments
Note on F32: Evaluators Comments
Note on G32: Evaluators Comments
Note on H32: Evaluators Comments
Note on I32: Evaluators Comments
Note on J32: Evaluators Comments
Note on E33: Evaluators Comments
Note on F33: Evaluators Comments
Note on G33: Evaluators Comments
Note on H33: Evaluators Comments
Note on I33: Evaluators Comments
Note on J33: Evaluators Comments
Note on E34: Evaluators Comments
Note on F34: Evaluators Comments
Note on G34: Evaluators Comments
Note on H34: Evaluators Comments
Note on I34: Evaluators Comments
Note on J34: Evaluators Comments
Note on E35: Evaluators Comments
Note on F35: Evaluators Comments
Note on G35: Evaluators Comments
Note on H35: Evaluators Comments
Note on I35: Evaluators Comments
Note on J35: Evaluators Comments
Note on E36: Evaluators Comments
Note on F36: Evaluators Comments
Note on G36: Evaluators Comments
Note on H36: Evaluators Comments
Note on I36: Evaluators Comments
Note on J36: Evaluators Comments
Note on E37: Evaluators Comments
Note on F37: Evaluators Comments
Note on G37: Evaluators Comments
Note on H37: Evaluators Comments
Note on I37: Evaluators Comments
Note on J37: Evaluators Comments
Note on E38: Evaluators Comments
Note on F38: Evaluators Comments
Note on G38: Evaluators Comments
Note on H38: Evaluators Comments
Note on I38: Evaluators Comments
Note on J38: Evaluators Comments
Note on E39: Evaluators Comments
Note on F39: Evaluators Comments
Note on G39: Evaluators Comments
Note on H39: Evaluators Comments
Note on I39: Evaluators Comments
Note on J39: Evaluators Comments
Note on E40: Evaluators Comments
Note on F40: Evaluators Comments
Note on G40: Evaluators Comments
Note on H40: Evaluators Comments
Note on I40: Evaluators Comments
Note on J40: Evaluators Comments
Note on E41: Evaluators Comments
Note on F41: Evaluators Comments
Note on G41: Evaluators Comments
Note on H41: Evaluators Comments
Note on I41: Evaluators Comments
Note on J41: Evaluators Comments
Note on E42: Evaluators Comments
Note on F42: Evaluators Comments
Note on G42: Evaluators Comments
Note on H42: Evaluators Comments
Note on I42: Evaluators Comments
Note on J42: Evaluators Comments
Note on E43: Evaluators Comments
Note on F43: Evaluators Comments
Note on G43: Evaluators Comments
Note on H43: Evaluators Comments
Note on I43: Evaluators Comments
Note on J43: Evaluators Comments
Note on E44: Evaluators Comments
Note on F44: Evaluators Comments
Note on G44: Evaluators Comments
Note on H44: Evaluators Comments
Note on I44: Evaluators Comments
Note on J44: Evaluators Comments
Note on E45: Evaluators Comments
Note on F45: Evaluators Comments
Note on G45: Evaluators Comments
Note on H45: Evaluators Comments
Note on I45: Evaluators Comments
Note on J45: Evaluators Comments
Note on E46: Evaluators Comments
Note on F46: Evaluators Comments
Note on G46: Evaluators Comments
Note on H46: Evaluators Comments
Note on I46: Evaluators Comments
Note on J46: Evaluators Comments
Note on E47: Evaluators Comments
Note on F47: Evaluators Comments
Note on G47: Evaluators Comments
Note on H47: Evaluators Comments
Note on I47: Evaluators Comments
Note on J47: Evaluators Comments
Note on E48: Evaluators Comments
Note on F48: Evaluators Comments
Note on G48: Evaluators Comments
Note on H48: Evaluators Comments
Note on I48: Evaluators Comments
Note on J48: Evaluators Comments
Note on E49: Evaluators Comments
Note on F49: Evaluators Comments
Note on G49: Evaluators Comments
Note on H49: Evaluators Comments
Note on I49: Evaluators Comments
Note on J49: Evaluators Comments
Note on E50: Evaluators Comments
Note on F50: Evaluators Comments
Note on G50: Evaluators Comments
Note on H50: Evaluators Comments
Note on I50: Evaluators Comments
Note on J50: Evaluators Comments
Note on E51: Evaluators Comments
Note on F51: Evaluators Comments
Note on G51: Evaluators Comments
Note on H51: Evaluators Comments
Note on I51: Evaluators Comments
Note on J51: Evaluators Comments
Note on E52: Evaluators Comments
Note on F52: Evaluators Comments
Note on G52: Evaluators Comments
Note on H52: Evaluators Comments
Note on I52: Evaluators Comments
Note on J52: Evaluators Comments
Note on E53: Evaluators Comments
Note on F53: Evaluators Comments
Note on G53: Evaluators Comments
Note on H53: Evaluators Comments
Note on I53: Evaluators Comments
Note on J53: Evaluators Comments
Note on E54: Evaluators Comments
Note on F54: Evaluators Comments
Note on G54: Evaluators Comments
Note on H54: Evaluators Comments
Note on I54: Evaluators Comments
Note on J54: Evaluators Comments
Note on E55: Evaluators Comments
Note on F55: Evaluators Comments
Note on G55: Evaluators Comments
Note on H55: Evaluators Comments
Note on I55: Evaluators Comments
Note on J55: Evaluators Comments
Note on E56: Evaluators Comments
Note on F56: Evaluators Comments
Note on G56: Evaluators Comments
Note on H56: Evaluators Comments
Note on I56: Evaluators Comments
Note on J56: Evaluators Comments
Note on E57: Evaluators Comments
Note on F57: Evaluators Comments
Note on G57: Evaluators Comments
Note on H57: Evaluators Comments
Note on I57: Evaluators Comments
Note on J57: Evaluators Comments
Note on E58: Evaluators Comments
Note on F58: Evaluators Comments
Note on G58: Evaluators Comments
Note on H58: Evaluators Comments
Note on I58: Evaluators Comments
Note on J58: Evaluators Comments
Note on E59: Evaluators Comments
Note on F59: Evaluators Comments
Note on G59: Evaluators Comments
Note on H59: Evaluators Comments
Note on I59: Evaluators Comments
Note on J59: Evaluators Comments
Note on E60: Evaluators Comments
Note on F60: Evaluators Comments
Note on G60: Evaluators Comments
Note on H60: Evaluators Comments
Note on I60: Evaluators Comments
Note on J60: Evaluators Comments
Note on E61: Evaluators Comments
Note on F61: Evaluators Comments
Note on G61: Evaluators Comments
Note on H61: Evaluators Comments
Note on I61: Evaluators Comments
Note on J61: Evaluators Comments
Note on E62: Evaluators Comments
Note on F62: Evaluators Comments
Note on G62: Evaluators Comments
Note on H62: Evaluators Comments
Note on I62: Evaluators Comments
Note on J62: Evaluators Comments
Note on E63: Evaluators Comments
Note on F63: Evaluators Comments
Note on G63: Evaluators Comments
Note on H63: Evaluators Comments
Note on I63: Evaluators Comments
Note on J63: Evaluators Comments
Note on E64: Evaluators Comments
Note on F64: Evaluators Comments
Note on G64: Evaluators Comments
Note on H64: Evaluators Comments
Note on I64: Evaluators Comments
Note on J64: Evaluators Comments
Note on E65: Evaluators Comments
Note on F65: Evaluators Comments
Note on G65: Evaluators Comments
Note on H65: Evaluators Comments
Note on I65: Evaluators Comments
Note on J65: Evaluators Comments
Note on E66: Evaluators Comments
Note on F66: Evaluators Comments
Note on G66: Evaluators Comments
Note on H66: Evaluators Comments
Note on I66: Evaluators Comments
Note on J66: Evaluators Comments
Note on E67: Evaluators Comments
Note on F67: Evaluators Comments
Note on G67: Evaluators Comments
Note on H67: Evaluators Comments
Note on I67: Evaluators Comments
Note on J67: Evaluators Comments
Note on E68: Evaluators Comments
Note on F68: Evaluators Comments
Note on G68: Evaluators Comments
Note on H68: Evaluators Comments
Note on I68: Evaluators Comments
Note on J68: Evaluators Comments
Note on E69: Evaluators Comments
Note on F69: Evaluators Comments
Note on G69: Evaluators Comments
Note on H69: Evaluators Comments
Note on I69: Evaluators Comments
Note on J69: Evaluators Comments
Note on E70: Evaluators Comments
Note on F70: Evaluators Comments
Note on G70: Evaluators Comments
Note on H70: Evaluators Comments
Note on I70: Evaluators Comments
Note on J70: Evaluators Comments
Note on E71: Evaluators Comments
Note on F71: Evaluators Comments
Note on G71: Evaluators Comments
Note on H71: Evaluators Comments
Note on I71: Evaluators Comments
Note on J71: Evaluators Comments
Note on E72: Evaluators Comments
Note on F72: Evaluators Comments
Note on G72: Evaluators Comments
Note on H72: Evaluators Comments
Note on I72: Evaluators Comments
Note on J72: Evaluators Comments
Note on E73: Evaluators Comments
Note on F73: Evaluators Comments
Note on G73: Evaluators Comments
Note on H73: Evaluators Comments
Note on I73: Evaluators Comments
Note on J73: Evaluators Comments
Note on E74: Evaluators Comments
Note on F74: Evaluators Comments
Note on G74: Evaluators Comments
Note on H74: Evaluators Comments
Note on I74: Evaluators Comments
Note on J74: Evaluators Comments
Note on E75: Evaluators Comments
Note on F75: Evaluators Comments
Note on G75: Evaluators Comments
Note on H75: Evaluators Comments
Note on I75: Evaluators Comments
Note on J75: Evaluators Comments
Note on E76: Evaluators Comments
Note on F76: Evaluators Comments
Note on G76: Evaluators Comments
Note on H76: Evaluators Comments
Note on I76: Evaluators Comments
Note on J76: Evaluators Comments
Note on E77: Evaluators Comments
Note on F77: Evaluators Comments
Note on G77: Evaluators Comments
Note on H77: Evaluators Comments
Note on I77: Evaluators Comments
Note on J77: Evaluators Comments
Note on E78: Evaluators Comments
Note on F78: Evaluators Comments
Note on G78: Evaluators Comments
Note on H78: Evaluators Comments
Note on I78: Evaluators Comments
Note on J78: Evaluators Comments
Note on E79: Evaluators Comments
Note on F79: Evaluators Comments
Note on G79: Evaluators Comments
Note on H79: Evaluators Comments
Note on I79: Evaluators Comments
Note on J79: Evaluators Comments
Note on E80: Evaluators Comments
Note on F80: Evaluators Comments
Note on G80: Evaluators Comments
Note on H80: Evaluators Comments
Note on I80: Evaluators Comments
Note on J80: Evaluators Comments
Note on E81: Evaluators Comments
Note on F81: Evaluators Comments
Note on G81: Evaluators Comments
Note on H81: Evaluators Comments
Note on I81: Evaluators Comments
Note on J81: Evaluators Comments
Note on E82: Evaluators Comments
Note on F82: Evaluators Comments
Note on G82: Evaluators Comments
Note on H82: Evaluators Comments
Note on I82: Evaluators Comments
Note on J82: Evaluators Comments
Note on E83: Evaluators Comments
Note on F83: Evaluators Comments
Note on G83: Evaluators Comments
Note on H83: Evaluators Comments
Note on I83: Evaluators Comments
Note on J83: Evaluators Comments
Note on E84: Evaluators Comments
Note on F84: Evaluators Comments
Note on G84: Evaluators Comments
Note on H84: Evaluators Comments
Note on I84: Evaluators Comments
Note on J84: Evaluators Comments
Note on E85: Evaluators Comments
Note on F85: Evaluators Comments
Note on G85: Evaluators Comments
Note on H85: Evaluators Comments
Note on I85: Evaluators Comments
Note on J85: Evaluators Comments
Note on E86: Evaluators Comments
Note on F86: Evaluators Comments
Note on G86: Evaluators Comments
Note on H86: Evaluators Comments
Note on I86: Evaluators Comments
Note on J86: Evaluators Comments
Note on E87: Evaluators Comments
Note on F87: Evaluators Comments
Note on G87: Evaluators Comments
Note on H87: Evaluators Comments
Note on I87: Evaluators Comments
Note on J87: Evaluators Comments
Note on E88: Evaluators Comments
Note on F88: Evaluators Comments
Note on G88: Evaluators Comments
Note on H88: Evaluators Comments
Note on I88: Evaluators Comments
Note on J88: Evaluators Comments
Note on E89: Evaluators Comments
Note on F89: Evaluators Comments
Note on G89: Evaluators Comments
Note on H89: Evaluators Comments
Note on I89: Evaluators Comments
Note on J89: Evaluators Comments
Note on E90: Evaluators Comments
Note on F90: Evaluators Comments
Note on G90: Evaluators Comments
Note on H90: Evaluators Comments
Note on I90: Evaluators Comments
Note on J90: Evaluators Comments
Note on E91: Evaluators Comments
Note on F91: Evaluators Comments
Note on G91: Evaluators Comments
Note on H91: Evaluators Comments
Note on I91: Evaluators Comments
Note on J91: Evaluators Comments
Note on E92: Evaluators Comments
Note on F92: Evaluators Comments
Note on G92: Evaluators Comments
Note on H92: Evaluators Comments
Note on I92: Evaluators Comments
Note on J92: Evaluators Comments
Note on E93: Evaluators Comments
Note on F93: Evaluators Comments
Note on G93: Evaluators Comments
Note on H93: Evaluators Comments
Note on I93: Evaluators Comments
Note on J93: Evaluators Comments
Note on E94: Evaluators Comments
Note on F94: Evaluators Comments
Note on G94: Evaluators Comments
Note on H94: Evaluators Comments
Note on I94: Evaluators Comments
Note on J94: Evaluators Comments
Note on E95: Evaluators Comments
Note on F95: Evaluators Comments
Note on G95: Evaluators Comments
Note on H95: Evaluators Comments
Note on I95: Evaluators Comments
Note on J95: Evaluators Comments
Note on E96: Evaluators Comments
Note on F96: Evaluators Comments
Note on G96: Evaluators Comments
Note on H96: Evaluators Comments
Note on I96: Evaluators Comments
Note on J96: Evaluators Comments
Note on E97: Evaluators Comments
Note on F97: Evaluators Comments
Note on G97: Evaluators Comments
Note on H97: Evaluators Comments
Note on I97: Evaluators Comments
Note on J97: Evaluators Comments
Note on E98: Evaluators Comments
Note on F98: Evaluators Comments
Note on G98: Evaluators Comments
Note on H98: Evaluators Comments
Note on I98: Evaluators Comments
Note on J98: Evaluators Comments
Note on E99: Evaluators Comments
Note on F99: Evaluators Comments
Note on G99: Evaluators Comments
Note on H99: Evaluators Comments
Note on I99: Evaluators Comments
Note on J99: Evaluators Comments
Note on E100: Evaluators Comments
Note on F100: Evaluators Comments
Note on G100: Evaluators Comments
Note on H100: Evaluators Comments
Note on I100: Evaluators Comments
Note on J100: Evaluators Comments
Note on E101: Evaluators Comments
Note on F101: Evaluators Comments
Note on G101: Evaluators Comments
Note on H101: Evaluators Comments
Note on I101: Evaluators Comments
Note on J101: Evaluators Comments
Note on E102: Evaluators Comments
Note on F102: Evaluators Comments
Note on G102: Evaluators Comments
Note on H102: Evaluators Comments
Note on I102: Evaluators Comments
Note on J102: Evaluators Comments
Note on E103: Evaluators Comments
Note on F103: Evaluators Comments
Note on G103: Evaluators Comments
Note on H103: Evaluators Comments
Note on I103: Evaluators Comments
Note on J103: Evaluators Comments
Note on E104: Evaluators Comments
Note on F104: Evaluators Comments
Note on G104: Evaluators Comments
Note on H104: Evaluators Comments
Note on I104: Evaluators Comments
Note on J104: Evaluators Comments
Note on E105: Evaluators Comments
Note on F105: Evaluators Comments
Note on G105: Evaluators Comments
Note on H105: Evaluators Comments
Note on I105: Evaluators Comments
Note on J105: Evaluators Comments
Note on E106: Evaluators Comments
Note on F106: Evaluators Comments
Note on G106: Evaluators Comments
Note on H106: Evaluators Comments
Note on I106: Evaluators Comments
Note on J106: Evaluators Comments
Note on E107: Evaluators Comments
Note on F107: Evaluators Comments
Note on G107: Evaluators Comments
Note on H107: Evaluators Comments
Note on I107: Evaluators Comments
Note on J107: Evaluators Comments
Note on E108: Evaluators Comments
Note on F108: Evaluators Comments
Note on G108: Evaluators Comments
Note on H108: Evaluators Comments
Note on I108: Evaluators Comments
Note on J108: Evaluators Comments
Note on E109: Evaluators Comments
Note on F109: Evaluators Comments
Note on G109: Evaluators Comments
Note on H109: Evaluators Comments
Note on I109: Evaluators Comments
Note on J109: Evaluators Comments
Note on E110: Evaluators Comments
Note on F110: Evaluators Comments
Note on G110: Evaluators Comments
Note on H110: Evaluators Comments
Note on I110: Evaluators Comments
Note on J110: Evaluators Comments
Note on E111: Evaluators Comments
Note on F111: Evaluators Comments
Note on G111: Evaluators Comments
Note on H111: Evaluators Comments
Note on I111: Evaluators Comments
Note on J111: Evaluators Comments
Note on E112: Evaluators Comments
Note on F112: Evaluators Comments
Note on G112: Evaluators Comments
Note on H112: Evaluators Comments
Note on I112: Evaluators Comments
Note on J112: Evaluators Comments
Note on E113: Evaluators Comments
Note on F113: Evaluators Comments
Note on G113: Evaluators Comments
Note on H113: Evaluators Comments
Note on I113: Evaluators Comments
Note on J113: Evaluators Comments
Note on E114: Evaluators Comments
Note on F114: Evaluators Comments
Note on G114: Evaluators Comments
Note on H114: Evaluators Comments
Note on I114: Evaluators Comments
Note on J114: Evaluators Comments
Note on E115: Evaluators Comments
Note on F115: Evaluators Comments
Note on G115: Evaluators Comments
Note on H115: Evaluators Comments
Note on I115: Evaluators Comments
Note on J115: Evaluators Comments
Note on E116: Evaluators Comments
Note on F116: Evaluators Comments
Note on G116: Evaluators Comments
Note on H116: Evaluators Comments
Note on I116: Evaluators Comments
Note on J116: Evaluators Comments
Note on E117: Evaluators Comments
Note on F117: Evaluators Comments
Note on G117: Evaluators Comments
Note on H117: Evaluators Comments
Note on I117: Evaluators Comments
Note on J117: Evaluators Comments
Note on E118: Evaluators Comments
Note on F118: Evaluators Comments
Note on G118: Evaluators Comments
Note on H118: Evaluators Comments
Note on I118: Evaluators Comments
Note on J118: Evaluators Comments
Note on E119: Evaluators Comments
Note on F119: Evaluators Comments
Note on G119: Evaluators Comments
Note on H119: Evaluators Comments
Note on I119: Evaluators Comments
Note on J119: Evaluators Comments
Note on E120: Evaluators Comments
Note on F120: Evaluators Comments
Note on G120: Evaluators Comments
Note on H120: Evaluators Comments
Note on I120: Evaluators Comments
Note on J120: Evaluators Comments
Note on E121: Evaluators Comments
Note on F121: Evaluators Comments
Note on G121: Evaluators Comments
Note on H121: Evaluators Comments
Note on I121: Evaluators Comments
Note on J121: Evaluators Comments
Note on E122: Evaluators Comments
Note on F122: Evaluators Comments
Note on G122: Evaluators Comments
Note on H122: Evaluators Comments
Note on I122: Evaluators Comments
Note on J122: Evaluators Comments
Note on E123: Evaluators Comments
Note on F123: Evaluators Comments
Note on G123: Evaluators Comments
Note on H123: Evaluators Comments
Note on I123: Evaluators Comments
Note on J123: Evaluators Comments
Note on E124: Evaluators Comments
Note on F124: Evaluators Comments
Note on G124: Evaluators Comments
Note on H124: Evaluators Comments
Note on I124: Evaluators Comments
Note on J124: Evaluators Comments
Note on E125: Evaluators Comments
Note on F125: Evaluators Comments
Note on G125: Evaluators Comments
Note on H125: Evaluators Comments
Note on I125: Evaluators Comments
Note on J125: Evaluators Comments
Note on E126: Evaluators Comments
Note on F126: Evaluators Comments
Note on G126: Evaluators Comments
Note on H126: Evaluators Comments
Note on I126: Evaluators Comments
Note on J126: Evaluators Comments
Note on E127: Evaluators Comments
Note on F127: Evaluators Comments
Note on G127: Evaluators Comments
Note on H127: Evaluators Comments
Note on I127: Evaluators Comments
Note on J127: Evaluators Comments
Note on E128: Evaluators Comments
Note on F128: Evaluators Comments
Note on G128: Evaluators Comments
Note on H128: Evaluators Comments
Note on I128: Evaluators Comments
Note on J128: Evaluators Comments
Note on E129: Evaluators Comments
Note on F129: Evaluators Comments
Note on G129: Evaluators Comments
Note on H129: Evaluators Comments
Note on I129: Evaluators Comments
Note on J129: Evaluators Comments
Note on E130: Evaluators Comments
Note on F130: Evaluators Comments
Note on G130: Evaluators Comments
Note on H130: Evaluators Comments
Note on I130: Evaluators Comments
Note on J130: Evaluators Comments
Note on E131: Evaluators Comments
Note on F131: Evaluators Comments
Note on G131: Evaluators Comments
Note on H131: Evaluators Comments
Note on I131: Evaluators Comments
Note on J131: Evaluators Comments
Note on E132: Evaluators Comments
Note on F132: Evaluators Comments
Note on G132: Evaluators Comments
Note on H132: Evaluators Comments
Note on I132: Evaluators Comments
Note on J132: Evaluators Comments
Note on E133: Evaluators Comments
Note on F133: Evaluators Comments
Note on G133: Evaluators Comments
Note on H133: Evaluators Comments
Note on I133: Evaluators Comments
Note on J133: Evaluators Comments
Note on E134: Evaluators Comments
Note on F134: Evaluators Comments
Note on G134: Evaluators Comments
Note on H134: Evaluators Comments
Note on I134: Evaluators Comments
Note on J134: Evaluators Comments
Note on E135: Evaluators Comments
Note on F135: Evaluators Comments
Note on G135: Evaluators Comments
Note on H135: Evaluators Comments
Note on I135: Evaluators Comments
Note on J135: Evaluators Comments
Note on E136: Evaluators Comments
Note on F136: Evaluators Comments
Note on G136: Evaluators Comments
Note on H136: Evaluators Comments
Note on I136: Evaluators Comments
Note on J136: Evaluators Comments
Note on E137: Evaluators Comments
Note on F137: Evaluators Comments
Note on G137: Evaluators Comments
Note on H137: Evaluators Comments
Note on I137: Evaluators Comments
Note on J137: Evaluators Comments
Note on E138: Evaluators Comments
Note on F138: Evaluators Comments
Note on G138: Evaluators Comments
Note on H138: Evaluators Comments
Note on I138: Evaluators Comments
Note on J138: Evaluators Comments
Note on E139: Evaluators Comments
Note on F139: Evaluators Comments
Note on G139: Evaluators Comments
Note on H139: Evaluators Comments
Note on I139: Evaluators Comments
Note on J139: Evaluators Comments
Note on E140: Evaluators Comments
Note on F140: Evaluators Comments
Note on G140: Evaluators Comments
Note on H140: Evaluators Comments
Note on I140: Evaluators Comments
Note on J140: Evaluators Comments
Note on E141: Evaluators Comments
Note on F141: Evaluators Comments
Note on G141: Evaluators Comments
Note on H141: Evaluators Comments
Note on I141: Evaluators Comments
Note on J141: Evaluators Comments
Note on E142: Evaluators Comments
Note on F142: Evaluators Comments
Note on G142: Evaluators Comments
Note on H142: Evaluators Comments
Note on I142: Evaluators Comments
Note on J142: Evaluators Comments
Note on E143: Evaluators Comments
Note on F143: Evaluators Comments
Note on G143: Evaluators Comments
Note on H143: Evaluators Comments
Note on I143: Evaluators Comments
Note on J143: Evaluators Comments
Note on E144: Evaluators Comments
Note on F144: Evaluators Comments
Note on G144: Evaluators Comments
Note on H144: Evaluators Comments
Note on I144: Evaluators Comments
Note on J144: Evaluators Comments
Note on E145: Evaluators Comments
Note on F145: Evaluators Comments
Note on G145: Evaluators Comments
Note on H145: Evaluators Comments
Note on I145: Evaluators Comments
Note on J145: Evaluators Comments
Note on E146: Evaluators Comments
Note on F146: Evaluators Comments
Note on G146: Evaluators Comments
Note on H146: Evaluators Comments
Note on I146: Evaluators Comments
Note on J146: Evaluators Comments
Note on E147: Evaluators Comments
Note on F147: Evaluators Comments
Note on G147: Evaluators Comments
Note on H147: Evaluators Comments
Note on I147: Evaluators Comments
Note on J147: Evaluators Comments
Note on E148: Evaluators Comments
Note on F148: Evaluators Comments
Note on G148: Evaluators Comments
Note on H148: Evaluators Comments
Note on I148: Evaluators Comments
Note on J148: Evaluators Comments
Note on E149: Evaluators Comments
Note on F149: Evaluators Comments
Note on G149: Evaluators Comments
Note on H149: Evaluators Comments
Note on I149: Evaluators Comments
Note on J149: Evaluators Comments
Note on E150: Evaluators Comments
Note on F150: Evaluators Comments
Note on G150: Evaluators Comments
Note on H150: Evaluators Comments
Note on I150: Evaluators Comments
Note on J150: Evaluators Comments
Note on E151: Evaluators Comments
Note on F151: Evaluators Comments
Note on G151: Evaluators Comments
Note on H151: Evaluators Comments
Note on I151: Evaluators Comments
Note on J151: Evaluators Comments
Note on E152: Evaluators Comments
Note on F152: Evaluators Comments
Note on G152: Evaluators Comments
Note on H152: Evaluators Comments
Note on I152: Evaluators Comments
Note on J152: Evaluators Comments
Note on E153: Evaluators Comments
Note on F153: Evaluators Comments
Note on G153: Evaluators Comments
Note on H153: Evaluators Comments
Note on I153: Evaluators Comments
Note on J153: Evaluators Comments
Note on E154: Evaluators Comments
Note on F154: Evaluators Comments
Note on G154: Evaluators Comments
Note on H154: Evaluators Comments
Note on I154: Evaluators Comments
Note on J154: Evaluators Comments
Note on E155: Evaluators Comments
Note on F155: Evaluators Comments
Note on G155: Evaluators Comments
Note on H155: Evaluators Comments
Note on I155: Evaluators Comments
Note on J155: Evaluators Comments
Note on E156: Evaluators Comments
Note on F156: Evaluators Comments
Note on G156: Evaluators Comments
Note on H156: Evaluators Comments
Note on I156: Evaluators Comments
Note on J156: Evaluators Comments
Note on E157: Evaluators Comments
Note on F157: Evaluators Comments
Note on G157: Evaluators Comments
Note on H157: Evaluators Comments
Note on I157: Evaluators Comments
Note on J157: Evaluators Comments
Note on E158: Evaluators Comments
Note on F158: Evaluators Comments
Note on G158: Evaluators Comments
Note on H158: Evaluators Comments
Note on I158: Evaluators Comments
Note on J158: Evaluators Comments
Note on E159: Evaluators Comments
Note on F159: Evaluators Comments
Note on G159: Evaluators Comments
Note on H159: Evaluators Comments
Note on I159: Evaluators Comments
Note on J159: Evaluators Comments
Note on E160: Evaluators Comments
Note on F160: Evaluators Comments
Note on G160: Evaluators Comments
Note on H160: Evaluators Comments
Note on I160: Evaluators Comments
Note on J160: Evaluators Comments
Note on E161: Evaluators Comments
Note on F161: Evaluators Comments
Note on G161: Evaluators Comments
Note on H161: Evaluators Comments
Note on I161: Evaluators Comments
Note on J161: Evaluators Comments
Note on E162: Evaluators Comments
Note on F162: Evaluators Comments
Note on G162: Evaluators Comments
Note on H162: Evaluators Comments
Note on I162: Evaluators Comments
Note on J162: Evaluators Comments
Note on E163: Evaluators Comments
Note on F163: Evaluators Comments
Note on G163: Evaluators Comments
Note on H163: Evaluators Comments
Note on I163: Evaluators Comments
Note on J163: Evaluators Comments
Note on E164: Evaluators Comments
Note on F164: Evaluators Comments
Note on G164: Evaluators Comments
Note on H164: Evaluators Comments
Note on I164: Evaluators Comments
Note on J164: Evaluators Comments
Note on E165: Evaluators Comments
Note on F165: Evaluators Comments
Note on G165: Evaluators Comments
Note on H165: Evaluators Comments
Note on I165: Evaluators Comments
Note on J165: Evaluators Comments
Note on E166: Evaluators Comments
Note on F166: Evaluators Comments
Note on G166: Evaluators Comments
Note on H166: Evaluators Comments
Note on I166: Evaluators Comments
Note on J166: Evaluators Comments
Note on E167: Evaluators Comments
Note on F167: Evaluators Comments
Note on G167: Evaluators Comments
Note on H167: Evaluators Comments
Note on I167: Evaluators Comments
Note on J167: Evaluators Comments
Note on E168: Evaluators Comments
Note on F168: Evaluators Comments
Note on G168: Evaluators Comments
Note on H168: Evaluators Comments
Note on I168: Evaluators Comments
Note on J168: Evaluators Comments
Note on E169: Evaluators Comments
Note on F169: Evaluators Comments
Note on G169: Evaluators Comments
Note on H169: Evaluators Comments
Note on I169: Evaluators Comments
Note on J169: Evaluators Comments
Note on E170: Evaluators Comments
Note on F170: Evaluators Comments
Note on G170: Evaluators Comments
Note on H170: Evaluators Comments
Note on I170: Evaluators Comments
Note on J170: Evaluators Comments
Note on E171: Evaluators Comments
Note on F171: Evaluators Comments
Note on G171: Evaluators Comments
Note on H171: Evaluators Comments
Note on I171: Evaluators Comments
Note on J171: Evaluators Comments
Note on E172: Evaluators Comments
Note on F172: Evaluators Comments
Note on G172: Evaluators Comments
Note on H172: Evaluators Comments
Note on I172: Evaluators Comments
Note on J172: Evaluators Comments
Note on E173: Evaluators Comments
Note on F173: Evaluators Comments
Note on G173: Evaluators Comments
Note on H173: Evaluators Comments
Note on I173: Evaluators Comments
Note on J173: Evaluators Comments
Note on E174: Evaluators Comments
Note on F174: Evaluators Comments
Note on G174: Evaluators Comments
Note on H174: Evaluators Comments
Note on I174: Evaluators Comments
Note on J174: Evaluators Comments
Note on E175: Evaluators Comments
Note on F175: Evaluators Comments
Note on G175: Evaluators Comments
Note on H175: Evaluators Comments
Note on I175: Evaluators Comments
Note on J175: Evaluators Comments
Note on E176: Evaluators Comments
Note on F176: Evaluators Comments
Note on G176: Evaluators Comments
Note on H176: Evaluators Comments
Note on I176: Evaluators Comments
Note on J176: Evaluators Comments
Note on E177: Evaluators Comments
Note on F177: Evaluators Comments
Note on G177: Evaluators Comments
Note on H177: Evaluators Comments
Note on I177: Evaluators Comments
Note on J177: Evaluators Comments
Note on E178: Evaluators Comments
Note on F178: Evaluators Comments
Note on G178: Evaluators Comments
Note on H178: Evaluators Comments
Note on I178: Evaluators Comments
Note on J178: Evaluators Comments
Note on E179: Evaluators Comments
Note on F179: Evaluators Comments
Note on G179: Evaluators Comments
Note on H179: Evaluators Comments
Note on I179: Evaluators Comments
Note on J179: Evaluators Comments
Note on E180: Evaluators Comments
Note on F180: Evaluators Comments
Note on G180: Evaluators Comments
Note on H180: Evaluators Comments
Note on I180: Evaluators Comments
Note on J180: Evaluators Comments
Note on E181: Evaluators Comments
Note on F181: Evaluators Comments
Note on G181: Evaluators Comments
Note on H181: Evaluators Comments
Note on I181: Evaluators Comments
Note on J181: Evaluators Comments
Note on E182: Evaluators Comments
Note on F182: Evaluators Comments
Note on G182: Evaluators Comments
Note on H182: Evaluators Comments
Note on I182: Evaluators Comments
Note on J182: Evaluators Comments
Note on E183: Evaluators Comments
Note on F183: Evaluators Comments
Note on G183: Evaluators Comments
Note on H183: Evaluators Comments
Note on I183: Evaluators Comments
Note on J183: Evaluators Comments
Note on E184: Evaluators Comments
Note on F184: Evaluators Comments
Note on G184: Evaluators Comments
Note on H184: Evaluators Comments
Note on I184: Evaluators Comments
Note on J184: Evaluators Comments
Note on E185: Evaluators Comments
Note on F185: Evaluators Comments
Note on G185: Evaluators Comments
Note on H185: Evaluators Comments
Note on I185: Evaluators Comments
Note on J185: Evaluators Comments
Note on E186: Evaluators Comments
Note on F186: Evaluators Comments
Note on G186: Evaluators Comments
Note on H186: Evaluators Comments
Note on I186: Evaluators Comments
Note on J186: Evaluators Comments
Note on E187: Evaluators Comments
Note on F187: Evaluators Comments
Note on G187: Evaluators Comments
Note on H187: Evaluators Comments
Note on I187: Evaluators Comments
Note on J187: Evaluators Comments
Note on E188: Evaluators Comments
Note on F188: Evaluators Comments
Note on G188: Evaluators Comments
Note on H188: Evaluators Comments
Note on I188: Evaluators Comments
Note on J188: Evaluators Comments
Note on E189: Evaluators Comments
Note on F189: Evaluators Comments
Note on G189: Evaluators Comments
Note on H189: Evaluators Comments
Note on I189: Evaluators Comments
Note on J189: Evaluators Comments
Note on E190: Evaluators Comments
Note on F190: Evaluators Comments
Note on G190: Evaluators Comments
Note on H190: Evaluators Comments
Note on I190: Evaluators Comments
Note on J190: Evaluators Comments
Note on E191: Evaluators Comments
Note on F191: Evaluators Comments
Note on G191: Evaluators Comments
Note on H191: Evaluators Comments
Note on I191: Evaluators Comments
Note on J191: Evaluators Comments
Note on E192: Evaluators Comments
Note on F192: Evaluators Comments
Note on G192: Evaluators Comments
Note on H192: Evaluators Comments
Note on I192: Evaluators Comments
Note on J192: Evaluators Comments
Note on E193: Evaluators Comments
Note on F193: Evaluators Comments
Note on G193: Evaluators Comments
Note on H193: Evaluators Comments
Note on I193: Evaluators Comments
Note on J193: Evaluators Comments
Note on E194: Evaluators Comments
Note on F194: Evaluators Comments
Note on G194: Evaluators Comments
Note on H194: Evaluators Comments
Note on I194: Evaluators Comments
Note on J194: Evaluators Comments
Note on E195: Evaluators Comments
Note on F195: Evaluators Comments
Note on G195: Evaluators Comments
Note on H195: Evaluators Comments
Note on I195: Evaluators Comments
Note on J195: Evaluators Comments
Note on E196: Evaluators Comments
Note on F196: Evaluators Comments
Note on G196: Evaluators Comments
Note on H196: Evaluators Comments
Note on I196: Evaluators Comments
Note on J196: Evaluators Comments
Note on E197: Evaluators Comments
Note on F197: Evaluators Comments
Note on G197: Evaluators Comments
Note on H197: Evaluators Comments
Note on I197: Evaluators Comments
Note on J197: Evaluators Comments
Note on E198: Evaluators Comments
Note on F198: Evaluators Comments
Note on G198: Evaluators Comments
Note on H198: Evaluators Comments
Note on I198: Evaluators Comments
Note on J198: Evaluators Comments
Note on E199: Evaluators Comments
Note on F199: Evaluators Comments
Note on G199: Evaluators Comments
Note on H199: Evaluators Comments
Note on I199: Evaluators Comments
Note on J199: Evaluators Comments
Note on E200: Evaluators Comments
Note on F200: Evaluators Comments
Note on G200: Evaluators Comments
Note on H200: Evaluators Comments
Note on I200: Evaluators Comments
Note on J200: Evaluators Comments
Note on E201: Evaluators Comments
Note on F201: Evaluators Comments
Note on G201: Evaluators Comments
Note on H201: Evaluators Comments
Note on I201: Evaluators Comments
Note on J201: Evaluators Comments
Note on E202: Evaluators Comments
Note on F202: Evaluators Comments
Note on G202: Evaluators Comments
Note on H202: Evaluators Comments
Note on I202: Evaluators Comments
Note on J202: Evaluators Comments
Note on E203: Evaluators Comments
Note on F203: Evaluators Comments
Note on G203: Evaluators Comments
Note on H203: Evaluators Comments
Note on I203: Evaluators Comments
Note on J203: Evaluators Comments
Note on E204: Evaluators Comments
Note on F204: Evaluators Comments
Note on G204: Evaluators Comments
Note on H204: Evaluators Comments
Note on I204: Evaluators Comments
Note on J204: Evaluators Comments
Note on E205: Evaluators Comments
Note on F205: Evaluators Comments
Note on G205: Evaluators Comments
Note on H205: Evaluators Comments
Note on I205: Evaluators Comments
Note on J205: Evaluators Comments
Note on E206: Evaluators Comments
Note on F206: Evaluators Comments
Note on G206: Evaluators Comments
Note on H206: Evaluators Comments
Note on I206: Evaluators Comments
Note on J206: Evaluators Comments
Note on E207: Evaluators Comments
Note on F207: Evaluators Comments
Note on G207: Evaluators Comments
Note on H207: Evaluators Comments
Note on I207: Evaluators Comments
Note on J207: Evaluators Comments
Note on E208: Evaluators Comments
Note on F208: Evaluators Comments
Note on G208: Evaluators Comments
Note on H208: Evaluators Comments
Note on I208: Evaluators Comments
Note on J208: Evaluators Comments
Note on E209: Evaluators Comments
Note on F209: Evaluators Comments
Note on G209: Evaluators Comments
Note on H209: Evaluators Comments
Note on I209: Evaluators Comments
Note on J209: Evaluators Comments
Note on E210: Evaluators Comments
Note on F210: Evaluators Comments
Note on G210: Evaluators Comments
Note on H210: Evaluators Comments
Note on I210: Evaluators Comments
Note on J210: Evaluators Comments
Note on E211: Evaluators Comments
Note on F211: Evaluators Comments
Note on G211: Evaluators Comments
Note on H211: Evaluators Comments
Note on I211: Evaluators Comments
Note on J211: Evaluators Comments
Note on E212: Evaluators Comments
Note on F212: Evaluators Comments
Note on G212: Evaluators Comments
Note on H212: Evaluators Comments
Note on I212: Evaluators Comments
Note on J212: Evaluators Comments
Note on E213: Evaluators Comments
Note on F213: Evaluators Comments
Note on G213: Evaluators Comments
Note on H213: Evaluators Comments
Note on I213: Evaluators Comments
Note on J213: Evaluators Comments
Note on E214: Evaluators Comments
Note on F214: Evaluators Comments
Note on G214: Evaluators Comments
Note on H214: Evaluators Comments
Note on I214: Evaluators Comments
Note on J214: Evaluators Comments
Note on E215: Evaluators Comments
Note on F215: Evaluators Comments
Note on G215: Evaluators Comments
Note on H215: Evaluators Comments
Note on I215: Evaluators Comments
Note on J215: Evaluators Comments
Note on E216: Evaluators Comments
Note on F216: Evaluators Comments
Note on G216: Evaluators Comments
Note on H216: Evaluators Comments
Note on I216: Evaluators Comments
Note on J216: Evaluators Comments
Note on E217: Evaluators Comments
Note on F217: Evaluators Comments
Note on G217: Evaluators Comments
Note on H217: Evaluators Comments
Note on I217: Evaluators Comments
Note on J217: Evaluators Comments
Note on E218: Evaluators Comments
Note on F218: Evaluators Comments
Note on G218: Evaluators Comments
Note on H218: Evaluators Comments
Note on I218: Evaluators Comments
Note on J218: Evaluators Comments
Note on E219: Evaluators Comments
Note on F219: Evaluators Comments
Note on G219: Evaluators Comments
Note on H219: Evaluators Comments
Note on I219: Evaluators Comments
Note on J219: Evaluators Comments
Note on E220: Evaluators Comments
Note on F220: Evaluators Comments
Note on G220: Evaluators Comments
Note on H220: Evaluators Comments
Note on I220: Evaluators Comments
Note on J220: Evaluators Comments
Note on E221: Evaluators Comments
Note on F221: Evaluators Comments
Note on G221: Evaluators Comments
Note on H221: Evaluators Comments
Note on I221: Evaluators Comments
Note on J221: Evaluators Comments
Note on E222: Evaluators Comments
Note on F222: Evaluators Comments
Note on G222: Evaluators Comments
Note on H222: Evaluators Comments
Note on I222: Evaluators Comments
Note on J222: Evaluators Comments
Note on E223: Evaluators Comments
Note on F223: Evaluators Comments
Note on G223: Evaluators Comments
Note on H223: Evaluators Comments
Note on I223: Evaluators Comments
Note on J223: Evaluators Comments
Note on E224: Evaluators Comments
Note on F224: Evaluators Comments
Note on G224: Evaluators Comments
Note on H224: Evaluators Comments
Note on I224: Evaluators Comments
Note on J224: Evaluators Comments
Note on E225: Evaluators Comments
Note on F225: Evaluators Comments
Note on G225: Evaluators Comments
Note on H225: Evaluators Comments
Note on I225: Evaluators Comments
Note on J225: Evaluators Comments
Note on E226: Evaluators Comments
Note on F226: Evaluators Comments
Note on G226: Evaluators Comments
Note on H226: Evaluators Comments
Note on I226: Evaluators Comments
Note on J226: Evaluators Comments
Note on E227: Evaluators Comments
Note on F227: Evaluators Comments
Note on G227: Evaluators Comments
Note on H227: Evaluators Comments
Note on I227: Evaluators Comments
Note on J227: Evaluators Comments
Note on E228: Evaluators Comments
Note on F228: Evaluators Comments
Note on G228: Evaluators Comments
Note on H228: Evaluators Comments
Note on I228: Evaluators Comments
Note on J228: Evaluators Comments
Note on E229: Evaluators Comments
Note on F229: Evaluators Comments
Note on G229: Evaluators Comments
Note on H229: Evaluators Comments
Note on I229: Evaluators Comments
Note on J229: Evaluators Comments
Note on E230: Evaluators Comments
Note on F230: Evaluators Comments
Note on G230: Evaluators Comments
Note on H230: Evaluators Comments
Note on I230: Evaluators Comments
Note on J230: Evaluators Comments
Note on E231: Evaluators Comments
Note on F231: Evaluators Comments
Note on G231: Evaluators Comments
Note on H231: Evaluators Comments
Note on I231: Evaluators Comments
Note on J231: Evaluators Comments
Note on E232: Evaluators Comments
Note on F232: Evaluators Comments
Note on G232: Evaluators Comments
Note on H232: Evaluators Comments
Note on I232: Evaluators Comments
Note on J232: Evaluators Comments
Note on E233: Evaluators Comments
Note on F233: Evaluators Comments
Note on G233: Evaluators Comments
Note on H233: Evaluators Comments
Note on I233: Evaluators Comments
Note on J233: Evaluators Comments
Note on E234: Evaluators Comments
Note on F234: Evaluators Comments
Note on G234: Evaluators Comments
Note on H234: Evaluators Comments
Note on I234: Evaluators Comments
Note on J234: Evaluators Comments
Note on E235: Evaluators Comments
Note on F235: Evaluators Comments
Note on G235: Evaluators Comments
Note on H235: Evaluators Comments
Note on I235: Evaluators Comments
Note on J235: Evaluators Comments
Note on E236: Evaluators Comments
Note on F236: Evaluators Comments
Note on G236: Evaluators Comments
Note on H236: Evaluators Comments
Note on I236: Evaluators Comments
Note on J236: Evaluators Comments
Note on E237: Evaluators Comments
Note on F237: Evaluators Comments
Note on G237: Evaluators Comments
Note on H237: Evaluators Comments
Note on I237: Evaluators Comments
Note on J237: Evaluators Comments
Note on E238: Evaluators Comments
Note on F238: Evaluators Comments
Note on G238: Evaluators Comments
Note on H238: Evaluators Comments
Note on I238: Evaluators Comments
Note on J238: Evaluators Comments
Note on E239: Evaluators Comments
Note on F239: Evaluators Comments
Note on G239: Evaluators Comments
Note on H239: Evaluators Comments
Note on I239: Evaluators Comments
Note on J239: Evaluators Comments
Note on E240: Evaluators Comments
Note on F240: Evaluators Comments
Note on G240: Evaluators Comments
Note on H240: Evaluators Comments
Note on I240: Evaluators Comments
Note on J240: Evaluators Comments
Note on E241: Evaluators Comments
Note on F241: Evaluators Comments
Note on G241: Evaluators Comments
Note on H241: Evaluators Comments
Note on I241: Evaluators Comments
Note on J241: Evaluators Comments
Note on E242: Evaluators Comments
Note on F242: Evaluators Comments
Note on G242: Evaluators Comments
Note on H242: Evaluators Comments
Note on I242: Evaluators Comments
Note on J242: Evaluators Comments
Note on E243: Evaluators Comments
Note on F243: Evaluators Comments
Note on G243: Evaluators Comments
Note on H243: Evaluators Comments
Note on I243: Evaluators Comments
Note on J243: Evaluators Comments
Note on E244: Evaluators Comments
Note on F244: Evaluators Comments
Note on G244: Evaluators Comments
Note on H244: Evaluators Comments
Note on I244: Evaluators Comments
Note on J244: Evaluators Comments
Note on E245: Evaluators Comments
Note on F245: Evaluators Comments
Note on G245: Evaluators Comments
Note on H245: Evaluators Comments
Note on I245: Evaluators Comments
Note on J245: Evaluators Comments
Note on E246: Evaluators Comments
Note on F246: Evaluators Comments
Note on G246: Evaluators Comments
Note on H246: Evaluators Comments
Note on I246: Evaluators Comments
Note on J246: Evaluators Comments
Note on E247: Evaluators Comments
Note on F247: Evaluators Comments
Note on G247: Evaluators Comments
Note on H247: Evaluators Comments
Note on I247: Evaluators Comments
Note on J247: Evaluators Comments
Note on E248: Evaluators Comments
Note on F248: Evaluators Comments
Note on G248: Evaluators Comments
Note on H248: Evaluators Comments
Note on I248: Evaluators Comments
Note on J248: Evaluators Comments
Note on E249: Evaluators Comments
Note on F249: Evaluators Comments
Note on G249: Evaluators Comments
Note on H249: Evaluators Comments
Note on I249: Evaluators Comments
Note on J249: Evaluators Comments
Note on E250: Evaluators Comments
Note on F250: Evaluators Comments
Note on G250: Evaluators Comments
Note on H250: Evaluators Comments
Note on I250: Evaluators Comments
Note on J250: Evaluators Comments
Note on E251: Evaluators Comments
Note on F251: Evaluators Comments
Note on G251: Evaluators Comments
Note on H251: Evaluators Comments
Note on I251: Evaluators Comments
Note on J251: Evaluators Comments
Note on E252: Evaluators Comments
Note on F252: Evaluators Comments
Note on G252: Evaluators Comments
Note on H252: Evaluators Comments
Note on I252: Evaluators Comments
Note on J252: Evaluators Comments
Note on E253: Evaluators Comments
Note on F253: Evaluators Comments
Note on G253: Evaluators Comments
Note on H253: Evaluators Comments
Note on I253: Evaluators Comments
Note on J253: Evaluators Comments
Note on E254: Evaluators Comments
Note on F254: Evaluators Comments
Note on G254: Evaluators Comments
Note on H254: Evaluators Comments
Note on I254: Evaluators Comments
Note on J254: Evaluators Comments
Note on E255: Evaluators Comments
Note on F255: Evaluators Comments
Note on G255: Evaluators Comments
Note on H255: Evaluators Comments
Note on I255: Evaluators Comments
Note on J255: Evaluators Comments
Note on E256: Evaluators Comments
Note on F256: Evaluators Comments
Note on G256: Evaluators Comments
Note on H256: Evaluators Comments
Note on I256: Evaluators Comments
Note on J256: Evaluators Comments
Note on E257: Evaluators Comments
Note on F257: Evaluators Comments
Note on G257: Evaluators Comments
Note on H257: Evaluators Comments
Note on I257: Evaluators Comments
Note on J257: Evaluators Comments
Note on E258: Evaluators Comments
Note on F258: Evaluators Comments
Note on G258: Evaluators Comments
Note on H258: Evaluators Comments
Note on I258: Evaluators Comments
Note on J258: Evaluators Comments
Note on E259: Evaluators Comments
Note on F259: Evaluators Comments
Note on G259: Evaluators Comments
Note on H259: Evaluators Comments
Note on I259: Evaluators Comments
Note on J259: Evaluators Comments
Note on E260: Evaluators Comments
Note on F260: Evaluators Comments
Note on G260: Evaluators Comments
Note on H260: Evaluators Comments
Note on I260: Evaluators Comments
Note on J260: Evaluators Comments
Note on E261: Evaluators Comments
Note on F261: Evaluators Comments
Note on G261: Evaluators Comments
Note on H261: Evaluators Comments
Note on I261: Evaluators Comments
Note on J261: Evaluators Comments
Note on E262: Evaluators Comments
Note on F262: Evaluators Comments
Note on G262: Evaluators Comments
Note on H262: Evaluators Comments
Note on I262: Evaluators Comments
Note on J262: Evaluators Comments
Note on E263: Evaluators Comments
Note on F263: Evaluators Comments
Note on G263: Evaluators Comments
Note on H263: Evaluators Comments
Note on I263: Evaluators Comments
Note on J263: Evaluators Comments
Note on E264: Evaluators Comments
Note on F264: Evaluators Comments
Note on G264: Evaluators Comments
Note on H264: Evaluators Comments
Note on I264: Evaluators Comments
Note on J264: Evaluators Comments
Note on E265: Evaluators Comments
Note on F265: Evaluators Comments
Note on G265: Evaluators Comments
Note on H265: Evaluators Comments
Note on I265: Evaluators Comments
Note on J265: Evaluators Comments
Note on E266: Evaluators Comments
Note on F266: Evaluators Comments
Note on G266: Evaluators Comments
Note on H266: Evaluators Comments
Note on I266: Evaluators Comments
Note on J266: Evaluators Comments
Note on E267: Evaluators Comments
Note on F267: Evaluators Comments
Note on G267: Evaluators Comments
Note on H267: Evaluators Comments
Note on I267: Evaluators Comments
Note on J267: Evaluators Comments
Note on E268: Evaluators Comments
Note on F268: Evaluators Comments
Note on G268: Evaluators Comments
Note on H268: Evaluators Comments
Note on I268: Evaluators Comments
Note on J268: Evaluators Comments
Note on E269: Evaluators Comments
Note on F269: Evaluators Comments
Note on G269: Evaluators Comments
Note on H269: Evaluators Comments
Note on I269: Evaluators Comments
Note on J269: Evaluators Comments
Note on E270: Evaluators Comments
Note on F270: Evaluators Comments
Note on G270: Evaluators Comments
Note on H270: Evaluators Comments
Note on I270: Evaluators Comments
Note on J270: Evaluators Comments
Note on E271: Evaluators Comments
Note on F271: Evaluators Comments
Note on G271: Evaluators Comments
Note on H271: Evaluators Comments
Note on I271: Evaluators Comments
Note on J271: Evaluators Comments
Note on E272: Evaluators Comments
Note on F272: Evaluators Comments
Note on G272: Evaluators Comments
Note on H272: Evaluators Comments
Note on I272: Evaluators Comments
Note on J272: Evaluators Comments
Note on E273: Evaluators Comments
Note on F273: Evaluators Comments
Note on G273: Evaluators Comments
Note on H273: Evaluators Comments
Note on I273: Evaluators Comments
Note on J273: Evaluators Comments
Note on E274: Evaluators Comments
Note on F274: Evaluators Comments
Note on G274: Evaluators Comments
Note on H274: Evaluators Comments
Note on I274: Evaluators Comments
Note on J274: Evaluators Comments
Note on E275: Evaluators Comments
Note on F275: Evaluators Comments
Note on G275: Evaluators Comments
Note on H275: Evaluators Comments
Note on I275: Evaluators Comments
Note on J275: Evaluators Comments
Note on E276: Evaluators Comments
Note on F276: Evaluators Comments
Note on G276: Evaluators Comments
Note on H276: Evaluators Comments
Note on I276: Evaluators Comments
Note on J276: Evaluators Comments
Note on E277: Evaluators Comments
Note on F277: Evaluators Comments
Note on G277: Evaluators Comments
Note on H277: Evaluators Comments
Note on I277: Evaluators Comments
Note on J277: Evaluators Comments
Note on E278: Evaluators Comments
Note on F278: Evaluators Comments
Note on G278: Evaluators Comments
Note on H278: Evaluators Comments
Note on I278: Evaluators Comments
Note on J278: Evaluators Comments
Note on E279: Evaluators Comments
Note on F279: Evaluators Comments
Note on G279: Evaluators Comments
Note on H279: Evaluators Comments
Note on I279: Evaluators Comments
Note on J279: Evaluators Comments
Note on E280: Evaluators Comments
Note on F280: Evaluators Comments
Note on G280: Evaluators Comments
Note on H280: Evaluators Comments
Note on I280: Evaluators Comments
Note on J280: Evaluators Comments
Note on E281: Evaluators Comments
Note on F281: Evaluators Comments
Note on G281: Evaluators Comments
Note on H281: Evaluators Comments
Note on I281: Evaluators Comments
Note on J281: Evaluators Comments
Note on E282: Evaluators Comments
Note on F282: Evaluators Comments
Note on G282: Evaluators Comments
Note on H282: Evaluators Comments
Note on I282: Evaluators Comments
Note on J282: Evaluators Comments
Note on E283: Evaluators Comments
Note on F283: Evaluators Comments
Note on G283: Evaluators Comments
Note on H283: Evaluators Comments
Note on I283: Evaluators Comments
Note on J283: Evaluators Comments
Note on E284: Evaluators Comments
Note on F284: Evaluators Comments
Note on G284: Evaluators Comments
Note on H284: Evaluators Comments
Note on I284: Evaluators Comments
Note on J284: Evaluators Comments
Note on E285: Evaluators Comments
Note on F285: Evaluators Comments
Note on G285: Evaluators Comments
Note on H285: Evaluators Comments
Note on I285: Evaluators Comments
Note on J285: Evaluators Comments
Note on E286: Evaluators Comments
Note on F286: Evaluators Comments
Note on G286: Evaluators Comments
Note on H286: Evaluators Comments
Note on I286: Evaluators Comments
Note on J286: Evaluators Comments
Note on E287: Evaluators Comments
Note on F287: Evaluators Comments
Note on G287: Evaluators Comments
Note on H287: Evaluators Comments
Note on I287: Evaluators Comments
Note on J287: Evaluators Comments
Note on E288: Evaluators Comments
Note on F288: Evaluators Comments
Note on G288: Evaluators Comments
Note on H288: Evaluators Comments
Note on I288: Evaluators Comments
Note on J288: Evaluators Comments
Note on E289: Evaluators Comments
Note on F289: Evaluators Comments
Note on G289: Evaluators Comments
Note on H289: Evaluators Comments
Note on I289: Evaluators Comments
Note on J289: Evaluators Comments
Note on E290: Evaluators Comments
Note on F290: Evaluators Comments
Note on G290: Evaluators Comments
Note on H290: Evaluators Comments
Note on I290: Evaluators Comments
Note on J290: Evaluators Comments
Note on E291: Evaluators Comments
Note on F291: Evaluators Comments
Note on G291: Evaluators Comments
Note on H291: Evaluators Comments
Note on I291: Evaluators Comments
Note on J291: Evaluators Comments
Note on E292: Evaluators Comments
Note on F292: Evaluators Comments
Note on G292: Evaluators Comments
Note on H292: Evaluators Comments
Note on I292: Evaluators Comments
Note on J292: Evaluators Comments
Note on E293: Evaluators Comments
Note on F293: Evaluators Comments
Note on G293: Evaluators Comments
Note on H293: Evaluators Comments
Note on I293: Evaluators Comments
Note on J293: Evaluators Comments
Note on E294: Evaluators Comments
Note on F294: Evaluators Comments
Note on G294: Evaluators Comments
Note on H294: Evaluators Comments
Note on I294: Evaluators Comments
Note on J294: Evaluators Comments
Note on E295: Evaluators Comments
Note on F295: Evaluators Comments
Note on G295: Evaluators Comments
Note on H295: Evaluators Comments
Note on I295: Evaluators Comments
Note on J295: Evaluators Comments
Note on E296: Evaluators Comments
Note on F296: Evaluators Comments
Note on G296: Evaluators Comments
Note on H296: Evaluators Comments
Note on I296: Evaluators Comments
Note on J296: Evaluators Comments
Note on E297: Evaluators Comments
Note on F297: Evaluators Comments
Note on G297: Evaluators Comments
Note on H297: Evaluators Comments
Note on I297: Evaluators Comments
Note on J297: Evaluators Comments
Note on E298: Evaluators Comments
Note on F298: Evaluators Comments
Note on G298: Evaluators Comments
Note on H298: Evaluators Comments
Note on I298: Evaluators Comments
Note on J298: Evaluators Comments
Note on E299: Evaluators Comments
Note on F299: Evaluators Comments
Note on G299: Evaluators Comments
Note on H299: Evaluators Comments
Note on I299: Evaluators Comments
Note on J299: Evaluators Comments
Note on E300: Evaluators Comments
Note on F300: Evaluators Comments
Note on G300: Evaluators Comments
Note on H300: Evaluators Comments
Note on I300: Evaluators Comments
Note on J300: Evaluators Comments
Note on E301: Evaluators Comments
Note on F301: Evaluators Comments
Note on G301: Evaluators Comments
Note on H301: Evaluators Comments
Note on I301: Evaluators Comments
Note on J301: Evaluators Comments
Note on E302: Evaluators Comments
Note on F302: Evaluators Comments
Note on G302: Evaluators Comments
Note on H302: Evaluators Comments
Note on I302: Evaluators Comments
Note on J302: Evaluators Comments
Note on E303: Evaluators Comments
Note on F303: Evaluators Comments
Note on G303: Evaluators Comments
Note on H303: Evaluators Comments
Note on I303: Evaluators Comments
Note on J303: Evaluators Comments
Note on E304: Evaluators Comments
Note on F304: Evaluators Comments
Note on G304: Evaluators Comments
Note on H304: Evaluators Comments
Note on I304: Evaluators Comments
Note on J304: Evaluators Comments
Note on E305: Evaluators Comments
Note on F305: Evaluators Comments
Note on G305: Evaluators Comments
Note on H305: Evaluators Comments
Note on I305: Evaluators Comments
Note on J305: Evaluators Comments
Note on E306: Evaluators Comments
Note on F306: Evaluators Comments
Note on G306: Evaluators Comments
Note on H306: Evaluators Comments
Note on I306: Evaluators Comments
Note on J306: Evaluators Comments
Note on E307: Evaluators Comments
Note on F307: Evaluators Comments
Note on G307: Evaluators Comments
Note on H307: Evaluators Comments
Note on I307: Evaluators Comments
Note on J307: Evaluators Comments