## General Requirements
| RFT Compliance Matrix |  |  |  | Reference Number | SF-CF-25
[5 empty] | Owner | PRO
[5 empty] | Revision Code | 3.0
[5 empty] | Implementation Date | 2024-03-01
Project Name:
Reference Number:
RFT Article (Part Number or Title) | Requirements (Description) | Killer | Fully Compliant | Partially Compliant | Non-Compliant | Reference (Specify document & page nb)
Article 4 | Conditions for the Participation of the Eligible Bidders
4.1 | 1- Bidders shall meet the following conditions, declared in accordance with the required documents in the First section of this Article mentioned below as (First: Envelope No. (1) Administrative Documents and Transactions):
a- That there is no proven violation, by the bidders, of professional ethics generally accepted and stipulated in the relevant provisions, if any;
b- Bidders have the legal capacity to enter into the procurement contract;
c- Bidders have fulfilled their obligations to pay taxes and social security contributions;
d- Bidders have not been convicted, neither their directors nor employees involved with the procurement process, by a court decision of any criminal offence - even if the verdict can still be appealed - related to their professional conduct or the making of false statements or misrepresentations as to their qualifications to enter into a procurement contract, or corrupting a public procurement or a contract awarding process, or have not been otherwise disqualified pursuant to administrative suspension or debarment proceedings, or have been in a situation of exclusion from participation in public procurements;
e- Bidders are not the subject of legal proceedings for insolvency or bankruptcy, or were declared bankrupt by a court of law;
f- Bidders have not been convicted by a court decision - even if the verdict can still be appealed - of usury or money laundering;
g- Bidders have not participated in the decision-making process of the contracting authority or have any conflict of interest, or any material interest linking them to any of the decision makers;
h- Any other conditions set forth by the contracting authority in the tender documents that are commensurate with the required works;
i- Certificate from the Ministry of Economy proving compliance with the provisions of the Law on Boycott of Israel for foreign companies (added by Law No. 309, dated April 19, 2023).
j- Declaration of the economic beneficiaries (according to Law No. 309, dated April 19, 2023).
4.2 | 2- The bid must be submitted clearly and unequivocally without any deletion, alteration, or modification.
4.3 | 3- The bidders state in their offer that they have reviewed the Tender document and its complementary documents and have obtained a copy. They accept and undertake to adhere to all the conditions outlined therein without any reservations or exceptions. The bidder submits their offer on this basis and affixes financial stamps worth fifty thousand Lebanese pounds covering all the documents.
4.4 | 4- Any bid containing reservations or exceptions is rejected.
4.5 | 5- The bidder mentions in their offer a clear address and place of residence for prompt communication.
Administrative Documents and Transactions | First: Envelope No. (1) Administrative Documents and Transactions
A- General Conditions:
1- Undertaking Letter (Declaration), according to the attached form, signed and stamped by the bidder, this Undertaking includes the bidder's confirmation of their commitment to the price and the validity of the offer. A financial stamp of 50,000 L.L. is affixed.
2- Commercial Circular specifying the authorized signatory of the bidder and a sample of their signature.
3- Legal Authorization: If the offer is signed by someone other than the person authorized to sign according to the commercial circular, it must be notarized by a notary public.
4- Police Record of the Authorized Signatory or his “legal representative”, not exceeding three months from the bid opening date.
5- Partnership Contract legalized by a notary public if required.
6- Registration Certificate before the Directorate of Value Added Tax, if applicable, or a certificate of non-registration if not subject to it. In the latter case, the bidder commits to their bid price even if they become registered for VAT during the execution period.
7- Registration Certificate issued by the Ministry of Finance – Department of Revenue.
8- Certificate issued by the Ministry of Finance proving the bidder's compliance with tax obligations.
9- Clearance Certificate from the National Social Security Fund “comprehensive or valid for participation in public tenders and bids” valid on the date of the bid opening session, stating that the bidder has paid all his subscriptions (the bidder must be registered before the National Social Security Fund and any statement mentioning the phrase “unregistered institution” will be rejected).
10- Certificate issued by the Municipality, proving full payment of municipal fees by the bidder, issued by the municipality within its jurisdiction based on the commercial registration certificate.
11- Comprehensive Certificate issued by the Commercial Register showing founders, members, contributors, or partners, authorized signatories, the manager, capital, the bidder's activity, and ongoing liabilities.
12- Certificate issued by the relevant authorities proving that the bidder is not in a state of bankruptcy.
13- Certificate issued by the relevant authorities proving that the bidder is not in a state of judicial liquidation.
14- Bid bond as required in the specific Tender document of the procurement project, in accordance with Articles 34 and 36 of the Public Procurement Law.
15- Declaration from the Bidder identifying the economic beneficiary/beneficiaries according to Form M18 issued by the Ministry of Finance (any natural person who owns or effectively controls the ultimate outcome of the activity practiced by the bidder, either directly or indirectly, whether the bidder is a natural person or a legal entity.)
16- Copies of Identification Cards (ID/Passport) for the economic beneficiary/beneficiaries.
17- Copies of Identification Cards (ID/Passport) for each person representing the bidder (those acting on behalf of the bidder in their relationship with the contracting authority: legal representative, representative of the legal entity, or authorized signatory).
18- Integrity Declaration Document signed by the bidder in accordance with the prescribed format
Miscellaneous | The bidder shall declare any relative relations with any Alfa employee up to the 4th degree under Clause 30 of the PPL, for MIC1 to be able to assess the existing of any potential conflict of interests which may lead to deprive the bidder from participating to the tender under the risk of disqualification.
The bidder or any of his employees, partners, agents, contributors, consultants, or their relatives shall declare any relationships that may lead to a conflict of interest in the subject of this contract.
Special Conditions | B- Special Conditions Regarding the Subject of the Contract:
Financial Qualifications | 1- Financial Qualifications (To be determined based on the size and nature of the contract).
Technical/Professional Qualifications | 2- Technical/Professional Qualifications (To be determined based on the nature of the contract):
1- Certificate from the Chamber of Commerce, Industry, and Agriculture confirming that the bidder is engaged in the activities related to the subject of the contract, valid as of the date of the bidding session and valid for participation in public tenders.
2- Clearance certificate from the Order of Engineers…
3- Clearance certificate from the Contractors Syndicate…
4- ISO certificate.
5- Five Certificates of good execution and completion for similar projects in terms of size and type.
6- Technical proposal according to the required specifications in the appendix (1) of the RFT.
7- Declaration of site inspection by the bidder, denying any unfamiliarity, according to the attached model.
Participation of a foreign bidder | C- In case of the participation of a foreign bidder, the bidder must comply with one of the following conditions:
1- is part of a coalition that includes at least one Lebanese company that meets the conditions required by the specific Tender document of the procurement project.
2- The personal presence of the legal representative of the company to participate in the procurement proceedings (not mandatory).
3- Has an authorized agent or representative in Lebanon responsible for signing the contract on its behalf.
In addition to the above conditions, the foreign bidder must submit the following:
1- Certificate registration of the company or certificate of establishment issued by the relevant authorities in their country.
2- Certificate from the Lebanese Ministry of Economy and Trade confirming compliance with the provisions of the Law on Israel Boycott.
3- The required certificates according to paragraph (First) above, according to the laws of the country where the bidder is located, provided that these certificates are authenticated according to the regulations of the competent authorities.
For certificates issued without an expiration date, the validity date of each certificate is determined according to its nature, not exceeding six months from the date of the bid opening session.
Information Security Specifications | Information Security Specifications Issuing Department to determine whether all or part of this Article is applicable to their specific RFT
The Bidder shall commit to refrain from offering any product / equipment which can cause security threat or information leakage that jeopardizes MIC1 network security. (K)
The Bidder shall accept that MIC1 runs a vulnerability scan on the proposed solution prior to issuing the acceptance and in case any vulnerability is found, the Bidder undertakes to take the necessary actions to remedy such vulnerability within _____________________ days from its notification.
The Bidder shall mention the security standards adopted/followed in designing the proposed solution.
The Bidder should specify if it has acquired the ISO27001 certification or any other equivalent security certification and submit with the Offer a copy of such certificate.
The Bidder shall not hard code passwords in the proposed solution.
The provided application should run without the need of root (unix) and / or admin (win) privileges.
Source code of proposed application should be owned by MIC1.
System shall allow generation of user, operator as well as alarms logs.
Solution and storage shall be sized to host history logs for at least 1 year back.
The Bidder should submit a data flow diagram and schema of the solution architecture.
In case of online payment, the Bidder shall use encryption. (K)
The Bidder shall harden systems servers / storage before being published online, and describe hardening aspects applied on each type.
The Bidder shall describe security checking and audits performed on the designed solution prior to putting it on the market.
The Bidder shall change default errors / messages and configuration.
Application should support role-based access, specific privileges per user (i.e specific access to application modules and reports)
Database should support restricted access per user or groups to data (i.e access per field or per table, …)
Encryption shall be used in all communications / interactions between systems, especially if the communication is through web access. Web based access shall always be used through HTTP+SSL.
Each user shall have only one account / profile to access data.
Least-privileges should always be specified on nodes / applications.
Pseudocode flow chart shall be provided by the Bidders.
The Bidder should commit to improve solution / systems information security weaknesses whenever needed or highlighted by MIC1 information security team.
Health, Safety and Environmental Specifications | To ensure that the proposed products and services bidders are compliant with HSE culture, bidders should state basic HSE specifications and compliance information:
Bidder shall provide the product’s specifications that have an environmental impact (power consumption, gas emissions, etc…)
Bidder shall provide the product specifications that contribute into preserving the environment (made of recycled material, ozone friendly, low volatile organic compounds, etc…)
Bidder shall provide the product’s specifications that contribute towards the health and safety of the users (ergonomic design, safety features, etc)
Bidder shall state the safety measures being followed by personnel performing the work on Alfa’s sites (ISO45001 certification, specific best practices, etc…).
Bidder shall provide the product’s life cycle data if available.

## Technical Requirements
| RFT Compliance Matrix |  |  |  | Reference Number | SF-CF-25
[5 empty] | Owner | PRO
[5 empty] | Revision Code | 3.0
[5 empty] | Implementation Date | 2024-03-01
Project Name: | JDEIDET DATA CENTER
Reference Number: | 26 33 13.00.BT01 - Batteries - Telco - 10.2023
RFT Article (Part Number or Title) | Requirements (Description) | Killer | Fully Compliant | Partially Compliant | Non-Compliant | Reference (Specify document & page nb)
1 GENERAL
1.1 SUMMARY
A. Batteries for core sites
1.2 REFERENCES
A. Compliancy with international standards:
1. IEC 60896-21:2004 - Stationary lead-acid batteries - Valve regulated types – Methods of test
2. IEC 60896-22:2004 - Stationary lead-acid batteries - Valve regulated types – Requirements
3. DIN 43534 – Lead storage batteries; MAINTENANCE-FREE, SEALED, IMMOBILIZED ELECTROLYTE; RATED CAPACITIES, VOLTAGES, MAIN DIMENSIONS, CONSTRUCTION-DETAILS, REQUIREMENTS
4. DIN 43539 Part 5 - Proof against deep discharge
5. UL 94-V0 – Standard for Tests for Flammability of Plastic Materials for Parts in Devices and Appliances
6. EUROBAT guide 1999 – Classified as “long life”
7. Manufactured in ISO 9001:2000 and ISO 14001:2004 certified production facilities
B. Laboratory approvals
1. The bidder should submit a test report certificate from one of the below laboratories:
a. Underwriters Laboratory (UL)
b. Germanisher Lloyd (GL)
c. Deutche Bahn
d. TUV
e. SGS
1.3 SUBMITTALS
A. Manuals
1. Two (2) complete set of documentations shall be provided by the supplier. Documents should include:
a. Technical specifications
b. Installation guide
c. Maintenance procedure
d. Manufacturer recommendations
e. Warranty Certificate
2. The supplier shall supply a completed Battery Discharge Table for all offered batteries.
1.4 WARRANTY
A. Equipment
1. The supplied products shall be covered by full supplier warranty for a minimum period of one (1) year from delivery to site at a full repair and replacement service.
2. Warranty shall include all defected spare parts and workmanship.
B. Services
1. Installation and dismantling
a. The supplier is responsible for the dismantling, hoisting, transportation and re-installation for parts that cannot be repaired or replaced on site
2. Part replacement/repair
a. For any part replacement or repair service the warranty for the repaired or new part shall be a minimum of 6 (six) months from the date of receipt of the repaired or new part. In case a part was repaired twice already under this warranty and the equipment becomes faulty again within up to six months the Operator on its discretion may request replacement of the complete equipment
3. Major defect
a. In case of major defect in the supplied products, the Operator reserves the right to reject the equipment. The supplier shall replace the defected system/parts under no cost from the Operator, including dismantling, hoisting, transportation and re-installation
2 PRODUCTS
2.1 MANUFACTURERS
1. Products manufacturer should be ISO certified
2. Batteries manufacturing date should not be older than four (4) months.
2.2 BATTERY CHARACTERISTICS
A. General
1. Application: Telecommunication
2. Type: Absorbent Glass Mat (AGM) or GEL – VRLA (valve regulated lead acid)
3. Reliability and robustness:
a. Positive tubular plates die-cast for longer life duration
b. Low self-discharge rate with optimized number of cycles for a long life expectancy
4. Design life: greater than 10 years at 60% depth of discharge @ 20°C ambient temperature; Eurobat 1999 – classified as long life
B. Battery Specifications
1. Design life: 15 years @ 20°C ambient temperature floating voltage
2. Cycle life: Minimum 1000 cycles @ 60% depth of discharge (DoD) @ 20°C. The bidder should submit support test documentation.
3. Nominal Block Voltage: 12Vdc
a. Capacity: Rated 10 hours to 1.8Vpc @ 20°C
4. Size: 165AH, C10, 1.8Vpc @ 20°C
5. System Voltage (string): -48Vdc (4x 12Vdc)
6. End (cut-off) voltage: 1.8Vdc per cell
7. Charging current: That can be applied to the battery during recharging under the specified float conditions and under any refresher charge conditions must be stated by the supplier.
8. Float voltage: Shall be in between 2.2 and 2.27Vdc per cell @ 25°C and shall remain stable (±0.05Vdc) throughout the battery life. Since the charging voltage differ due to acid Ph and metallurgy between the various battery manufacturers and is also related to the working temperature, hence charging voltages shall be adjusted according to the graph supplied with each battery type; Supplier should deliver the charge voltages graph per cell (charging and floating)
9. Self-discharge rate: The self-discharge rate of the battery shall be less than 0.5% per week.
10. Recharge rate: Recharge rate of 90% shall be within 12hours.
11. Efficiency of Recharging – AH: greater than 90%
12. Recombination efficiency: Shall not be less than 97% @ 25°C after ten (10) discharge cycles or twelve (12) months on float operation.
13. Operating temperature: is from -10°C to +45°C and Humidity <90%. Battery should withstand hard freezing without damage of the alloy, plates, or cell container assembly.
14. Ventilation: gas discharge rate should be indicated and the required ventilation system should be proposed.
2.3 BATTERY STORAGE
1. Storage: Temperature range of -20°C to +45°C, Humidity <90%
2. Shelf life: one (1) year at 20°C without recharge.
3. Batteries storage time shall not exceed 2 years.
4. The supplier is responsible to perform one refreshing charge to stored batteries at his warehouse free of charge during the first year of storage. If the supplied batteries need more than one refreshing charge per year, the supplier shall bear the expenses of the additional refreshing charges.
2.4 BATTERY REFRSHING CHARGE
1. Batteries must be given a refreshing charge:
a. When maximum storage time is reached, or
b. When the OCV (Open Charge Voltage) approaches 2.10Volts/cell whichever occurs first
2. Refreshing charge: The refresh charge should be conducted using constant voltage (adjusted to the temperature) eg. 2.23Vpc at 20-25°C with 0.1 C10 Amps current limit for a minimum period of 96h.
2.5 BATTERY CONSTRUCTION
1. AGM
a. Positive plates: tubular plates consisting of Lead-Calcium alloy with high corrosion resistance
b. Negative plates: grid plate consisting of Lead-Calcium alloy
c. Separators: low resistance microporous material
2. GEL
a. Lead/calcium alloys in both positive and negative electrodes.
b. Thick plates with mechanical strengthening of the positive mass.
3. Case material: container and lid in ABS (Acrylanitrile Butadiene Styrene) according to UL94-V0 (V-0: burning stops within 10 seconds on a vertical specimen; drips of particles allowed as long as they are not inflamed.)
4. Installation: vertical installation inside rack
5. Terminals: Front with brass insert and M10/M8 stainless steel bolts. Colored washers to be provided for easy polarity recognition. Terminals should be protected during transport.
6. Connectors:
a. Insulated solid copper connector (30 x 3mm) for vertical installations or insulated flexible cable connectors (70-90mm²) for horizontal installations.
b. Each connector design is of the bolt-on type
c. Each connector allows for voltage measurements
7. Pressure relief valve: one way gas release valve in case of excess pressure with integral flame arrestor and protects cell against atmosphere.
2.6 BATTERY INSTALLATION
1. Physical arrangement shall ensure access to each battery block terminals.
2. Must be easy to install and virtually maintenance free
3. Mixing of different capacity rating is not permitted
2.7 LABELS
A. Each cell shall be clearly and permanently labeled identifying:
1. Manufacturer
2. Model
3. Origin of manufacturer
4. Date of manufacture (year and month)
5. Nominal voltage
6. Nominal AH capacity at 10hrs to 1.8V/cell @ 25°C
B. Each cell shall be consequently numbered at the positive (GND) terminal.
C. Each string shall be labeled with a clear string identification number.
2.8 ACCESSORIES
1. Connectors, bolts, nuts, buss bars, lugs, insulation covers, labels, jumpers to connect the batteries strings in parallel, lifting straps, etc. necessary for the installation of the batteries should be delivered with the batteries. Note that inter-cell connectors shall be lead plated copper.
3 EXECUTION
3.1 STORAGE
A. All products including batteries should be stored at the supplier warehouse till the date of installation on site.
B. The supplier is responsible to perform one refreshing charge to stored batteries at his warehouse free of charge during the first year of storage. If the supplied batteries need more than one refreshing charge per year, the supplier shall bear the expenses of the additional refreshing charges.
C. Storage Conditions and Time
1. If a battery cannot be immediately installed it should be stored in a clean, cool, dry area.
2. High temperature increases the rate of self-discharge and reduces the storage life. Therefore, the storage temperature should be 20°C ~ 25°C.
D. Refresh Charge
1. Mono-blocs and cells must be given a freshening charge when the OCV approaches the equivalent of 2.10 Volts per cell or when the maximum storage time has been reached.
2. Freshening charge should be by means of constant voltage charge set between 2.29 and 2.40Vpc with current limit 0.1C10 A for 24 hours. Recommended OCV audit intervals are given in the table below.
E. Commissioning Charge
1. Before conducting a capacity discharge or commencing cycling, the battery must be given a commissioning charge.
2. In float applications the commissioning charge shall consist of 7 continuous days of float charge at the recommended float voltage (2.29Vpc at 20°C) with no load connected to the battery.
3.2 INSTALLATION
A. All batteries transported to site should be fully charged at the supplier warehouse in order to prevent overload on the site mains power supply, EDL & generator.
B. Blocs and cells can be mounted in the orientation indicated by manufacturer
C. Blocs and cells should not be inverted.
D. Do not use terminal posts to lift or handle cells.
E. Do not install the cells in such a way that the box-lid bond is resting on a runner.
F. Always ensure that the arrow on the lid of each unit is pointing in vertical orientation
G. The battery compartment/room must have adequate ventilation to limit hydrogen accumulation to a maximum of 1% by volume of free air.
H. Each mono-bloc/cell is supplied with the terminal/connector Fasteners.
I. On each mono-bloc/cell the positive terminal is identified by a “+” symbol. Install the batteries in accordance with the instructions and/or layout drawing, taking care to ensure correct terminal location and polarity.
J. Connect the blocs/cells with the connectors and fasteners provided. Tighten the fastener set bolt(s) / nut(s) to the fastening torque level indicated on the product label.
K. Place the insulating covers in position immediately after tightening the fasteners.
3.3 COMMISSIONING
A. Safety, installation & ventilation
1. The battery room should be well ventilated in order to remove gases produced during charging. The gases (mixture of oxygen and hydrogen) liberated by the cells when on charge may cause an explosion, and therefore, care must be taken not to produce SPARKS.
2. NAKED LIGHTS must be not allowed, and remember NO SMOKING.
B. Following precautions must also be taken:
1. Do not wear clothing likely to create static electricity (nylon) during maintenance operations
2. Do not use a portable apparatus linked to an electric plug
C. The electrical protective measures and the accommodation and ventilation of the battery installation must be in accordance with the applicable “local” national standards, rules and regulations. Specifically EN 50272-2 standard applies. Low ventilation requirement according to EN 50272-2.
D. The battery should be installed in a clean, dry area.
E. Avoid placing the battery in a hot place or in front of a window (no direct sunlight). Battery racks are recommended for proper installation. Place the cells on the rack and arrange the positive and the negative terminals for connection according the wiring diagram.
F. Check that all contact surfaces are clean. Tighten terminal screws, taking care to use the correct torque loading.
G. Follow the polarity to avoid short circuiting of cell groups. A loose connector can cause trouble in adjusting the system, erratic battery performance, and possible damage to the battery and/or personal injury.
H. Commissioning: The initial charge is extremely important as it will condition the battery service life. So the battery must be fully recharged to ensure that it is in an optimum state of charge. The recommended float charge voltage is 2.25Vpc (20°C).
I. End-of-charge
1. End-of-charge is when all cell voltages and electrolyte specific gravities (corrected to 25°C) cease to rise for three consecutive hourly readings.
2. Continue charging until the specific gravity of electrolyte for all cells rise to nominal specific gravity at maximum level.
J. Electrolyte specific gravities:
1. Measure the specific gravity with a hydrometer
2. After reading, squirt the solution back into the cell from which it was drawn
3. The nominal specific gravity at the end of the charge at the specified level is for a temperature of 25ºC
4. If temperature is above or below 25ºC, specific gravity reading must be adjusted using the table provided by supplier.
K. Nominal electrolyte specific gravity of cells at maximum level = 1.240 at 25°C
3.4 OPERATION
A. Stand-by / Float Operation
1. Constant voltage chargers are recommended. The charging voltage should be set at the equivalent of 2.29Vpc at 20°C or 2.27Vpc at 25°C.
2. Operation at temperatures higher than 20°C will reduce life expectancy. Life is reduced by typically 50% for every 10°C rise in temperature.
3. To offset the impact of higher temperatures compensation to the f oat voltage should be applied.
4. The recommended float voltage temperature compensation is:
5. Due to the very low internal resistance, mono-blocs and cells will accept unlimited current during recharge but for cost and practical purposes in float applications where recharge time to repeat duty is not critical, the rectifier current can be limited to the load plus 0.1C10 Amps.
B. Cyclic Operation
1. In cyclic applications the charging voltage should be set at the equivalent of 2.40Vpc cell at 20°C, with the rectifier current limit set to a minimum of 0.1C10A
2. The optimal cyclic performance is achieved by returning the battery to full state of charge between discharge cycles.
3.5 MAINTENANCE
1. The following may be used as a suggested maintenance schedule.
2. Monthly (record all readings)
a. Measure the battery string voltage.
b. If necessary, adjust the float voltage to the correct value.
3. Every six months (record all readings)
a. Measure the battery string voltage. If necessary, adjust the f oat voltage to the correct value.
b. Measure individual bloc/cell voltages. The blocs/cells should be within 5% of the average.
c. Inspect for contamination by dust, loose or corroded connections. If necessary isolate the string/bloc/cell and clean with a damp soft cloth.
d. Warning - Do NOT use any type of oil, solvent, detergent, petroleum-based solvent or ammonia solution to clean the battery containers or lids. These materials will cause permanent damage to the battery container and lid and will invalidate the warranty.
3.6 DISCHARGE TESTS
A. The supplier shall perform a discharge test to confirm the quoted capacity of the battery.
B. This test will be performed after the installation and will be conducted at the nominal 10hrs discharge rate to 1.8V/cell.
C. Use the following test procedure or use the test procedure described in IEEE standard 1188.
D. An equalizing charge, as described in Section 3.1, must have been given within the last 7 days. (Battery should be returned to float for 7 days before the test.)
1. Make sure all battery connections are clean, tight and free of corrosion.
2. While the battery is on float read and record voltage of each cell, temperature of at least every tenth cell and battery terminal float voltage.
3. Disconnect the battery charger.
4. Select the discharge rate based upon the critical load and time period. The test discharge current is equal to the rated discharge current divided by the K Factor (see Table below) for the initial battery temperature.
5. With the variable load bank having an ammeter in series and a voltmeter across the battery terminals, connect the load, simultaneously starting the timing device. Maintain the correct current while periodically reading and recording total battery voltage. When the minimum total voltage has been reached, it is desirable to read and record each cell voltage including an inter-cell connector.
6. Observe the battery for inter-cell connector heating.
7. Calculate the capacity using the following formula:
a. % Capacity at 25˚C = (Ta/Ts) x100
b. Where Ta = test discharge time to specified voltage
c. Where Ts = rated discharge time to specified voltage
8. Recharge the battery, preferably using an equalizing charge (Section3.1) to minimize the recharge time.
E. The supplier shall submit the following records prior to issuance of an Acceptance Certificate.
1. Initial charge records
2. Discharge test records
3. Recharge records
4. Test forms
3.7 DISPOSAL
A. Batteries are recyclable. End of life batteries must be packaged and transported according to prevailing transportation rules and regulations. End of life batteries must be disposed of in compliance with local and national laws by a licensed battery recycler.
END OF SECTION

## Grade of Compliancy
| RFT Compliance Matrix | Reference Number | SF-CF-25
|  | Owner | PRO
|  | Revision Code | 3.0
|  | Implementation Date | 2024-03-01
Grade of Compliance range from 0 to 15 with a step of 1 unit:
15 : Compliant with additional value, not initially included in the requirements
10 : Fully compliant
4 - 5 - 6: Partially compliant
0 : Not compliant
K : Disqualification