## General Requirements
| RFT Compliance Matrix |  |  |  | Reference Number | SF-CF-25
[5 empty] | Owner | PRO
[5 empty] | Revision Code | 3.0
[5 empty] | Implementation Date | 2024-03-01
Project Name:
Reference Number:
RFT Article (Part Number or Title) | Requirements (Description) | Killer | Fully Compliant | Partially Compliant | Non-Compliant | Reference (Specify document & page nb)
Article 4 | Conditions for the Participation of the Eligible Bidders
4.1 | 1- Bidders shall meet the following conditions, declared in accordance with the required documents in the First section of this Article mentioned below as (First: Envelope No. (1) Administrative Documents and Transactions):
a- That there is no proven violation, by the bidders, of professional ethics generally accepted and stipulated in the relevant provisions, if any;
b- Bidders have the legal capacity to enter into the procurement contract;
c- Bidders have fulfilled their obligations to pay taxes and social security contributions;
d- Bidders have not been convicted, neither their directors nor employees involved with the procurement process, by a court decision of any criminal offence - even if the verdict can still be appealed - related to their professional conduct or the making of false statements or misrepresentations as to their qualifications to enter into a procurement contract, or corrupting a public procurement or a contract awarding process, or have not been otherwise disqualified pursuant to administrative suspension or debarment proceedings, or have been in a situation of exclusion from participation in public procurements;
e- Bidders are not the subject of legal proceedings for insolvency or bankruptcy, or were declared bankrupt by a court of law;
f- Bidders have not been convicted by a court decision - even if the verdict can still be appealed - of usury or money laundering;
g- Bidders have not participated in the decision-making process of the contracting authority or have any conflict of interest, or any material interest linking them to any of the decision makers;
h- Any other conditions set forth by the contracting authority in the tender documents that are commensurate with the required works;
i- Certificate from the Ministry of Economy proving compliance with the provisions of the Law on Boycott of Israel for foreign companies (added by Law No. 309, dated April 19, 2023).
j- Declaration of the economic beneficiaries (according to Law No. 309, dated April 19, 2023).
4.2 | 2- The bid must be submitted clearly and unequivocally without any deletion, alteration, or modification.
4.3 | 3- The bidders state in their offer that they have reviewed the Tender document and its complementary documents and have obtained a copy. They accept and undertake to adhere to all the conditions outlined therein without any reservations or exceptions. The bidder submits their offer on this basis and affixes financial stamps worth fifty thousand Lebanese pounds covering all the documents.
4.4 | 4- Any bid containing reservations or exceptions is rejected.
4.5 | 5- The bidder mentions in their offer a clear address and place of residence for prompt communication.
Administrative Documents and Transactions | First: Envelope No. (1) Administrative Documents and Transactions
A- General Conditions:
1- Undertaking Letter (Declaration), according to the attached form, signed and stamped by the bidder, this Undertaking includes the bidder's confirmation of their commitment to the price and the validity of the offer. A financial stamp of 50,000 L.L. is affixed.
2- Commercial Circular specifying the authorized signatory of the bidder and a sample of their signature.
3- Legal Authorization: If the offer is signed by someone other than the person authorized to sign according to the commercial circular, it must be notarized by a notary public.
4- Police Record of the Authorized Signatory or his “legal representative”, not exceeding three months from the bid opening date.
5- Partnership Contract legalized by a notary public if required.
6- Registration Certificate before the Directorate of Value Added Tax, if applicable, or a certificate of non-registration if not subject to it. In the latter case, the bidder commits to their bid price even if they become registered for VAT during the execution period.
7- Registration Certificate issued by the Ministry of Finance – Department of Revenue.
8- Certificate issued by the Ministry of Finance proving the bidder's compliance with tax obligations.
9- Clearance Certificate from the National Social Security Fund “comprehensive or valid for participation in public tenders and bids” valid on the date of the bid opening session, stating that the bidder has paid all his subscriptions (the bidder must be registered before the National Social Security Fund and any statement mentioning the phrase “unregistered institution” will be rejected).
10- Certificate issued by the Municipality, proving full payment of municipal fees by the bidder, issued by the municipality within its jurisdiction based on the commercial registration certificate.
11- Comprehensive Certificate issued by the Commercial Register showing founders, members, contributors, or partners, authorized signatories, the manager, capital, the bidder's activity, and ongoing liabilities.
12- Certificate issued by the relevant authorities proving that the bidder is not in a state of bankruptcy.
13- Certificate issued by the relevant authorities proving that the bidder is not in a state of judicial liquidation.
14- Bid bond as required in the specific Tender document of the procurement project, in accordance with Articles 34 and 36 of the Public Procurement Law.
15- Declaration from the Bidder identifying the economic beneficiary/beneficiaries according to Form M18 issued by the Ministry of Finance (any natural person who owns or effectively controls the ultimate outcome of the activity practiced by the bidder, either directly or indirectly, whether the bidder is a natural person or a legal entity.)
16- Copies of Identification Cards (ID/Passport) for the economic beneficiary/beneficiaries.
17- Copies of Identification Cards (ID/Passport) for each person representing the bidder (those acting on behalf of the bidder in their relationship with the contracting authority: legal representative, representative of the legal entity, or authorized signatory).
18- Integrity Declaration Document signed by the bidder in accordance with the prescribed format
Miscellaneous | The bidder shall declare any relative relations with any Alfa employee up to the 4th degree under Clause 30 of the PPL, for MIC1 to be able to assess the existing of any potential conflict of interests which may lead to deprive the bidder from participating to the tender under the risk of disqualification.
The bidder or any of his employees, partners, agents, contributors, consultants, or their relatives shall declare any relationships that may lead to a conflict of interest in the subject of this contract.
Special Conditions | B- Special Conditions Regarding the Subject of the Contract:
Financial Qualifications | 1- Financial Qualifications (To be determined based on the size and nature of the contract).
Technical/Professional Qualifications | 2- Technical/Professional Qualifications (To be determined based on the nature of the contract):
1- Certificate from the Chamber of Commerce, Industry, and Agriculture confirming that the bidder is engaged in the activities related to the subject of the contract, valid as of the date of the bidding session and valid for participation in public tenders.
2- Clearance certificate from the Order of Engineers…
3- Clearance certificate from the Contractors Syndicate…
4- ISO certificate.
5- Five Certificates of good execution and completion for similar projects in terms of size and type.
6- Technical proposal according to the required specifications in the appendix (1) of the RFT.
7- Declaration of site inspection by the bidder, denying any unfamiliarity, according to the attached model.
Participation of a foreign bidder | C- In case of the participation of a foreign bidder, the bidder must comply with one of the following conditions:
1- is part of a coalition that includes at least one Lebanese company that meets the conditions required by the specific Tender document of the procurement project.
2- The personal presence of the legal representative of the company to participate in the procurement proceedings (not mandatory).
3- Has an authorized agent or representative in Lebanon responsible for signing the contract on its behalf.
In addition to the above conditions, the foreign bidder must submit the following:
1- Certificate registration of the company or certificate of establishment issued by the relevant authorities in their country.
2- Certificate from the Lebanese Ministry of Economy and Trade confirming compliance with the provisions of the Law on Israel Boycott.
3- The required certificates according to paragraph (First) above, according to the laws of the country where the bidder is located, provided that these certificates are authenticated according to the regulations of the competent authorities.
For certificates issued without an expiration date, the validity date of each certificate is determined according to its nature, not exceeding six months from the date of the bid opening session.
Information Security Specifications | Information Security Specifications Issuing Department to determine whether all or part of this Article is applicable to their specific RFT
The Bidder shall commit to refrain from offering any product / equipment which can cause security threat or information leakage that jeopardizes MIC1 network security. (K)
The Bidder shall accept that MIC1 runs a vulnerability scan on the proposed solution prior to issuing the acceptance and in case any vulnerability is found, the Bidder undertakes to take the necessary actions to remedy such vulnerability within _____________________ days from its notification.
The Bidder shall mention the security standards adopted/followed in designing the proposed solution.
The Bidder should specify if it has acquired the ISO27001 certification or any other equivalent security certification and submit with the Offer a copy of such certificate.
The Bidder shall not hard code passwords in the proposed solution.
The provided application should run without the need of root (unix) and / or admin (win) privileges.
Source code of proposed application should be owned by MIC1.
System shall allow generation of user, operator as well as alarms logs.
Solution and storage shall be sized to host history logs for at least 1 year back.
The Bidder should submit a data flow diagram and schema of the solution architecture.
In case of online payment, the Bidder shall use encryption. (K)
The Bidder shall harden systems servers / storage before being published online, and describe hardening aspects applied on each type.
The Bidder shall describe security checking and audits performed on the designed solution prior to putting it on the market.
The Bidder shall change default errors / messages and configuration.
Application should support role-based access, specific privileges per user (i.e specific access to application modules and reports)
Database should support restricted access per user or groups to data (i.e access per field or per table, …)
Encryption shall be used in all communications / interactions between systems, especially if the communication is through web access. Web based access shall always be used through HTTP+SSL.
Each user shall have only one account / profile to access data.
Least-privileges should always be specified on nodes / applications.
Pseudocode flow chart shall be provided by the Bidders.
The Bidder should commit to improve solution / systems information security weaknesses whenever needed or highlighted by MIC1 information security team.
Health, Safety and Environmental Specifications | To ensure that the proposed products and services bidders are compliant with HSE culture, bidders should state basic HSE specifications and compliance information:
Bidder shall provide the product’s specifications that have an environmental impact (power consumption, gas emissions, etc…)
Bidder shall provide the product specifications that contribute into preserving the environment (made of recycled material, ozone friendly, low volatile organic compounds, etc…)
Bidder shall provide the product’s specifications that contribute towards the health and safety of the users (ergonomic design, safety features, etc)
Bidder shall state the safety measures being followed by personnel performing the work on Alfa’s sites (ISO45001 certification, specific best practices, etc…).
Bidder shall provide the product’s life cycle data if available.

## Technical Requirements
| RFT Compliance Matrix |  |  |  | Reference Number | SF-CF-25
[5 empty] | Owner | PRO
[5 empty] | Revision Code | 3.0
[5 empty] | Implementation Date | 2024-03-01
Project Name: | JDEIDET DATA CENTER
Reference Number: | 26 33 53.00.UPSC02 - Static Uninterruptible Power Supply - Core - 10.2023
RFT Article (Part Number or Title) | Requirements (Description) | Killer | Fully Compliant | Partially Compliant | Non-Compliant | Reference (Specify document & page nb)
1 GENERAL
1.1 SUMMARY
A. Uninterruptible power source (UPS) for core sites.
B. Scope: Provide design and engineering, labor, material, equipment, related services, and supervision required, including, but not limited to, manufacturing, fabrication, erection, and installation for a static uninterruptible power supply (UPS) as required for the complete performance of the work, and as shown on the Drawings and as herein specified.
1.2 REFERENCES
A. Institute of Electrical and Electronics Engineers, Inc. (IEEE):
1. ANSI/IEEE 519 – Guide for Harmonic Control and Reactive Compensation of Static Power Converters
B. International Organization for Standardization (ISO):
1. ISO 9001:2015 – Quality Management Systems ‑ Requirements.
2. ISO 14001 – Environmental Management Systems ‑ Requirements with Guidance for Use.
C. Underwriters Laboratories, Inc. (UL):
1. UL 891 – Standard for Dead‑Front Switchboards
2. UL 1558 – Standard for Metal‑Enclosed Low‑Voltage Power Circuit Breaker Switchgear
3. UL 1778 – Standard for Uninterruptible Power Supply Equipment
4. UL 60950 – Standard for Information Technology Equipment
D. International Electrotechnical Commission (IEC):
1. IEC 61000-4-2 –Electromagnetic Compatibility ‑ Testing and Measurement Techniques; Electrostatic Discharge Immunity Test
2. IEC 61000-4-3 – Electromagnetic Compatibility ‑ Testing and Measurement Techniques; Radiated, Radio Frequency, Electromagnetic Field Immunity Test
3. IEC 61000-4-4 – Electromagnetic Compatibility ‑ Testing and Measurement Techniques; Electrical Fast Transient/Burst Immunity Test
4. IEC 61000-4-5 – Electromagnetic Compatibility ‑ Testing and Measurement Techniques; Surge Immunity Test
5. IEC 62040‑2 – Uninterruptible Power Systems ‑ Electromagnetic Compatibility (EMC) Requirements
6. IEC 62040‑3 – Uninterruptible Power Systems ‑ Method of Specifying the Performance and Test Requirements
1.3 SUBMITTALS
A. Product Data: Submit product data showing material proposed. Submit sufficient information to determine compliance with the Drawings and Specifications. Product data shall include, but shall not be limited to, the following:
1. Bill of materials
2. Product data sheets
3. Product guide specifications.
4. Manufacturer recommendations
5. Warranty Certificate
B. Shop Drawings: Submit shop drawings for each product and accessory required. Include information not fully detailed in manufacturer’s standard product data, including, but not limited to, the following:
1. Installation information, including, but not limited to, weights and dimensions.
2. Information about terminal locations for power and control connections.
3. Drawings for requested optional accessories.
C. Wiring Diagrams: Submit wiring diagrams detailing power, signal, and control systems, clearly differentiating between manufacturer‑installed wiring and field‑installed wiring, and between components provided by the manufacturer and those provided by others.
1. Submit system single‑line operation diagram.
D. Operation and Maintenance Data: Submit operation and maintenance data to include in operation and maintenance manuals, including, but not limited to, safe and correct operation of UPS functions.
1. Submit an installation manual, which shall include, but shall not be limited to, instructions for storage, handling, examination, preparation, installation, and start‑up of UPS.
2. Submit an operation and maintenance manual, which shall include, but shall not be limited to, operating instructions.
1.4 WARRANTY
A. Equipment
1. The supplied products shall be covered by full supplier warranty for a minimum period of one (1) year from delivery to site at a full repair and replacement service.
2. Warranty shall include all defected spare parts and workmanship.
B. Services
1. Installation and dismantling
a. The supplier is responsible for the dismantling, hoisting, transportation and re-installation for parts that cannot be repaired or replaced on site
2. Part replacement/repair
a. For any part replacement or repair service the warranty for the repaired or new part shall be a minimum of 6 (six) months from the date of receipt of the repaired or new part. In case a part was repaired twice already under this warranty and the equipment becomes faulty again within up to six months the Operator on its discretion may request replacement of the complete equipment
3. Major defect
a. In case of major defect in the supplied products, the Operator reserves the right to reject the equipment. The supplier shall replace the defected system/parts under no cost from the Operator, including dismantling, hoisting, transportation and re-installation
2 PRODUCTS
2.1 MANUFACTURERS
A. Origin and manufacturing:
1. Products manufacturer should be ISO 9001:2015 certified.
2.2 APPROVED BRANDS
A. APC / Schneider Electric
B. Socomec
C. Emerson
D. General Electric
E. PCE
F. or equivalent
2.3 SYSTEM RATING
A. UPS Capacity:
4. 120KVA – 108KW @ 0.9pf
B. The UPS battery shall be sized for 100% load at a power factor of 0.9 for 2 hours.
2.4 SYSTEM DESCRIPTION
A. Type: Double Conversion On-Line
B. Synchro mode ready
C. Input: The system input shall be configurable as dual mains. Mains 1 derived from a three-phase delta source while mains 2 is derived from a three-phase wye source. Standard cable entry shall be through the top. Bottom cable entry shall also be facilitated. Depending on the specific configuration, the use of the optional bottom feed enclosure may be required. An option shall be available to facilitate the connection of NEMA 2 compression lugs for main input, bypass input, DC input, and output cable connections.
D. AC Input Nominal Voltage: 380 volts
E. AC Input Voltage Window:
1. ±15% for full performance (323V to 437V at 380Vac).
2. ‑20% with reduced charge power (304V at 380Vac).
F. Short Circuit Withstand Rating: 100KA symmetrical.
G. Maximum Frequency Range: 40 to 60 hertz. Frequency shall be synchronized to bypass input when available over the standard range of 47 to 53 hertz. Optional frequency tolerance range shall be configurable from 0.5 percent to 8 percent from front panel.
H. Input Power Factor:
1. Greater than 0.995 with load at 100 percent.
2. Greater than 0.99 with loads above 50 percent.
3. Greater than 0.97 with loads above 25 percent.
I. Input Current in Normal Operation: Shall be limited to a maximum of 137 percent of the system capacity.
J. Input Current Distortion with No Additional Filters: <5 %
K. Soft‑Start: Shall be linear from 0 percent to 100 percent input current and shall not exhibit inrush. This shall take place over an Owner‑selectable 1 second to 60 second time period with a factory default of 10 seconds.
L. UPS Output:
1. Waveform: pure sinusoidal waveform
2. AC Output Nominal Output: System voltage shall be selectable at the graphical user interface by service personnel with the following options: 380 volts.
3. AC Output Voltage Distortion: Less than 2 percent at 100 percent linear load, less than 6 percent for SMPS load as defined by IEC 62040‑3.
4. AC Output Voltage Regulation: ±1% for 100% linear or non‑linear load.
5. Voltage Transient Response: ±5% maximum RMS change in a half cycle at load step 0 percent to 100 percent or 100% to 0%.
6. Voltage Transient Recovery: Within less than 50 milliseconds.
7. Output Voltage Harmonic Distortion: Less than 2% THD maximum and 1% single harmonic for a 100% linear load.
8. Phase Angle Displacement:
a. 120 degrees ±0.1 degree for balanced load.
b. 120 degrees ±0.1 degree for 50 percent imbalanced load.
c. 120 degrees ±0.3 degrees for 100 percent imbalanced load.
M. Overload Rating:
1. Normal Operation:
a. 150% for 30 seconds before transfer to bypass.
b. 125% for 10 minutes before transfer to bypass.
2. Battery Operation: 125% for 30 seconds.
3. Bypass Operation:
a. 125% continuous at 480 volts.
b. 1000% for 100 milliseconds.
N. System AC-AC Efficiency:
1. Normal operation greater than 96% at 40% to 100% load.
2. Battery operation greater than 95% at 40% to 100% load.
O. Output Power Factor Rating: 0.5 leading to 0.5 lagging without any derating.
2.5 ENVIRONMENTAL REQUIREMENTS
A. Storage Ambient Temperature: ‑15°C to 40°C
B. Operating Ambient Temperature: 0°C to 40°C
C. Relative Humidity: 0% to 95%
D. Operating Relative Humidity: 0% To 95% non‑condensing.
E. Altitude: Maximum installation with no derating of the UPS output shall be 1000m above sea level.
F. Audible Noise at 480Vac operation at 25 °C:
1. 54 dBA at 100% load.
2. 45 dBA at 70% load.
2.6 MODES OF OPERATION
A. Normal: The power factor correction (PFC) input stage and output inverter shall operate in an on‑line manner to continuously regulate power to the critical load. The input and output converters shall be capable of full battery recharge while simultaneously providing regulated power to the load for all line and load conditions within the range of the UPS specifications.
B. Battery: Upon failure of the AC input source, the critical load shall continue being supplied by the output inverter, which shall derive its power from the battery system. There shall be no interruption in power to the critical load during both transfers to battery operation and retransfers from battery to normal operation. Upon restoration of utility power to the UPS input, the UPS shall recharge the battery.
C. Static Bypass: The static bypass shall be used to provide controller transfer of critical load from the inverter output to the bypass source. This transfer, along with its retransfer, shall take place with no power interruption to the critical load. In the event of a UPS output fault or significant output overload emergency, this transfer shall be an automatic function. Manual transfer to static bypass (called “requested bypass”) shall be available in order to facilitate a controlled transfer to maintenance bypass.
2.7 POWER FACTOR CORRECTION (PFC) INPUT STAGE
A. General: The power factor correction (PFC) input stage converters of the system shall constantly control the power imported from the mains input of the system, to provide the necessary UPS power for precise regulation of the DC bus voltage, battery charging, and main inverter regulated output power.
B. Input Current Total Harmonic Distortion: The input current THDI shall be held to less than 5 percent at system load greater than 50 percent while providing conditioned power to the critical load bus, and charging the batteries under steady‑state operating conditions. This shall be true while supporting both a linear or non‑linear load. This shall be accomplished without the requirement for additional or optional filters, magnetic devices, or other components.
C. Soft‑Start Operation: As a standard feature, the UPS shall contain soft‑start functionality, capable of limiting the input current from 0 percent to 100 percent of the nominal input over a default 10 second period, when returning to the AC utility source from battery operation. The change in current over the change in time shall take place in a linear manner throughout the entire operation.
D. Magnetization Inrush Current: The UPS shall exhibit zero inrush current.
E. Input Current Limit:
1. The PFC input stage shall control and limit the input current draw from utility to 137 percent of the UPS output. During conditions where input current limit is active, the UPS shall be able to support 100 percent load, charge batteries at 10 percent of the UPS output rating, and provide voltage regulation with mains deviation ‑15 percent.
2. In cases where the source voltage to the UPS is nominal and the applied UPS load is equal to or less than 100 percent of UPS capacity, input current shall not exceed 116 percent of UPS output current, while providing full battery recharge power and importing necessary power to account for system losses.
F. Charging:
1. The battery charging shall keep the DC bus float voltage of ±327Vdc, ±1%.
2. The battery charging circuit shall contain a temperature compensation circuit, which shall regulate the battery charging to optimize battery life.
3. The battery charging circuit shall remain active when in static bypass and in normal operation.
4. The UPS shall be capable of reducing the battery charging current under low input voltage conditions.
5. Battery charge shall be limited to 10% of battery bank capacity (AH) by default. The UPS shall be capable of recharging the battery at a capacity up to 20% of battery bank capacity (AH) at reduced loads.
6. The UPS shall be capable of being programmed to reduce battery charging current in normal operation by 10 percent or 20 percent by service personnel.
G. Back‑Feed Protection: The above-mentioned logic‑controlled contactor shall also provide the back‑feed protection required by UL 1778.
2.8 OUTPUT INVERTER
A. General: The UPS output inverter shall constantly develop the UPS output voltage waveform by converting the DC bus voltage to AC voltage through a set of IGBT driven bi‑directional power converters. In both normal operation and battery operation, the output inverters shall create an output voltage independent of the mains input voltage. Input voltage anomalies such as brown‑outs, spikes, surges, sags, and outages shall not affect the amplitude or sinusoidal nature of the output voltage sine wave of the inverters.
B. Overload Capability: The output power converters shall be capable of 230 percent for short circuit clearing. Steady‑state overload conditions, of up to 150 percent of system capacity shall be sustained by the inverter for 30 seconds in normal operation. Overloads persisting past the outlined time limitation the critical load shall be switched to the automatic static bypass output of the UPS.
C. Output Contactor: The output inverter shall be provided with an output mechanical contactor to provide physical isolation of the inverter from the critical bus. With this feature a failed inverter shall be isolated from the critical bus.
D. Battery Protection: The inverter shall be provided with monitoring and control circuits to limit the level of discharge on the battery system.
E. Redundancy: The UPS shall be capable of being configured with redundant output inverters, each with semiconductor fusing, and logic‑controlled contactors to remove a failed component from the input, DC, and output critical bus.
2.9 STATIC BYPASS
A. General: As part of the UPS, a system static bypass cabinet shall be provided. The system static bypass shall provide no break transfer of the critical load from the inverter output to the static bypass input source during times where maintenance is required, or the inverter cannot support the critical bus. Such times may be due to prolonged or severe overloads, or UPS failure. The UPS and static bypass switch shall constantly monitor the auxiliary contacts of their respective circuit breakers, as well as the bypass source voltage, and inhibit potentially unsuccessful transfers to static bypass from taking place.
B. Design: The design of the static switch power path shall consist of silicon‑controlled rectifiers (SCR) with a continuous duty rating of 125 percent of the UPS output rating.
C. Automatic Transfers: An automatic transfer of load to static bypass shall take place whenever the load on the critical bus exceeds the overload rating of the UPS. Automatic transfers of the critical load from static bypass back to normal operation shall take place when the overload condition is removed from the critical output bus of the system. Automatic transfers of load to static bypass shall also take place if for any reason the UPS cannot support the critical bus.
D. Manual Transfers: Manually initiated transfers to and from static bypass shall be initiated through the UPS graphical user interface.
E. Overloads: The static bypass shall be rated and capable of handling overloads equal to or less than 125 percent of the rated system output continuously. For instantaneous overloads caused by inrush current from magnetic devices, or short circuit conditions, the static bypass shall be capable of sustaining overloads of 1000 percent of system capacity for periods of up to 100 milliseconds.
F. System Protection: As a requirement of UL 1778, back‑feed protection in the static bypass circuit shall also be incorporated in the system design. To achieve back‑feed protection, a mechanical contactor in series with the bypass SCR(s) shall be controlled by the UPS/static switch, to open immediately upon sensing a condition where back‑feeding of the static switch by any source connected to the critical output bus of the system is occurring. One such condition could be a result of a shorted SCR.
2.10 DISPLAY AND CONTROLS
A. Control Logic: The UPS shall be controlled by intelligence module (IM).
B. Graphical User Interface: A microprocessor‑controlled user interface/display unit shall be located on the front of the system. The display shall consist of a 10.4 inch (264 mm) multicolor graphical display with 800 x 600 resolution.
C. Metered Data: The following data shall be available on the graphical user interface/display:
1. Input/output voltages, currents, frequencies
2. Breaker and switch status
3. Battery status
4. Event log
D. Event Log: The display unit shall allow the Owner to display a time and date stamped log.
E. Alarms: The display unit shall allow the Owner to display a log of active alarms. The following minimum set of alarm conditions shall be available:
1. Input frequency outside configured range.
2. AC adequate for UPS but not for bypass.
3. Low/No AC input, startup on battery.
4. Number of batteries changed since last on.
5. Number of batteries increased.
6. Number of batteries decreased.
7. Number of external battery cabinets increased.
8. Number of external battery cabinets decreased.
9. Redundancy restored.
10. Need battery replacement.
11. UPS fault.
12. On battery.
13. Shutdown or unable to transfer to battery due to overload.
14. Load shutdown from bypass. input frequency, volts outside limits.
15. Fault, internal temperature exceeded system normal limits.
16. Input circuit breaker open.
17. System level fan failed.
18. Redundancy lost.
19. Redundancy below alarm threshold.
20. Runtime below alarm threshold.
21. Load above alarm threshold.
22. Load no longer above alarm threshold.
23. Minimum runtime restored.
24. Bypass not in range (either frequency or voltage).
25. Back‑feed contactor stuck in off position.
26. Back‑feed contactor stuck in on position.
27. UPS in bypass due to internal fault.
28. UPS in bypass due to overload.
29. System in forced bypass.
30. Fault bypass relay malfunction.
31. Mains 1 input circuit breaker open/closed.
32. Mains 2 input circuit breaker open/closed.
33. Battery circuit breaker open/closed.
34. Output circuit breaker open/closed.
35. High DC warning.
36. High DC shutdown.
37. Low battery shutdown.
38. Low battery warning.
39. Door open.
F. Controls: The following controls or programming functions shall be accomplished by the use of the user interface/display unit. The touch screen display shall facilitate these operations:
1. Silence audible alarm.
2. Display or set the date and time.
3. Enable or disable the automatic restart feature.
4. Transfer critical load to and from static bypass.
5. Test battery condition on demand.
6. Set intervals for automatic battery tests.
7. Adjust set points for different alarms.
8. Potential free (dry) contacts.
G. Free Contacts: The following potential free contacts shall be available on an optional relay interface board:
1. Normal operation
2. Battery operation
3. Bypass operation
4. Common fault
5. Low battery
6. UPS off
H. Communication Interface Board: A communication interface board shall provide the following communication ports which shall be able to be used simultaneously:
1. RS232
2. RS485
3. Ethernet
4. Ethernet interface port for a remote display
5. SNMP
2.11 BATTERY
A. The UPS shall support an extended battery bank consisting of several strings. Each battery string shall be monitored for voltage and temperature for use by the UPS battery diagnostic. Battery charging current shall be temperature compensated.
B. Each battery string shall be protected by fuse at both ends of the battery cable, at battery rack side and at UPS side.
C. The UPS shall incorporate a battery management system to continuously monitor the status of each battery string. This system shall notify the Owner in the event a failed or weak battery string is found.
D. Battery Breaker Cabinet: To facilitate third party battery configuration, a battery breaker cabinet in a line‑p net shelter enclosure shall be available. Each cabinet shall monitor breaker status and battery temperature. Each circuit breaker shall be equipped shunt trip mechanisms and 1A/1B auxiliary contacts. The battery breaker cabinet shall accommodate top or bottom entry for cables.
E. Remote Batteries: Batteries shall have the capability to be located remote to the UPS. In such installations, an optional side car shall be used to connect the batteries by cables to the UPS. The battery side car shall accommodate top or bottom cable entry. The side car shall have overcurrent fuses to protect the cables. The fuse status shall be monitored by the UPS.
2.12 COMMUNICATION
A. Software and Connectivity:
1. Network Adaptor: The ethernet web/SNMP adaptor shall allow one or more network management systems (NMS) to monitor and manage the UPS in TCP/IP network environments. The management information base (MIB) shall be provided in DOS and UNIX "tar" formats. The SNMP interface adaptor shall be connected to the UPS via the RS‑232 serial port on the standard communication interface board.
2. Unattended Shutdown: The UPS, in conjunction with a network interface card, shall be capable of gracefully shutting down one or more operating systems during when the UPS is operation from the battery.
B. Remote UPS Monitoring: The following methods of remote UPS monitoring shall be available:
1. Web Monitoring: Remote monitoring shall be available via a web browser such as Internet Explorer.
2. Simple Network Management Protocol (SNMP): Remote UPS monitoring shall be possible through a standard MIB II compliant platform.
C. Software Compatibility: The UPS manufacturer shall have available software to support remote monitoring and initiate the graceful shutdown for the following systems:
1. Microsoft Windows 95/98/XP
2. Microsoft Windows NT 4.0 SP6/2000
3. OS/2
4. Netware 3.2 – 5.1
5. MAC OS 9.04, 9.22, 10
6. Digital Unix/True 64
7. SGI 6.0-6.5
8. SCO UNIX
9. SVR4 2.3, 2.41
10. SCO Unix Ware 7.0 - 7.11
11. SUN Solaris 2.6-2.8
12. SUN OS 4.13, 4.14
13. IBM AIX 4.3x-4.33g, 5.1
14. HP-UX 9.x-11.i
2.13 ACCESSORIES
A. Bottom‑Feed Enclosure: For installations greater than 250kW, a bottom‑feed enclosure shall provide the mechanical means necessary to support bottom feeds for specific system configurations.
B. Relay Board: Relay boards shall be provided for Owner connections to external alarms or to activate external Owner circuits.
C. All necessary accessories required for the proper installation and operation should be included and delivered with the system.
2.14 SPARE PARTS
A. Recommended Spare Parts
1. A detailed list of the recommended spare parts for 10 years should be submitted. The exhaustive list of all required spare parts must be provided with pricing information (USD) about each item. The calculation methodology must be described in a separate document based on preventive maintenance procedure and the MTBF for each part.
B. Spare Parts Availability
1. Specify delivery time of spare parts which are in stock and that which are ex-stock. Spare parts should be available for at least 10 years from the PO date.
3 EXECUTION
3.1 EXAMINATION
A. Verification of Conditions:
1. Examine areas and conditions under which the work is to be installed, and notify the Contractor in writing, with a copy to the Owner and the Architect/Engineer, of any conditions detrimental to the proper and timely completion of the work. Do not proceed with the work until unsatisfactory conditions have been corrected.
2. Beginning of the work shall indicate acceptance of the areas and conditions as satisfactory by the Installer.
3.2 INSTALLATION
A. General: Preparation and installation shall be in accordance with reviewed product data, final shop drawings, manufacturer’s written recommendations, and as indicated on the Drawings.
B. Factory‑Assisted Start‑Up: A factory‑trained service personnel shall perform the following inspections, test procedures, and on‑site training:
1. Visual Inspection:
a. Inspect equipment for signs of damage.
b. Verify installation per manufacturer's instructions.
c. Inspect cabinets for foreign objects.
d. Inspect battery units.
2. Mechanical Inspection:
a. Check UPS and external maintenance bypass cabinet internal control wiring connections.
b. Check UPS and external maintenance bypass cabinet internal power wiring connections.
c. Check UPS and external maintenance bypass cabinet terminal screws, nuts, and/or spade lugs for tightness.
3. Electrical Inspection:
a. Verify correct input and bypass voltage.
b. Verify correct phase rotation of mains connections.
c. Verify correct UPS control wiring and terminations.
d. Verify voltage of battery.
e. Verify neutral and ground conductors are properly landed.
f. Inspect external maintenance bypass switch for proper terminations and phasing.
4. Site Testing:
a. Ensure proper system start‑up.
b. Verify proper firmware control functions.
c. Verify proper firmware bypass operation.
d. Verify proper maintenance bypass switch operation.
e. Verify system set points.
f. Verify proper inverter operation and regulation circuits.
g. Simulate utility power failure.
h. Verify proper charger operation.
i. Document, sign, and date test results.
C. On‑Site Operational Training: During the factory‑assisted start‑up, operational training for site personnel shall include, but shall not be limited to, key pad operation, LED indicators, start‑up and shutdown procedures, maintenance bypass and AC disconnect operation, and alarm information.
3.3 DEMONSTRATION
A. General: Provide the services of a factory‑authorized service representative of the manufacturer to provide start‑up service and to demonstrate and train the Owner’s personnel.
1. Test and adjust controls and safeties. Replace damaged or malfunctioning controls and equipment.
2. Train the Owner’s maintenance personnel on procedures and schedules related to start‑up and shutdown, troubleshooting, servicing, and preventive maintenance.
3. Review data in operation and maintenance manuals with the Owner’s personnel.
4. Schedule training with the Owner, through the Architect/Engineer, with at least seven day’s advanced notice.
B. UPS Training Workshop: A UPS training workshop shall be available from the UPS manufacturer. The training workshop shall include, but shall not be limited to, a combination of lecture and practical instruction with hands‑on laboratory sessions. The training workshop shall include, but shall not be limited to, instruction about safety procedures, UPS operational theory, sub‑assembly identification and operation, system controls, adjustments, preventative maintenance, and troubleshooting.
END OF SECTION

## Grade of Compliancy
| RFT Compliance Matrix | Reference Number | SF-CF-25
|  | Owner | PRO
|  | Revision Code | 3.0
|  | Implementation Date | 2024-03-01
Grade of Compliance range from 0 to 15 with a step of 1 unit:
15 : Compliant with additional value, not initially included in the requirements
10 : Fully compliant
4 - 5 - 6: Partially compliant
0 : Not compliant
K : Disqualification