## General Requirements
| RFT Compliance Matrix |  |  |  | Reference Number | SF-CF-25
[5 empty] | Owner | PRO
[5 empty] | Revision Code | 3.0
[5 empty] | Implementation Date | 2024-03-01
Project Name:
Reference Number:
RFT Article (Part Number or Title) | Requirements (Description) | Killer | Fully Compliant | Partially Compliant | Non-Compliant | Reference (Specify document & page nb)
Article 4 | Conditions for the Participation of the Eligible Bidders
4.1 | 1- Bidders shall meet the following conditions, declared in accordance with the required documents in the First section of this Article mentioned below as (First: Envelope No. (1) Administrative Documents and Transactions):
a- That there is no proven violation, by the bidders, of professional ethics generally accepted and stipulated in the relevant provisions, if any;
b- Bidders have the legal capacity to enter into the procurement contract;
c- Bidders have fulfilled their obligations to pay taxes and social security contributions;
d- Bidders have not been convicted, neither their directors nor employees involved with the procurement process, by a court decision of any criminal offence - even if the verdict can still be appealed - related to their professional conduct or the making of false statements or misrepresentations as to their qualifications to enter into a procurement contract, or corrupting a public procurement or a contract awarding process, or have not been otherwise disqualified pursuant to administrative suspension or debarment proceedings, or have been in a situation of exclusion from participation in public procurements;
e- Bidders are not the subject of legal proceedings for insolvency or bankruptcy, or were declared bankrupt by a court of law;
f- Bidders have not been convicted by a court decision - even if the verdict can still be appealed - of usury or money laundering;
g- Bidders have not participated in the decision-making process of the contracting authority or have any conflict of interest, or any material interest linking them to any of the decision makers;
h- Any other conditions set forth by the contracting authority in the tender documents that are commensurate with the required works;
i- Certificate from the Ministry of Economy proving compliance with the provisions of the Law on Boycott of Israel for foreign companies (added by Law No. 309, dated April 19, 2023).
j- Declaration of the economic beneficiaries (according to Law No. 309, dated April 19, 2023).
4.2 | 2- The bid must be submitted clearly and unequivocally without any deletion, alteration, or modification.
4.3 | 3- The bidders state in their offer that they have reviewed the Tender document and its complementary documents and have obtained a copy. They accept and undertake to adhere to all the conditions outlined therein without any reservations or exceptions. The bidder submits their offer on this basis and affixes financial stamps worth fifty thousand Lebanese pounds covering all the documents.
4.4 | 4- Any bid containing reservations or exceptions is rejected.
4.5 | 5- The bidder mentions in their offer a clear address and place of residence for prompt communication.
Administrative Documents and Transactions | First: Envelope No. (1) Administrative Documents and Transactions
A- General Conditions:
1- Undertaking Letter (Declaration), according to the attached form, signed and stamped by the bidder, this Undertaking includes the bidder's confirmation of their commitment to the price and the validity of the offer. A financial stamp of 50,000 L.L. is affixed.
2- Commercial Circular specifying the authorized signatory of the bidder and a sample of their signature.
3- Legal Authorization: If the offer is signed by someone other than the person authorized to sign according to the commercial circular, it must be notarized by a notary public.
4- Police Record of the Authorized Signatory or his “legal representative”, not exceeding three months from the bid opening date.
5- Partnership Contract legalized by a notary public if required.
6- Registration Certificate before the Directorate of Value Added Tax, if applicable, or a certificate of non-registration if not subject to it. In the latter case, the bidder commits to their bid price even if they become registered for VAT during the execution period.
7- Registration Certificate issued by the Ministry of Finance – Department of Revenue.
8- Certificate issued by the Ministry of Finance proving the bidder's compliance with tax obligations.
9- Clearance Certificate from the National Social Security Fund “comprehensive or valid for participation in public tenders and bids” valid on the date of the bid opening session, stating that the bidder has paid all his subscriptions (the bidder must be registered before the National Social Security Fund and any statement mentioning the phrase “unregistered institution” will be rejected).
10- Certificate issued by the Municipality, proving full payment of municipal fees by the bidder, issued by the municipality within its jurisdiction based on the commercial registration certificate.
11- Comprehensive Certificate issued by the Commercial Register showing founders, members, contributors, or partners, authorized signatories, the manager, capital, the bidder's activity, and ongoing liabilities.
12- Certificate issued by the relevant authorities proving that the bidder is not in a state of bankruptcy.
13- Certificate issued by the relevant authorities proving that the bidder is not in a state of judicial liquidation.
14- Bid bond as required in the specific Tender document of the procurement project, in accordance with Articles 34 and 36 of the Public Procurement Law.
15- Declaration from the Bidder identifying the economic beneficiary/beneficiaries according to Form M18 issued by the Ministry of Finance (any natural person who owns or effectively controls the ultimate outcome of the activity practiced by the bidder, either directly or indirectly, whether the bidder is a natural person or a legal entity.)
16- Copies of Identification Cards (ID/Passport) for the economic beneficiary/beneficiaries.
17- Copies of Identification Cards (ID/Passport) for each person representing the bidder (those acting on behalf of the bidder in their relationship with the contracting authority: legal representative, representative of the legal entity, or authorized signatory).
18- Integrity Declaration Document signed by the bidder in accordance with the prescribed format
Miscellaneous | The bidder shall declare any relative relations with any Alfa employee up to the 4th degree under Clause 30 of the PPL, for MIC1 to be able to assess the existing of any potential conflict of interests which may lead to deprive the bidder from participating to the tender under the risk of disqualification.
The bidder or any of his employees, partners, agents, contributors, consultants, or their relatives shall declare any relationships that may lead to a conflict of interest in the subject of this contract.
Special Conditions | B- Special Conditions Regarding the Subject of the Contract:
Financial Qualifications | 1- Financial Qualifications (To be determined based on the size and nature of the contract).
Technical/Professional Qualifications | 2- Technical/Professional Qualifications (To be determined based on the nature of the contract):
1- Certificate from the Chamber of Commerce, Industry, and Agriculture confirming that the bidder is engaged in the activities related to the subject of the contract, valid as of the date of the bidding session and valid for participation in public tenders.
2- Clearance certificate from the Order of Engineers…
3- Clearance certificate from the Contractors Syndicate…
4- ISO certificate.
5- Five Certificates of good execution and completion for similar projects in terms of size and type.
6- Technical proposal according to the required specifications in the appendix (1) of the RFT.
7- Declaration of site inspection by the bidder, denying any unfamiliarity, according to the attached model.
Participation of a foreign bidder | C- In case of the participation of a foreign bidder, the bidder must comply with one of the following conditions:
1- is part of a coalition that includes at least one Lebanese company that meets the conditions required by the specific Tender document of the procurement project.
2- The personal presence of the legal representative of the company to participate in the procurement proceedings (not mandatory).
3- Has an authorized agent or representative in Lebanon responsible for signing the contract on its behalf.
In addition to the above conditions, the foreign bidder must submit the following:
1- Certificate registration of the company or certificate of establishment issued by the relevant authorities in their country.
2- Certificate from the Lebanese Ministry of Economy and Trade confirming compliance with the provisions of the Law on Israel Boycott.
3- The required certificates according to paragraph (First) above, according to the laws of the country where the bidder is located, provided that these certificates are authenticated according to the regulations of the competent authorities.
For certificates issued without an expiration date, the validity date of each certificate is determined according to its nature, not exceeding six months from the date of the bid opening session.
Information Security Specifications | Information Security Specifications Issuing Department to determine whether all or part of this Article is applicable to their specific RFT
The Bidder shall commit to refrain from offering any product / equipment which can cause security threat or information leakage that jeopardizes MIC1 network security. (K)
The Bidder shall accept that MIC1 runs a vulnerability scan on the proposed solution prior to issuing the acceptance and in case any vulnerability is found, the Bidder undertakes to take the necessary actions to remedy such vulnerability within _____________________ days from its notification.
The Bidder shall mention the security standards adopted/followed in designing the proposed solution.
The Bidder should specify if it has acquired the ISO27001 certification or any other equivalent security certification and submit with the Offer a copy of such certificate.
The Bidder shall not hard code passwords in the proposed solution.
The provided application should run without the need of root (unix) and / or admin (win) privileges.
Source code of proposed application should be owned by MIC1.
System shall allow generation of user, operator as well as alarms logs.
Solution and storage shall be sized to host history logs for at least 1 year back.
The Bidder should submit a data flow diagram and schema of the solution architecture.
In case of online payment, the Bidder shall use encryption. (K)
The Bidder shall harden systems servers / storage before being published online, and describe hardening aspects applied on each type.
The Bidder shall describe security checking and audits performed on the designed solution prior to putting it on the market.
The Bidder shall change default errors / messages and configuration.
Application should support role-based access, specific privileges per user (i.e specific access to application modules and reports)
Database should support restricted access per user or groups to data (i.e access per field or per table, …)
Encryption shall be used in all communications / interactions between systems, especially if the communication is through web access. Web based access shall always be used through HTTP+SSL.
Each user shall have only one account / profile to access data.
Least-privileges should always be specified on nodes / applications.
Pseudocode flow chart shall be provided by the Bidders.
The Bidder should commit to improve solution / systems information security weaknesses whenever needed or highlighted by MIC1 information security team.
Health, Safety and Environmental Specifications | To ensure that the proposed products and services bidders are compliant with HSE culture, bidders should state basic HSE specifications and compliance information:
Bidder shall provide the product’s specifications that have an environmental impact (power consumption, gas emissions, etc…)
Bidder shall provide the product specifications that contribute into preserving the environment (made of recycled material, ozone friendly, low volatile organic compounds, etc…)
Bidder shall provide the product’s specifications that contribute towards the health and safety of the users (ergonomic design, safety features, etc)
Bidder shall state the safety measures being followed by personnel performing the work on Alfa’s sites (ISO45001 certification, specific best practices, etc…).
Bidder shall provide the product’s life cycle data if available.

## Technical Requirements
| RFT Compliance Matrix |  |  |  | Reference Number | SF-CF-25
[5 empty] | Owner | PRO
[5 empty] | Revision Code | 3.0
[5 empty] | Implementation Date | 2024-03-01
Project Name: | JDEIDET DATA CENTER
Reference Number: | 26 32 13.13.DG12 - Diesel-Engine-Driven Generator Sets - 100KVA-LA & Up_10.2023
RFT Article (Part Number or Title) | Requirements (Description) | Killer | Fully Compliant | Partially Compliant | Non-Compliant | Reference (Specify document & page nb)
1 GENERAL
1.1 STANDARDS
A. Equipment and component parts are to comply with:
1. IEC 60085:2007 – Electrical insulation - Thermal evaluation and designation
2. IEC 60034-1:2017 RLV - Rotating electrical machines - Part 1: Rating and performance
3. BS 5514 - Specification for reciprocating internal combustion engines
4. ISO 3046 - Reciprocating internal combustion engines
5. CISPR, AS1359, CSA
6. ISO 8528 - Reciprocating internal combustion engine driven alternating current generating sets
7. ISO 3046-1:2002 - Reciprocating internal combustion engines -- Performance -- Part 1: Declarations of power, fuel and lubricating oil consumptions, and test methods -- Additional requirements for engines for general use
8. NEMA MG 1-22, NEMA MG 1-33
9. UL508A - Standard for Industrial Control Equipment
10. 72/23/EEC, 98/37/EC, 2004/108/EC or equivalent
11. NFPA, ANSI, IEEE
12. DIN Standards and recommendations of ABGSM (Association of British Set Manufacturers) where such standards meet with or supersede the ISO and IEC Standards
B. Manufacturing Standards: ISO 9001 & ISO 14001
1.2 SUBMITTALS
A. The Bidder shall submit all relevant technical data sheets in hard and soft copies. Offer with missing technical data sheets will be disqualified.
B. Documentation – Technical Data Sheets
1. General description and characteristics of engine-generating set, standards with which components comply, site rating and overload capability, overall efficiency, fuel and lubricant consumption at 100%, 75% 50% and 25% of rated load.
2. Description and operating criteria of engine; Type, model, manufacturer, fuel and lubricating oil types and specific consumption, starting conditions and starting periods from cold to full-load pick-up, governor and response characteristics due to sudden load changes, super-charger, fuel injection system and radiator, air filters, fuel filters, oil filters and pumps.
3. Description and operating criteria of generator, exciter and voltage regulator, with loading response and short-circuit characteristics, insulation, cooling and accessories dimensions, weights and forces, mounting methods, vibration protection, etc.
4. Battery type, make, charge / discharge characteristics, capacity and constructional features. Battery charger, method of charging, equalizing and trickle charging.
5. Fuel pipes and accessories; Materials and construction and supports.
6. Cooling air flow system and silencers; Materials, construction and supports.
7. Cool instruments, protection, alarms, cut-outs, indicating lamps, indicating instruments and all other devices or components.
8. Engine/generator control panel: make and type of meters and controls.
9. Engine noise level in dB at full frequency spectrum.
10. Calculated noise levels in dB at typical points within engine room and at various locations inside and outside.
11. Vibration isolation analysis and vibration isolating material.
12. Performance characteristics based on standard conditions of 100 KPA and 40°C.
13. Wiring diagrams showing interconnection points of all electrical components.
14. Operating instructions:
a. Automatic starting and transfer to load and back to normal power, including time in seconds from start of cranking until unit reaches rated voltage and frequency.
b. Manual starting.
c. Automatic shutdown.
C. Certificates
1. Factory test results (sample copy should be submitted with the offer whereas the final copy shall be submitted upon delivery)
2. Certificate of origin (sample copy should be submitted with the offer whereas the final copy shall be submitted upon delivery)
3. ISO certificate of generator assembler
4. ISO certificate of local supplier
D. Operation and maintenance manuals
1. Operation instructions: including description and illustration of all switchgear controls and indicators and engine and generator controls
2. Parts Book: illustrating and listing all assemblies, sub-assemblies and components, except standard fastening hardware (nuts, bolts, washers, etc.).
3. Preventative maintenance instructions: on the complete system that covers daily, weekly, monthly, bi-annual and annual maintenance requirements and includes a complete lubrication chart.
4. Troubleshooting chart - covering the complete generator set showing description of trouble, probable cause, and suggested remedy
5. Recommended spare parts list - showing all consumables anticipated shall be required during routine maintenance and test.
6. Wiring diagrams and schematics - showing function of all electrical components.
7. Maintenance materials
a. Fuel filters replacement elements.
b. Lube oil filter replacement elements.
c. Air cleaner filter elements.
d. Set of fuses for control panel.
e. Battery hydrometer
1.3 TESTING
A. Factory Testing
1. Factory test of the generator set shall include engine, alternator, control panels, transfer equipment and accessories for performance and proper functioning of control and interfacing circuits.
2. A certificate certifying that these tests have been performed should be submitted. Test procedures shall include:
a. Load test at rated load and power factor (0.8) for a continuous 2 hour time period to observe engine blow by, slobber, combustion gas leaks, inlet air leaks, excessive vibration and unusual noise.
b. Single step 50% load pickup.
c. Transient response and steady state governing.
d. Safety shutdown device testing
e. Voltage regulation
f. Rated power
g. Maximum power (110%)
h. Alternator temperature rise by resistance method.
i. Functional compatibility between generator set controls and transfer switch controls (start, transfer, re transfer, stop, with all time delays).
j. Fuel consumption at ¼, ½, ¾ and full load.
B. Witness Testing at Supplier’s Workshop
1. Witness testing, also known as a Factory Acceptance Test (FAT), shall takes place prior to full site installation and commissioning.
2. EQUIPMENT: Inspect and report any loss equipment upon delivery to site or damage to the Engineer.
3. EARTHING RESISTANCE TESTS: if any are to be carried out to verify specified requirements.
4. LOAD TESTS: are to be carried out at low loads to overload conditions, at various power factors. Measurements are to include voltage and frequency deviations and regulating time under various step-loading conditions, temperature measurements and pressure measurements at various locations, and in accordance with an approved plan under conditions equal to worst site ambient conditions.
5. LOAD BANKS: Provide load banks, of rating equal to 110% of generator power, to carry out complete test cycle of the system under loading and switching conditions necessary to prove compliance with the Specification.
6. TESTS are to include:
a. Insulation measurement.
b. Functional tests for voltage sensing, automatic start and transfer of load as applicable.
c. Operation of engine shut- down and alarm a signaling and indication, under simulated fault conditions.
d. Measurement of vibration transmission to building structure.
7. Test Procedure:
a. Prepare blank forms and check sheet with spaces to record data. At top of first sheet record:
1) Date
2) Generator set serial number.
3) Engine make, model, serial number.
4) Alternator make, model, serial number.
5) Voltage regulator make and model.
6) Rating of generator set kW, kVA, V, A, RPM, Hz.
b. Mark check sheet and record data on forms in duplicate as test proceeds.
c. Submit test results with the Maintenance Manuals.
d. With a portable resistive load bank at 100% rated load of generator, operate set for 8 hours continuously, taking readings at 30 minutes intervals, and followed by 10% overload for 1 hour, without interruption, record the following:
1) Time of reading
2) Running time
3) Ambient temperature in °C
4) Lube oil pressure in KPa.
5) Lube oil temperature in °C
6) Engine coolant temperature in °C
7) Exhaust stack temperature in °C
8) Alternator voltage, Phase L1, L2, L3, L1L2, L1L3, L2L3
9) Alternator current, Phase L1, L2, and L3
10) Power in kW
11) Frequency in Hz
12) Power factor
13) Battery charger current in A
14) Battery voltage
15) Alternator stator temperature in °C
e. Demonstrate automatic starting of set and automatic transfer of load on failure of normal power and transfer on resumption of normal power.
f. Demonstrate automatic cool down and shut down of engine on resumption of normal power.
g. Demonstrate that battery charger reverts to high rate charge after cranking.
h. Demonstrate two-minute total cranking capacity consisting of a minimum of 3 cranks with a time internal of 10 sec between each crank.
i. Demonstrate low oil pressure, high engine temperature and water low level shutdowns.
j. Simulate loss of normal power by de-energizing main distribution feeder breaker. Allow generator to operate with load bank. R-energize main distribution feeder breaker. Note operation of transfer switch and controls during the simulated power failure test.
k. All testing shall conform to testing standards - total of 8 hours.
1.4 SHOP DRAWING
A. Submit drawings for approval including, but not limited to, the followings:
1. Certified manufacturers’ dimensional drawings, templates and installation instructions for equipment and accessories, showing weights and distribution of forces, location, and size of cabling (power and control), piping connections to equipment, and other pertinent data.
2. Plans and elevations of all equipment.
3. Separate unit wiring diagrams, schematics and interconnecting wiring diagrams.
4. Constructional details of bulk fuel storage tanks and daily service tank, including outline drawings showing piping arrangements, connections and dimensions.
5. Complete execution drawings of associated auxiliaries.
B. All protecting device shall show: the Short circuit current value, the voltage drop, the indirect protection function in case of a fault with respect the earthing system.
C. Soundproofing and vibration calculation.
1.5 TOOLS AND INSTRUMENTS
A. Tools and instruments required for normal routine inspection, testing, operations, and general maintenance, as recommended by the manufacturer, should be provided by the supplier.
2 PRODUCTS
2.1 GENERATOR SET
A. Diesel Generator Set shall be manufactured by an ISO certified assembler s per ISO 9001:2015.
B. Preferred brands:
1. Caterpillar
2. Cummins
3. SDMO
4. F.G. Wilson
5. Marapco
6. Genmac
7. or equivalent
C. Net Output Prime Power:
1. 350KVA
D. COMPONENTS: set is to basically consist of diesel engine, brushless synchronous generator with direct flexible coupling to engine and control cubicle.
E. GOVERNING: is to be A1 Class to ISO 3046 or BS 5514, using electronic type governor with limits of speed control as specified.
F. STARTING AND STOPPING: when in the automatic mode the set is to start automatically by a signal sent through an auxiliary contact in the load transfer switchgear. Once generator voltage and frequency are within acceptable limits, the transfer switch shall operate to allow emergency power to be supplied to the emergency loads. Upon return of the normal power the load shall be re transferred to the normal power supply and the engine-generator set shall cool down and stop after an adjustable cool-down period (2-30 minutes). The generators operation shall be rotated such that equal running times are distributed on the generators (in the case one generator fulfils the required load).
G. DUTY: Generator shall start, achieve rated voltage and frequency (speed), and transfer to the load within 10 seconds of start impulse. The generator shall accept immediately 60% of net rated output (load being mixed, steady and inductive, with motor starting loads as shown on the drawings). During the load connection/shedding process, transient voltage variation is not to exceed 10% under any step-load application for which the system is intended, up to full rated load, recovering within +/-2% within a few cycles.
H. FAILURE TO START: Cranking limiter to provide 3 cranking periods of 10 seconds duration, each separated by a maximum rest period of 20 seconds. Should the set fail to start after three attempts, an alarm is to sound and a start failure signal illuminate, while a distinctive alarm is communicated to the ATS panels downstream.
I. HAND OPERATION: is to be possible for testing or normal operation through a Test/Manual/Off/Auto selector switch.
2.2 DIESEL ENGINE
A. Preferred brands:
1. Caterpillar
2. Cummins
3. Volvo
4. Perkins
5. Deutz
6. or equivalent
B. Factory of origin should be indicated.
C. DESIGN: diesel engine is to be designed for type of load and application required. Engine and governor are to be selected to meet operating requirements and response specified.
D. ENGINE TYPE: compression-ignition type with direct solid- injection, turbo-charged after-cooled, in line or V-type cylinder arrangement, 1500 rpm, operating on number 2 diesel oil (distillate), suitable for direct coupling to driven machine. Flywheel is to be suitably sized for type of service and constraints specified (should be enough for a load pick-up capability of 70% of the generator’s rating), and capable of being rotated at 125% of rated speed without failure. Torsional vibration dampers are to be provided. Engine is to be preheated in order to reach 70% of the load in 10 seconds and 100% of the load in 3 minutes.
E. ACCESSIBILITY: it shall be possible to:
1. Remove rocker-box covers without disturbing fuel injection pipes or other components.
2. Remove and replace pistons and rods, liners, big and small end shells and caps without decoupling engine.
3. Bar engine over by hand for spill timing check and adjustment.
F. COOLING SYSTEM: engine is to be water cooled with gear-driven water pumps. System is to be pressurized, with heavy-duty tropical radiator cooled by reverse flow fan. Fan cowl and hand protection guard are to be fitted. Coolant temperature is to be controlled by one or more thermostats as determined by design of system. Radiator is to be sized for continuous performance at 110% rated load at worst operating ambient conditions with a 40°C temperature differential. Radiator is to be non-ferrous metal, incorporating pressure valve, and radiator cap and drain cock and with integral expansion tank; Direct acting modulating thermostatic diversion valve is to control engine cooling water and anti-corrosion additives are to be used as recommended by manufacturer for specific conditions of installation.
G. ANTIFREEZE: Antifreeze coolant of 50% ratio should be added to the radiator water.
H. COOLING AIRFLOW: obstructions in path of cooling airflow (openings, louvers, grilles, mesh, ducts, bends, etc.) are not to reduce airflow below that needed at full rated output. Fan and radiator characteristics are to be selected accordingly. Advise if additional booster fans are required and provide necessary control gear for automatic operation.
I. LUBRICATING OIL SYSTEM: pressurized circulating type, using engine-driven, gear type lubricating oil pumps with full flow filters and replaceable elements and lubricating oil heat exchanger. Filter system is to have spring load by-pass valve to permit oil circulation if filters become clogged. Audible and visual alarms are to cut-in when valve starts opening. Lubrication oil cooler is to be shell and tube heat exchanger with water from engine radiator as the cooling medium. Direct acting thermostatic diversion valve is to control oil temperature. Under normal operation by-pass is not to be fully closed. Engine shall have an oil level indicator, oil pressure gauge and low oil pressure shutdown switch.
J. FUEL SYSTEM: is to have injection pump and injectors that are easily removable and replaceable for servicing. Engine is to have integral, gear type engine driven transfer pump to lift fuel against a head of 2.5m and supply it through filters to injection pump at constant pressure. Fuel filter elements are to be easily replaceable.
K. COLD STARTING: engine is to be fully equipped to start and pick up initial load specified at 0°C ambient temperature. Cold starting aids, such as engine jacket water heater, lubricating oil heater, intake-air heater, oversize standby battery and all devices, accessories, connections, thermostatic switches and off-duty disconnects with pilot lights and necessary protection, are to be supplemented as recommended by the manufacturer and approved.
L. AIR INTAKE SYSTEM: Engine air filter is to be either dry filter with replaceable paper filter elements or oil-bath filter dipstick and provision for adding oil while engine is running. Filters are to be capable of removing particles 10 microns and larger.
M. ELECTRIC STARTING SYSTEM: engine starting shall be manual by push-button or automatic through control system at control panel. System shall consist of heavy duty 24 V DC starter motor, heavy duty battery and battery charger. Cranking motor and battery are to be rated for cranking the engine when cold and at lowest temperature recorded. Starting pinion is to automatically disengage when engine fires.
N. GOVERNOR OVERSPEED TRIP: is to automatically close fuel pump racks in event of engine over-speed. Device is to be separate and independent from governing mechanism.
O. PROTECTIVE SYSTEM: is to comprise automatic engine shutdown and generator trip with visual and audible alarm in event of over-speed, low lubricating oil pressure, high cooling water temperature and over cranking.
P. Guards shall be integrally mounted on unit to protect personnel from hot and moving parts.
2.3 ELECTRONIC GOVERNOR
A. Governor is to have zero percent (isochronous) setting and adjustable drop from zero percent to 10% drop. System is to include power supply unit, magnetic speed pick-up, control module and actuator using fast response DC motor drive or equally approved alternative.
B. Governor is to be designed for fast-response and high-precision of speed (frequency) control and is to include speed adjustment to +/-5% of normal, while running, and with remote control interface. Frequency deviation under 25% sudden load change is not to exceed 1 Hz, recovering to stable speed condition of +/-0.1 Hz in 1 second.
2.4 ALTERNATOR
A. Preferred brands:
1. Leroy Somer
2. Caterpillar
3. Stamford
4. Marelli Motori
5. or equivalent
B. Factory of origin should be indicated.
C. GENERATOR RATING
1. PRIME RATED POWER (PRP): ISO 8528-1 – The maximum power which a generating set is capable of delivering continuously whilst supplying a variable electrical load when operated for an unlimited number of hours per year under the agreed operating conditions with the maintenance intervals and procedures being carried out as prescribed by the manufacturer. The permissible average power output over 24 hours of operation shall not exceed 70% of the PRP rating. A 10% overload is available but limited to 1 in 12 hours and not to exceed 25 hours per year. The 10% overload is available in accordance with ISO 3046-1.
D. TYPE: synchronous, low reactance, high efficiency, revolving field type, with brushless exciter and flexible coupling, sized to pick up effective load without exceeding transient and steady-state voltage deviation limits specified up to its full nominal rating and designed for the performance stipulated in the specification. It is to be single bearing construction with bearing type sleeve or sealed ball.
E. LEADS AND CABLES: phase leads are to be brought out fully insulated to a terminal cables box of heavy gauge sheet steel, protection IP44 to IEC 529. Control and protection cables are to be brought out to a separate terminal box.
F. MAXIMUM VOLTAGE DIFFERENCE: between the three phases at 100% balanced load is not to exceed 1%. With unbalanced load up to 30% on one phase at unity power factor and zero loads on other phases, the line-to neutral voltages are not to differ by more than 5%.
G. CHARACTERISTICS:
1. Number of phase: 3
2. Rated voltage, Frequency: 380Vac, 50Hz
3. Rated power factor: 0.8
4. Winding connection: re-connectable with ends brought out and fully insulated
5. Unbalanced load current with none of the phase currents exceeding rated current: 30% minimum
6. Overload: 10% nameplate rating for 1 hour every 12 hours
7. Rotor: Salient pole type, incorporating damping grid.
8. Excitation: brushless, with rotating armature rectifiers and discharge resistors.
9. Voltage regulator: automatic with an adequate filter such that THD (Total Harmonic Distortion) is less than 4% under non-linear load together with readily accessible controls for voltage level.
10. Insulation: class H for stator, class H for Rotor and exciter.
11. Enclosure: drip proof and screen protected (IP 23 to IEC 529)
12. Cooling: built-in centrifugal fans
H. VOLTAGE REGULATION: overall voltage deviation within normal speed variations is to be within limits specified from no-load to full-load, from hot to cold and with load power factor from 0.8 lagging to unity. Regulator is to automatically reduce voltage if load exceeds capacity of generator. Voltage build-up is to be positive and rapid even when full load is suddenly applied. Line-to-line voltage wave-from deviation factor is not to exceed +/-5%. Total harmonic content is not to exceed 4%. Radio interference suppression grade is to be within the limits set by the Standards; better than grade (N).
I. EXCITER: armature is to be 3-phases, directly mounted to generator shaft and connected to generator field windings through six solid state, hermetically sealed, silicon rectifiers, accessible for maintenance or repair. Exciter is to have field suppression system to eliminate any source of diode failure resulting from high inductive loads and surges. Exciter field windings are to be stationary. Exciter-regulator combination is to maintain output voltage within limits specified for any load up to 110% generator rating and under any sudden load changes specified.
2.5 AUTOMATIC VOLTAGE REGULATOR
A. Solid state, volts/Hz type, utilizing silicon semi-conductor devices in control and power stages, with built-in electro-magnetic interference suppression and designed for singles or parallel operation.
C. Optional manual adjustment to +/-5% of regulated voltage level is to be possible.
D. All components are to be sealed, moisture and heat resistant, with a suitable environmentally protected enclosure.
E. Voltage regulator is to automatically reduce voltage if load exceeds capacity of generator and is to sustain a 3-phase short-circuit current at the generator terminals for the period for which the short-circuit protection operates and at least for 3 seconds.
F. The voltage regulator has to monitor the 3-phases outputs.
G. The AVR should be powered by two auxiliary windings which are independent of the voltage match circuit. The first winding has a voltage in proportion to that of the alternator (characteristic Shunt), the second has a voltage in proportion to the stator current (compound characteristic: Booster effect).
H. The power supply voltage is rectified and filtered before being used by the AVR monitoring transistor.
I. Voltage regulator power is to be supported by a permanent magnet to maintain excitation field power (PMG).
2.6 PERMANENT MAGNET GENERATOR
A. A Permanent Magnet Generator (PMG) shall provide excitation power to the AVR to provide immunity from voltage distortion from non-linear loads.
B. The PMG produces an AC current proportional to the speed, used as field excitation power by the AVR.
C. With PMG excitation, the permanent magnet generator (PMG) added to the alternator supplies the AVR with voltage which is independent of the main alternator winding. The AVR monitors and corrects the alternator output voltage by adjusting the excitation current.
D. Machine short-circuit current capacity of:
1. Option A: 2.7 IN for 5s
E. The PMG assembly forms a rotating part which can be fitted at the rear of the alternator as required.
F. Operating temperature: - 20°C to + 70°C
2.7 CONTROL PANEL
A. Provide a unit mounted control console that is factory built, wired, tested and shock-mounted by the unit manufacturer. Control console shall be a rigid, ‘sprinkler proof’, metal enclosure, mounted on the generator end of the set, containing all devices as specified herein, and as required for described functions. Control console shall include a control section and control panel with required access to all components. Control wire shall have termination identification on each wire for ease of tracing. Control wires which run between generator set controls and automatic transfer switches shall have identical termination identification on both ends. Aluminum nameplates shall be provided to identify each device or function.
B. Approved brands:
1. Woodward
2. Deep Sea Electronics
3. Or Equivalent
C. Control panel shall consist of the following control boards:
1. Standard manual start board with low coolant protection
2. Remote start board equipped with USB, RS485 & RS232 ports
3. Standard manual start board shall override the remote start board only when the remote start board fails
D. A real-time clock for date and time stamping of diagnostics and events in the control’s logs as well as service maintenance reminders based on engine operating hours or calendar days.
E. Set points & software to be stored in nonvolatile memory, preventing loss during a power outage.
F. True RMS sensing ensures AC metering accuracy to within ± 1% of rated AC voltage (L-L and L-N) and current. KW and KVA metering to within ± 5% of rating.
G. Voltage set to LN 220Vac / LL 380Vac at no load.
H. Frequency set to 50Hz at no load
I. Controls:
1. Engine Run-Stop-Auto switch
2. Engine emergency stop button with provision for remote emergency stop button.
3. Lamp test switch and reset switch.
4. Voltage adjusting control
5. Frequency adjusting control
6. Engine Cool-Down timer adjusting control
7. Engine Cycle Cranking
8. Engine Speed/Generator Frequency adjusting control
J. Digital (LCD) Indication
1. Generator AC Voltage – 3 phase (L-L & L-N)
2. Generator AC Current (per phase & average)
3. Generator Power kW (total & per phase)
4. Generator KVAR (total & per phase)
5. Generator KVAR-hr (total)
6. Generator % of rated power (total) (KW, KVA, KVAR)
7. Generator KVA (total & per phase)
8. Generator KW-hr (total)
9. Generator Power Factor (PF) (average & per phase)
10. Generator Frequency
11. Engine RPM
12. Battery Voltage
13. Engine Hours
14. Engine Successful Start Counter
15. Engine Oil Pressure
16. Engine Coolant Temperature
17. Engine Crank Attempt Counter
18. Service Maintenance Interval
19. (Engine Operating Hours or Calendar Days)
20. Real Time Clock
21. Twenty (20) Event Fault Log
K. Automatic shut-down lights and alarms
1. Over-crank (shutdown after 3 cranking attempts)
2. Engine over speed (shutdown at 115%)
3. High engine temperature (shutdown at 120%)
4. Engine - low lube oil pressure (shutdown at 40%)
5. Short circuit and over current
6. Loss-of-field protection
7. Negative phase sequence protection
8. Low coolant temperature (alarm at 20°C to 30°C)
9. Low coolant level
10. High/Low Battery Voltage
11. Auxiliary contact for “not in auto” (alarm)
12. Emergency Stop Activated
13. No battery voltage: provide a separate relay audible device and 240V AC power source.
14. Alternator over voltage and under voltage (shutdown at 110% and 90% sustained for 3 seconds)
15. Common alarm dry contacts NCO (connect to NOC)
16. Warning condition activates common alarm output signal and common flashing yellow indicating lamp
17. Shutdown condition activates common shutdown output signal and common flashing red indicating lamp
18. Warning/Shutdown conditions result in text message in the display event log
L. Digital Inputs
1. Emergency Stop
2. Remote Start
3. 3 Programmable
2.8 COMMUNICATION
A. User configurable communication through:
1. USB
2. RS232
3. RS485
B. Fully configurable using PC software via USB
C. Remote SCADA monitoring
D. MODBUS RTU & TCP support
E. User configurable MODBUS pages
2.10 PROTECTION AND CONTROL EQUIPMENT
A. GENERATING SET INSTRUMENTS, PROTECTION AND CONTROLS: control relays, sensing equipment, switchgear protective relays and devices and start, stop and shutdown controls are to be provided as necessary for operation specified. Generating set, instruments, protection, and controls are to be mounted preferably in one control cubicle.
B. PROTECTIVE GEAR: is to ensure orderly engine stop or shutdown with reset relays, as required for safety and operational reliability, and is to include the following:
1. Output circuit breaker (MCCB), with generator specific solid-state trip unit, Type:
b. Merlin Gerin NS630N, 4 poles, 4D, with Micrologic 5.0 for 350KVA or equivalent
C. Neutral of generator, at the CB incoming side, shall be earthed by an insulated conductor green/yellow of the same cross-section of the power conductors to the earth bar.
D. Automatic Control Components:
1. Generator main circuit breaker as specified and generator protective relays.
2. Electronic governor control.
3. First start sensor for monitoring the voltage and frequency of the genset as it is starting.
4. Pulse alarm system to sound alarm at first fault and each additional fault.
5. DC Voltage sensor with time delay monitor for starting battery system.
6. The status of the generator’s breaker shall be monitored such that if it is open or tripped an alarm signal is sent to the ATS panels downstream.
E. CURRENT RELAYS: front adjustable, sealed type, with dust-tight enclosures, removable covers, test terminal blocks and plugs for testing relay without removal from case. Removal from casing is to automatically short-circuit respective current transformer secondary windings.
F. INSTRUMENTS: are to be housed in enameled metal cases for switchboard flush installation, with scales and markings protected and sealed. Including meters are to be minimum 76 mm square. Accuracy is to be within 2% unless otherwise specified. Voltmeters and moving coil type for D.C. measurements.
G. CURRENT TRANSFORMERS: class 1 for measuring and protection.
2.11 STARTER BATTERY
A. Battery country of origin should be indicated.
B. Lead-acid, sealed-in-plastic type, and inter-cell connectors.
C. Battery should have sufficient capacity to crank engine for 3 minutes at 0°C without using more than 25% of ampere-hour capacity. Calculation notes should be submitted to confirm the above.
D. Battery capacity in AH should be indicated.
E. Battery cold cranking current (CCA) according to SAE (Society of Automotive Engineers) standard should be indicated.
F. Fixed to corrosion resistant mounting rack with fasteners.
2.12 BATTERY CHARGER
A. Rating: 10 Amps at 24Vdc
B. Country of origins should be indicated.
C. Description: 25% over-rated, solid state, full-wave rectifier type, adequate to fully recharge depleted battery in not more than 8 hours and to automatically control rate of charge (providing a high-charge rate to a depleted battery and reducing to a trickle-charge rate when battery is fully charged).
D. Ammeter is to be provided to indicate charging rate, which is to be adjustable.
E. Battery is to be mounted in control cubicle, unless otherwise approved.
F. The charger is to monitor the battery and an alarm signal (dry contact NCO) shall be sent to the NOC in case of battery or charger breakdown.
2.13 FUEL HOSES
A. Hydraulic flexible hoses for connecting fuel lines to engine should be of high pressure (20bar).
B. Hydraulic flexible hoses should be of minimum length of 125cm, fitted on both sided with male pressed connector.
2.15 ENGINE COOLANT HEATER
A. Engine mounted, jacket water heater type, thermostatically controlled, 220V AC, single phase power liquid coolant heaters shall allow engine to start in room ambient temperature of 0°C.
B. Ball valves, of industrial type, should be provided on both ends in order to isolate the jacket water heater in case of defect.
2.17 ENGINE EXHAUST SYSTEM
A. Muffler
1. Critical type, sized as recommended by engine manufacturer.
2. Rated sound level reduction of 37 dBA or more in order to ensure 63±2dBA at 1m.
B. Connections from Engine to Exhaust System: Flexible section of corrugated stainless-steel pipe.
C. Connection from Exhaust Pipe to Muffler: Stainless-steel expansion joint with liners.
D. Insulation for Mufflers: 10 cm rock wool.
E. Supports for Muffler: Spring hangers and all-thread rods and vibration hangers with approved masonry expansion bolts, minimum 14 mm diameter and installed in accordance with manufacturer’s instructions and attached to building structure.
2.18 NEUTRAL CONNECTION
A. TN-S shall be adopted for the generator power supply.
B. Neutral of generator, at the CB input side, shall be earthed by an insulated conductor green/yellow of the same cross-section of the generator power conductors and to the generator earth bar.
2.19 EARTH BAR
A. Earth bar dimensions: 200x50x5mm fixed to generator metallic main frame by threaded rods.
2.20 SOUND PROOF CANOPY
A. A weatherproof canopy to house the diesel generator that complies with a minimum IP 34 rating
B. Submittals
1. Canopy drawing in Autocad format
2. Sound study
3. Ventilation study
C. Two canopy models:
1. Model NC55: Shall ensure a sound level of 63dBA ± 2dBA at 1m from source from all directions, at 100% load, according to noise criteria NC-55 as per table below:
D. Exhaust pipe and muffler inside the canopy shall be rock wool insulated and protected with a cover of 1x1cm wire mesh.
E. Muffler exhaust pipe should be extended 20cm outside the canopy
F. Radiator to canopy canvas should be minimum 5cm width and made of a cloth tissue and not of rubber joints.
G. Construction
1. Freestanding enclosure constructed from carbon steel sheets lined with sound absorbent material designed to accommodate engine-alternator and control panel.
2. Fitted with 4 doors, two doors on each side
3. Service doors at each side, rotating on hinges, for inlet and outlet attenuators for easy service.
4. Hinges should be of heavy duty welded type
5. Unit body is made of Carbon Steel Cold Rolled Sheet Metal with structure beam where necessary.
6. Inlet and Outlet attenuators at the Engine and alternator ends provide ample air flow to insure proper cooling with maximum 8 m/s air speed @ the total air flow quantity generated by the engine and alternator cooling fan.
7. Fixed blades weather louvers constructed from carbon mild sheets
8. High density sound proofing rigid boards fiber of density and thickness required to reduce external sound pressure to the level required
9. Opening passages for oil drain, fuel pipes, breather, and cables are located according to the required position of installation. Opening passages are labeled on the outside canopy body.
10. Wall thickness: 10 cm
11. Thickness of outer skin: minimum 2mm to 3mm
12. Battery can only be reached via lockable access doors
H. Internal flexible exhaust pipe
I. Paint
1. All the material is treated with corrosion resistant and enhanced by a phosphate chemical conversion coating which provides an excellent corrosion resistant surface.
2. The metal components are then painted by applying an epoxy polyester paint which is subjected to high temperatures and form a continuous, high gloss and extremely durable coating
3. Color code: RAL 7015
J. Locks
1. Provide welded heavy duty sliding latch, for each canopy door, lockable with padlock.
2. Padlock hole diameter should be 10mm.
3. Padlocks will be supplied by MIC1.
3 MAINTENANCE CONTRACT
A. Obtain an undertaking by the equipment manufacturer and his authorized local representative to provide an annual maintenance contract, available after substantial completion of the work, covering routine service and emergency service by trained employees, and to ensure supply of necessary standard spare parts.
B. The authorized local representative shall be apt to provide a variety of maintenance services that are vital for the customers to get the best possible reliability, performance and productivity from their equipment.
C. Services shall include but not limited to:
1. Customer Service Agreements (CSA)
a. Full Equipment Maintenance
b. Full Equipment Repair
c. Equipment Testing / Analysis
d. 24-hour Service Availability & Response
2. Selective engine repair program (SER):
3. Preventive engine maintenance program
4. Scheduled oil sampling (SOS): Oil samples taken from various machine compartments are tested in a specialized SOS lab. By analyzing the results, problems can be detected in advance and before costly failures.
5. Custom Track Service (CTS): Custom track service is performed with special ultra-sonic measuring instrumentation to detect undercarriage wear patterns. CTS indicates turning intervals for pins and bushings when needed in order to prolong the operation life of the tracks.
6. Six (6) month warranty on all repairs
7. Field service dispatching / response within 24 hours.
D. The bidder shall also offer the following:
1. Training Programs for the customer free of charge
2. Lifetime Equipment Estimation
3. Preventive Maintenance Scheduling
4. Equipment Owning and Operating Cost Analysis
END OF SECTION

## Commercial Requirements
| RFT Compliance Matrix |  |  |  | Reference Number | SF-CF-25
[5 empty] | Owner | PRO
[5 empty] | Revision Code | 3.0
[5 empty] | Implementation Date | 2024-03-01
Project Name:
Reference Number:
RFT Article (Part Number or Title) | Requirements (Description) | Killer | Fully Compliant | Partially Compliant | Non-Compliant | Reference (Specify document & page nb)

## Grade of Compliancy
| RFT Compliance Matrix | Reference Number | SF-CF-25
|  | Owner | PRO
|  | Revision Code | 3.0
|  | Implementation Date | 2024-03-01
Grade of Compliance range from 0 to 15 with a step of 1 unit:
15 : Compliant with additional value, not initially included in the requirements
10 : Fully compliant
4 - 5 - 6: Partially compliant
0 : Not compliant
K : Disqualification