## BOQ
Mobile Interim Company 2 S.A.L
MIC 2
Civil works on existing sites (Estimated BOQ)
Various sites
# | Description | Unit | Estimated Qty | U/Price | Total
1 | Horch Tabet S81 (RT,1G) 12 floors
1 | Supply & installation of cable tray 22cm with cover to replace damaged/rusty ones;including removing cables, remove the old tray and cable re-installation,on blocks. | L.m | 14
2 | Repair for waterproofing membrane by removing the old one and apply 3 coats of PU liquid membrane (roof & parapet); including all preparation works (slabs edges repair,cleaning,removing debris,unused poles, antennas,drains repair,cracks treatment,closing and sealing tray path by tiling,screed,...,....).All complete with testing & guarantee. | M2 | 75
3 | Replacement for the damaged Shelter stairs by new one.(150x100)cm Details:platform 100x80cm,stairs landing 25cm, ,H=88cm,plates 8mm as stairs feet,made up of UPN beams 10cm and checkered plates 3mm.All complete with paint. | each | 1
4 | Painting repair for shelter HEA beams (estimated 20m) | L.S | 1
2 | Movenpick S156 (seaside)
1 | Replacement for the damaged/rusty supports of radio/MW sector (one radio antenna,one MW antenna,RRUs,cables) Works include new 6m mast,4" wall mounted,new offset for MW antenna,new support for RRUs;dismantling of old material & re-installation.Special protection paint for masts. | L.S | 1
2 | Supply & installation of cable tray 10cm with cover including cabling arrangement & special protection paint for tray. | L.m | 12
3 | Gemmayzeh S959 (RT,1G on roof) 10 floors (relocation of generator)
1 | Dismantling from roof of generator with silencer (with its related installations) (ATS,Stabilizer,2 FT,2 HEA beams, refueling pipe 40m,trays,cables,blocks) & re-install on GF level with all related items & connections (ATS,stabilizer, power,control & ground cables,sylomer pads,..).All remaining material to be transported to MIC2 warehouse. Minor repairs of (paint,sealing) in the dismantled areas. | each | 1
2 | Supply & installation of FT (to be fit in the dedicated area) ,presumeably (100x50x200)cm,with related accessories & installations (pipes,leveling sensor,tray,paint,…) (as per MIC2 requirement) | each | 1
3 | Supply & installation of exhaust system (HDG pipes,3",4mm thickness,antivibration supports each 3m along the building wall to roof,needed flanges,drains,valves,locks,connection to cyclon filter on roof),works include new cyclon filter on roof (filter to be fixed on blocks,with underneath area made up of membrane & gravel layer 10cm thickness),filter outlet 150cm directed as on site recommendation. | L.m | 36
4 | Aamchit Coast S569 (RT,1G on roof) 4 floors (relocation of generator)
1 | Reinforced Concrete for generator area (500x450)cm including preparation works (excavation,remove un-necessary material,clean up,..) | M3 | 5
2 | Steel tent (MIC2 specs) with roofing made up of resin sheets 3mm.(brick type) | M2 | 20
3 | Steel fence & gate (MIC2 specs) | M2 | 40
4 | Dismantling from roof of generator with silencer (with its related installations) (ATS,Stabilizer,1 FT,HEA beams, refueling pipe 24m,trays,cables,blocks) & re-install in garden area (-3mm level) with all related items & connections (ATS,stabilizer, power,control & ground cables,sylomer pads,..).All remaining material to be transported to MIC2 warehouse.Minor repairs of (paint,sealing) in the dismantled areas. | each | 1
5 | Transportation & installation of FT,with related accessories & installations (pipes,leveling sensor,tray,paint,…) (as per MIC2 requirement) | each | 1
6 | Supply & installation of exhaust system (HDG pipes,3",4mm thickness,antivibration supports each 3m along the building wall to roof,needed flanges,drains,valves,locks,connection to cyclon filter on roof),works include new cyclon filter on roof (filter to be fixed on blocks,with underneath area made up of membrane & gravel layer 10cm thickness),filter outlet 150cm directed as on site recommendation. | L.m | 20
5 | Mazraat El Daher S1540 (RT,1G on roof) 4 floors
1 | Repair for waterproofing membrane by removing the old one and apply 3 coats of PU liquid membrane (roof & parapet); including all preparation works (slabs edges repair,cleaning,removing debris,drains repair,cracks treatment,screed,...,....).All complete with testing & guarantee. | M2 | 75
TOTAL