## BOQ-Port of Tripoli
Port of Tripoli Tender documents
PV installation- Tender No RS-B22/0111 January 2023
Bill of quantities- Photovoltaic system
Item No. | Description | Unit | Quantity | Unit price USD | Total price USD
I- | PHOTOVOLTAIC SYSTEM
Supply, transport, install and connect complete high end hybrid solar photovoltaic system with batteries including all specified (BOQ & drawings) equipment, but not limited to items specified
Regulatory compliance: IEC 61724; IEC 61727; IEC 61730; IEC 61829; IEC 61345; IEC 61215; UL Standard 1741
The Photovoltaic System Design is for tender purposes, the contractor shell verify the conformity of design and present shop drawings for approval.
I-1- | System 1: Port of Tripoli - zone 1 - Entrance check point
I-1-A | Supply and install photovoltaic panels 550Wp as indicated in the specs , Austa, longi, Philadelphia or other equal and approved | Nr. | 60 |  | 0
I-1-B | Supply solar panels 550Wp same brand as spare part on site. | Nr. | 6 |  | 0
I-1-C | Supply and install Aluminum anodized Structure, thickness 2mm, aluminum rails 41x41mm, railed mount profile as specified. | Item | 60 |  | 0
I-1-D | Supply and install Tie-grid inverter 40kw as specified, Brand Huawei, GoodWe or other equal and approved. | Nr. | 1 |  | 0
I-1-E | Supply and install Fuel save controller Deif or approved equal. | Nr. | 1 |  | 0
I-1-F | Supply and install cables, MC4 connectors , fuses, cable trays, rigid PVC conduits, and all needed accessories as mentioned in the single line diagram and as per international standards- European Brand; Distance between solar modules and inverter room is around 25m, and Distance between inverter room and electrical room is around 20m | Item | 1 |  | 0
I-1-G | Supply and install combiner box including but not limited to breakers, contactors, surge arrestors, fuses, busbar, and all needed accessories as mentioned in the single line diagram and as per international standards-Brand Schneider, Dehn or other equal and approved. | Item | 1 |  | 0 | 350
I-2- | System 2: Port of Tripoli - zone 2 - Administration area
I-2-A | Supply and install photovoltaic panels 550Wp as indicated in the specs , Austa, longi, Philadelphia or other equal and approved | Nr. | 90 |  | 0
I-2-B | Supply solar panels 550Wp same brand as spare part on site. | Nr. | 10 |  | 0
I-2-C | Supply and install Aluminum anodized Structure thickness 2mm, aluminum rails 41x41mm, ballasted type triangular low profile as specified. No drilling allowed on the roof | Item | 90 |  | 0
I-2-D | Supply and install Tie-grid inverter 60kW as specified. Brand Huawei, GoodWe or aproved equal | Nr. | 1 |  | 0
I-2-E | Supply and install Fuel save controller Deif or other equal and approved. | Nr. | 1 |  | 0
I-2-F | Supply and install cables, MC4 connectors , fuses, cable trays, rigid PVC conduits, and all needed accessories as mentioned in the single line diagram and as per international standards- European Brand. Distance between solar modules and inverter room is around 220m, Distance between inverter room and main electrical board is around 20m | Item | 1 |  | 0
I-2-G | Supply and install combiner box including but not limited to breakers, contactors, surge arrestors, fuses, busbar, and all needed accessories as mentioned in the single line diagram and as per international standards-Brand Schneider, Dehn or other equal and approved. | Item | 1 |  | 0
I-2-H | Supply and install batteries (12v, 9amp) for UPS server - Brand PCE, KONIC, Sky Gate or other equal and approved. | Nr. | 96 |  | 0 | 87500
I-2-I | Test, inspect and repair the existing ups server (Brand Schneider - APC) to put it in good order | Item | 1 |  | 0
I-3- | System 3: Port of Tripoli - zone 3 - Sea Side
I-3-A | Supply and install photovoltaic panels 550Wp as indicated in the specs , Austa, longi, Philadelphia or other equal and approved | Nr. | 90 |  | 0
I-3-B | Supply solar panels 550Wp same brand as spare part on site. | Nr. | 10 |  | 0
I-3-C | Supply and install Aluminum anodized Structure thickness 2mm, aluminum rails 41x41mm, ballasted type triangular low profile as specified. No drilling allowed on the roof | Item | 90 |  | 0
I-3-D | Supply and install Tie-grid inverter 60kW as specified. Brand Huawei, GoodWe or aproved equal | Nr. | 1 |  | 0
I-3-E | Supply and install Fuel save controller Deif or other equal and approved. | Nr. | 1 |  | 0
I-3-F | Supply and install hybrid inverter 5kW as specified. Brand Growatt, Felicity or other equal and approved. | Nr. | 2 |  | 0
I-3-G | Supply and install lithium ion batteries 200AH, 48V equivalent to Blue Carbon, Felicity solar, Sako or other equal and approved | Nr. | 4 |  | 0
I-3-H | Supply and install cables, MC4 connectors , fuses, cable trays, rigid PVC conduits, and all needed accessories as mentioned in the single line diagram and as per international standards- European Brand. Distance between solar modules and inverter room is around 70m ; Distance between inverter room and electrical room is around 15m | Item | 1 |  | 0
I-3-I | Supply and install combiner box including but not limited to breakers, contactors, surge arrestors, fuses, busbar, and all needed accessories as mentioned in the single line diagram and as per international standards-Brand Schneider, Dehn or other equal and approved. | Item | 1 |  | 0
II- | EARTHING & LIGHTNING SYSTEM (As per specifications and B.O.Q.)
Supply, install and connect earthing systems including earth rods, 2.4m long and 2 cm diameter, (Similar to Copper weld or Furse) to provide low connecting earth resistance (<5 Ohms), earth stranded bare copper conductor for earthing network (as specified), earth pits, connectors, clamps, test links, earth bar, excavation and backfilling as mentioned on drawings. The earthing system has to be installed for a perfect operation and to the satisfaction of the engineers- European brand
II-1 | Supply and installation of earthing network for the electrical system for system 1 | Item | 1 |  | 0
II-2 | Supply and installation of lightning protection system LPS to cover an area of 60m radius for system 1 | Item | 1 |  | 0
II-3 | Supply and installation of earthing network for the electrical system for system 2 | Item | 1 |  | 0
II-4 | Supply and installation of lightning protection system LPS to cover an area of 60m radius for system 2 | Item | 1 |  | 0
II-5 | Supply and installation of earthing network for the electrical system for system 3 | Item | 1 |  | 0
II-6 | Supply and installation of lightning protection system LPS to cover an area of 60m radius for system 3 | Item | 1 |  | 0
III- | ELECTRIC NETWORK MODIFICATION - Zone 1 (As per specifications and B.O.Q.)
A- Zone 1 - Entrance check point
III-A-1 | Supply , install ,connect and test a diesel generator of 60 KVA to be connected to system 1 , complete with protection and control devices and panels control cables, sound proofers, silencers, mufflers, supports, concrete base antivibration system , batteries ,battery chargers, conductors, with all necessary accessories and exhaust systems with insulating materials, necessary link to earth system, etc ...all as specified and to the satisfaction of the Engineers. Cummins, Volvo, Iveco or other equal and approved. | Item | 1 |  | 0
III-A-2 | Modifications on electric power panels to link EDL, generator and solar PV system in system 1 with all accessories needed such as ATS 100A (European Brand) | Item | 1 |  | 0
B- Zone 2 - Administration area
III-B-1 | Supply , install ,connect and test a diesel generator of 120 KVA to be connected to system 2 , complete with protection and control devices and panels control cables, sound proofers, silencers,mufflers, supports, concrete base antivibration system , batteries ,battery chargers, conductors, with all necessary accessories and exhaust systems with insulating materials, necessary link to earth system,etc ...all as specified and to the satisfaction of the Engineers. Cummins, Volvo, Iveco or other equal and approved. | Item | 1 |  | 0
III-B-2 | Modifications on electric power panels to link EDL, generator and solar PV system in system 2 with all accessories needed such as ATS 200A (European Brand) | Item | 1 |  | 0
C- Zone 3 - Sea Side
III-C-1 | Supply , install ,connect and test a diesel generator of 100 KVA to be connected to system 3 , complete with protection and control devices and panels control cables, sound proofers, silencers, mufflers, supports, concrete base antivibration system , batteries ,battery chargers, conductors, with all necessary accessories and exhaust systems with insulating materials, necessary link to earth system,etc ...all as specified and to the satisfaction of the Engineers . Cummins, Volvo, Iveco or other equal and approved. | Item | 1 |  | 0
III-C-2 | Supply , install and connect EDL network with new 100KVA generator and solar ON grid system with all accessories needed such ATS 200A European brand, torsade cable size 35mm2, distance is around 320m from electrical room to link the three buidlings: مبنى الدائرة الفنية و مبنى الزراعة و مبنى الصحة | Item | 1 |  | 0
IV- | CIVIL WORKS FOR ALL THE PROJECT
IV-1 | Construct and build a new room, with dimensions 2.5x2.2m and 2.8 m height. Room door to be with grills and a louvered window (size 0.8mx0.8m) for natural ventilation. (For system 3) | Item | 1 |  | 0
IV-2 | Electrical road crossing (3 PVC pipes 3") for future use. | متر جر | 100 |  | 0
V- | GENERAL ITEMS IN CONNECTION WITH SYSTEM (As per specifications and B.O.Q.)
V-1 | Test and inspect existing three generators ( 275kva - 135kva and 100kva ), maintain these generatos to work in good conditions and high efficiency and replace damaged parts. Check fuel, air and oil filter, joints, protection and control devices, cables, sound proofers, silencers,mufflers, supports, concrete base antivibration system , batteries ,battery chargers, conductors, with all necessary accessories, etc ...all as specified and to the satisfaction of the engineers. (Genuine parts) | Item | 1 |  | 0
V-2 | Supply, install and connect wall type split air conditioner 12000BTU with inverter for technical room (for zone 1 & 3) with proper copper pipes and all needed installations. Brand: Trane, Gree, Mitsubishi or other equal and approved. | Item | 2 |  | 0
V-3 | Provide a complete training for the operators (at least 5 peoples) in operation and maintenance of the project | Item | 1 |  | 0
V-4 | Supply and installation of portable dry powder fire extinguisher on roof (12kg) near panels and in inverter room (4kg), an automatic dry powder fire extinguisher (6kg) with stand alone smoke detector with alarm & standalone hydrogen fluoride sensor with alarm in inverter room for system 1 | Item | 1 |  | 0
V-5 | Supply and installation of portable dry powder fire extinguisher on roof (12kg) near panels and in inverter room (4kg), an automatic dry powder fire extinguisher (6kg) with stand alone smoke detector with alarm & standalone hydrogen fluoride sensor with alarm in inverter room for system 2 | Item | 1 |  | 0
V-6 | Supply and installation of portable dry powder fire extinguisher on roof (12kg) near panels and in inverter room (4kg), an automatic dry powder fire extinguisher (6kg) with stand alone smoke detector with alarm & standalone hydrogen fluoride sensor with alarm in inverter room for system 3 | Item | 1 |  | 0
V-7 | Supply and install automatic system to clean panels on pitched roof for zone 1: A waterless solar panel cleaning robot that sweeps, blows and vacuums dust and dirty | Item | 1 |  | 0
V-8 | Supply and install automatic system to clean panels on flat roof for zone 2 & 3, one unit for each panel row, dry system, rails for motor guiding, 0.5 Hp, high quality: Walking with frame panel rail, running multiple times under the control of switch and remote controller, aim at fully cleaning for photovoltaic panel surface | Nr. | 24 |  | 0
0
Grand total |  |  |  |  | 0