## Grade of Compliance Range
| RFT Scoring Sheet | Reference Number | SF-CF-87
|  | Owner | PRO/PMO
|  | Revision Code | 3.0
|  | Implementation Date | 2024-05-01
Grade of Compliance range:
2 : Fully compliant
1 : Partially compliant
0 : Not compliant
K : Disqualification

## Technical Scoring
| RFT Scoring Sheet | [11 empty] | Reference Number |  | SF-CF-87
[13 empty] | Owner |  | PRO/PMO
[13 empty] | Revision Code |  | 3.0 | 3.0
[13 empty] | Implementation Date |  | 2024-05-01 | 2024-05-01
Project Name | Passive Cabling for Jdeideh Site
Article | Requirements | Weight | Mandatory | Supplier 1 | Supplier 2 | Supplier 3 | Supplier 4 | Supplier 5 | Supplier 6 | Remarks | Supplier 1 Final | Supplier 2 Final | Supplier 3 Final | Supplier 4 Final | Supplier 5 Final | Supplier 6 Final
1 | ARTICLE 1 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
1.1 | The following section provides a summary of the mandatory requirements for the technical submittal as a part of the tender response. This shall be accompanied by the relevant manufacturer and installer documentation. The list outlined below is not exhaustive and reference shall be made to the appropriate sections within this document to ensure full compliance to all areas | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
1.2 | The Registered SCS (Structured Cabling System) installation shall meet or exceed the permanent link requirements of the latest ANSI/TIA-568 and ISO/IEC 11801 series of standards | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
1.3 | All copper cabling shall be UTP throughout the channel with no shields or foils included within the cable and component design. This includes cable, modules, panels and cords. | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
1.4 | Manufacturer shall provide a list of the current applications and guaranteed distances supported by the copper infrastructure. | 300 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
1.5 | All Passive Components in the SCS shall meet or exceed the relevant optical fiber link specifications as detailed in the latest ANSI/TIA-568 and ISO 11801 series of standards. | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
1.6 | Multimode fibre shall conform to the Differential Mode Delay (DMD) requirements outlined for the appropriate grade of cable – testing details along with third party test results to be submitted | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
1.7 | Manufacturer shall provide a list of the current applications and guaranteed distances supported by the fiber infrastructure, including the number of MPO and LC connectors. | 200 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
1.8 | Data Sheets for all specified products outlining compliance to the specifications shall be provided. | 100 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
1.9 | Manufacturer shall guarantee that all current and future applications designed to operate on a standards compliant cabling system, will be covered under the terms and conditions of the Manufacturer’s warranty at the time of submission of this project. | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
1.10 | All components shall be manufactured solely by the proposed vendor. A full list of the company’s manufacturing locations along with their ISO 9000 accreditations shall be included in the response. This includes all copper and fiber cable and components. | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
1.11 | Full details of the manufacturers’ 25 year Applications Assurance Warranty shall be included within the response | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
1.12 | Full details of the installers’ qualifications shall be provided, including up to date manufacturers’ training requirements and CV’s of key personnel that will be assigned to the project. | 500 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
2 | The installation shall be installed and comply with the following standards and guidelines. This list is not exhaustive and the latest versions should be referenced and adopted.
2.1 | · ANSI/TIA-568.0-D: Generic Telecommunications Cabling for Customer Premises, 2015 | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
2.2 | · ANSI/TIA-568-C.2: Balanced Twisted-Pair Telecommunication Cabling and Components Standard, 2014 | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
2.3 | · ANSI/TIA-568.3-D: Optical Fiber Cabling Components Standard, 2016 | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
2.4 | · ANSI/TIA-569-D-1 :Addendum 1, Revised Temperature and Humidity Requirements for Telecommunications Spaces, 2016 | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
2.5 | · ANSI/TIA-942-B: Telecommunications Infrastructure Standard for Data Centers, 2017 | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
2.6 | Bidder shall supply and install, complete Fiber and Copper cables with all accessories as per provided BOM sheet and floor plan attached in Annex B | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
3 | Performance Requirements
3.1 | Shall guarantee significant channel margin over the entire swept frequency range, from 1 to 500 MHz. | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
3.2 | The Manufacturer shall provide printed and electronic independent 3rd Party certification certificates (such as ETL Laboratories) for Guaranteed Worst Case, Category 6A, Class EA Channels to both ISO and TIA standards according to the full standards defined channel model (4 connectors over 100 metres). Test Certificates for both long and short channel configurations to be submitted. | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
3.3 | The Manufacturer shall provide a full list of tested and guaranteed copper applications that are supported under the warranty, including the distances and number of connectors supported. | 300 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
3.4 | Full support for applications up to 10Gb/s. | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
4 | Category 6A support for Short Channels (< 15 meters) and Patch Cords
4.1 | the Category 6A/ Class EA UTP SCS must be able to support channels that are significantly shorter than the minimum 15 meters stated in the cabling standards. Based on the number of connectors 4,3,2, the SCS must be able to support the following connections minimum horizontal lengths of 5m,5m, and 3 meters consecutively. As part of a compliant channel, the SCS must also be able to support patch cords lengths of 1 meter minimum, and equipment cords of 2-meter minimum. | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
4.2 | Cords shall be equipped with 8-pin modular plugs on each end. | 300 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
4.3 | All cords shall be round, and consist of copper conductors, tightly twisted into individual pairs. | 300 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
4.4 | Plugs shall be designed with an anti-snag latch to facilitate easy removal during move, add and change processes. | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
4.5 | The cordage must be available in the following options: | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
4.6 | 8 solid 28AWG copper conductors reduced diameter cables. | 300 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
4.7 | Copper clad aluminium is not permitted. | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
4.8 | The cordage shall be available in Low-Smoke, Zero Halogen (LSZH) compatibility. | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
5 | Category 6A Patch Panels
5.1 | The Patch Panels shall be modular in design, capable of utilizing individual modules, ganged style adaptors (pre-terminated) or pre-populated configurations. | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
5.2 | The following provides the requirements and options that should available for the design: | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
5.3 | · Available in 24-port or 48-Port Configurations in 1U or 2U sizes as standard. | 300 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
5.4 | · Available in Angled or Standard/straight Configurations. | 300 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
5.5 | · Panels should also be available with integrated cable managers to reduce the space/use of cable managers. | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
5.6 | · Compatible with 19 inch mounting hardware as per IEC 60297. | 300 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
5.7 | · Compliant with IEC 60603-7-4. | 300 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
5.8 | · Integral termination managers at the rear of the panel shall be provided. | 300 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
5.9 | · The panel shall provide adequate space for labeling. | 300 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
5.10 | When configured in a 4 connector channel, as specified within this document, the panel shall be capable of delivering the minimum guaranteed channel performance specified. | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
5.11 | The bidder shall label all cables using printed labels- handwritten labeling is not accepted | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
5.12 | The OM4 multimode fibre shall be manufactured with an inside vapour deposition process such as the MCVD (Modified Chemical Vapour Deposition) or PCVD (Plasma Clad Vapour Deposition) processes. Multimode fibres produced with outside vapour deposition processes, such as OVD or VAD, will not be accepted. | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
5.13 | The OM4 multimode fibre shall be tested in accordance with: • IEC/EN 60793-1-49 • ANSI/TIA-455-220-A • ANSI/TIA-492AAAC-A Third Party DMD Test Certification shall be included within the technical response | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
6 | Fibre Optic Shelves
6.1 | Fibre Optic Shelves shall be modular in design and available in High Density and Ultra High Density Configurations and be available in 1U, 2U and 4U sizes that are compatible with 19 inch mounting hardware. | 300 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
6.2 | The shelves shall be designed to accept LC or MPO. | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
6.3 | The shelves shall be designed to accept individual modules, adaptor panels and cassettes for both Multimode and Singlemode solutions | 300 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
6.4 | The shelves shall provide adequate room for splice trays (Fusion & Mechanical) with better cable management at the front and rear of the shelf | 300 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
7 | Fiber Optic Cords and Pigtails
7.1 | Optical fibre cordage shall be UNIBOOT style and duplex | 200 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
7.2 | Optical fibre cordage shall be available in 1.mm enhanced durability. | 200 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
7.3 | All copper CAT6A U/UTP cables to be field terminated and not pre-terminated, the specifications of the panels, | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
8 | The optical fiber system shall be a factory-Preterminated, fully assembled system to facilitate rapid installation and simplified design for Data Centre and LAN applications. The system shall be offered with the following components:
8.1 | · Pre-terminated fiber cable assemblies utilizing MPO connectors. | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
8.2 | · Pre-Terminated fibre optic modules with LC connectors on the line side and MPO connectors on the trunk side. | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
8.3 | · Ruggedized fan-outs and array cords with LC connectors on the line side and MPO connectors on the trunk side were needed. | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
8.4 | The preterminated fiber system should be intelligent ready from the same manufacturer with all panel sizes and configuration being LC or MPO as detailed above | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
8.5 | Pre-Terminated Fiber optic systems must:
8.6 | · Utilize Method B enhanced polarity as defined in TIA 568 and EN 50174 standards, Special or non-standard polarity components shall not be permitted. | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
8.7 | · Use Method B enhanced polarity for efficient migration of duplex and parallel optics | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
8.8 | · Support multimode 8-, 12- and 24-fiber MPO connectors | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
9 | The Pre-Terminated Fiber optic assemblies must comply with the below:
9.1 | · MPO trunks feature alignment pins on both ends | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
9.2 | · Support current and future applications with manufacturers Application Assurance | 300 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
9.3 | · Bend-insensitive fiber improves cable management and maintains industry-leading link loss | 300 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
9.4 | · The pre-terminated cable assemblies shall be terminated with industry standard MPO (Multi-Push On) fiber connectors compliant with IEC 61754-7 in a round-boot design. | 100 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
9.5 | · Pre-terminated trunk cables will be terminated on both ends with MPO connectors and will be available from 12 fiber up to 144 fiber. | 200 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
9.6 | · Pre-Terminated trunk cables shall be made with 12-fibre sub-units in loose fiber configuration. Ribbon fiber matrices will not be accepted due to excess bend loss. | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
9.7 | · Pre-terminated trunk cables shall be orderable by length and fiber type, and shall be available as indoor LSZH assemblies. | 300 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
9.8 | Factory test data with insertion loss shall be provided with each trunk assembly. Loss values at 850nm will be provided for multimode assemblies | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
10 | Pre-Terminated Fiber Optic modules
10.1 | · Pre-Terminated Fiber Optic modules shall provide high-density, factory terminated, factory tested, and modular optical fiber connectivity that allows quick connection of system components. Shelves and panels shall accommodate OM4 multimode optical fiber cabling. | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
10.2 | · Pre-terminated modules shall be self-contained enclosures that shall consist of LC adapters on the line side and MPO adapters on the trunk side. These modules shall be available with OM4 multimode fiber for connection with MPO pre-terminated fiber trunk cables. | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
10.3 | · Translucent dust covers or caps will be provided on the LC ports. These will simplify use of Visual Fault Locators (VFLs) used to ensure connectivity and polarity. | 300 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
10.4 | · Pre-terminated modules shall be available in 12-fibre and 24-fibre LC in OM4 multimode | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
10.5 | · The maximum insertion loss or the LC OM4 multimode pre-terminated module shall not exceed 0.50 dB at 850 nm on any fiber. | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
10.6 | · The minimum return loss for the LC OM4 multimode pre-terminated module shall not be less than 20 dB on any fiber. | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
10.7 | · OM4 modules will be colored coded with industry standard aqua green | 100 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
11 | Warranty
11.1 | The solution shall include a 25 Year Extended Product and Applications Assurance Warranty. | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
11.2 | The Manufacturer shall give the following assurances during the Warranty Period: | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
11.3 | · The Registered System will meet or exceed the System Performance Specifications | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
11.4 | · The Registered System will support Applications as specified in the Application Performance Specifications. | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
11.5 | · The Registered System will support future Applications introduced during the Warranty Period, to the extent such Applications are defined to operate in conformance with the applicable Application Performance Specification for the Registered System. | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
11.6 | The Warranty should include both Parts and Labor. | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
11.7 | Bidder shall provide post installation support services to fix any issues that arise | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
11.8 | The Manufacturer’s Warranty details and the Terms and Conditions shall be included within the response. | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
11.9 | All testing shall conform to the latest release of the appropriate standards, the manufacturer’s warranty criteria, and the project acceptance criteria. | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
11.10 | The System Installer shall be responsible to repair or replace any cable that does not meet specification with no additional cost to the project. | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
11.11 | After delivery of Materials to the Site, and prior to installation, all cables, cable reels and shipping cartons shall be visually inspected to detect possible damage incurred during the shipping and transport. Visibly damaged goods should be immediately reported to the manufacturer for inspection. | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
11.12 | All test results are required to be documented and submitted in hard copy (summary only) and electronic (softcopy) format with the as-built documentation. | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
11.13 | The System Installer shall provide unaltered electronic test results submitted in the original software format of the respective test equipment manufacturer. Text files or files that have been imported into a word processor or other text editor application shall not be acceptable. | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
11.14 | MIC1 Representative retains the right to be present at any or all testing. The System Installer shall provide due notice prior to the beginning of the testing process. | 300 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
11.15 | MIC1 reserves the right to mandate re-termination or other reasonable rework to improve the performance of any cabling indicated as being a “marginal pass”. | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
11.16 | MIC1 should have the ability to retrieve the factory test result of any installed cable on site by using a unique number printed on the cable jacket. | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
12 | Copper Testing
12.1 | The test equipment shall comply with the following standards: | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
12.2 | · Compliant with proposed ISO (IEC WG9 Standard IEC61935-1) Level V accuracy requirements to 1000 MHz | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
12.3 | · Supports the complete suite of Resistance Unbalance standards needed for Power over Ethernet (PoE) – IEC61935-1 & 11801-1-4, IEEE 802.3af, IEEE 802.3at, ANSI/TIA-568-C.2 | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
12.4 | · Next generation balance drafts – IEEE 802.3, TIA TR42.7 | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
13 | Optical Fibre Testing
13.1 | The test equipment shall comply with the following standards: | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
13.2 | · TIA/EIA-526-14-B | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
13.3 | · IEC 61280-4-1 edition 2 | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
13.4 | · TIA/EIA-526-7 | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
13.5 | · IEC 61280-4-2 ed 1 | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
13.6 | Each multimode fibre strand shall be tested at 850nm and 1300nm. | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
13.7 | All optical power meter tests shall be performed using a stable light source. | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
13.8 | The System Installer shall use the test equipment manufacturer’s standard form for all results. | 300 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
13.9 | The System Installer shall ensure that all results are within the Manufacturers Link Loss Budget Calculations for Warranty purposes. | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
13.10 | The System Installer shall provide three references of projects of a similar size and nature, undertaken within the country. | 500 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
13.11 | The System Installer shall provide details of any sub-contract labor to be involved in the project. | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
13.12 | The System Installer shall provide adequate supervision of any subcontract personnel. This should be by directly employed supervisors. | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
13.13 | The System Installer shall provide CV’s of all key personnel to be involved in the project. This should include Project Managers, Designers and Supervisors. | 300 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
13.14 | Manufacturer training shall be a prerequisite of System Installer Compliance to this response. The System Installer shall provide current certificates for the manufacturers design training requirements. These shall be relevant to the personnel involved in the project. | 500 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
13.15 | The System Installer shall provide written confirmation from the manufacturer that they are a current business partner and certified to carry out installations and issue a warranty for the solution. | 100 | k | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
13.16 | Bidder should specify the delivery timeline of the proposed equipment. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
13.17 | Additional cost or delay due to any missing equipment, accessories, or software needed for the proper operation of the proposed material and which was not taken into account in the offered BOM will be borne by the Bidder | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
13.18 | In case of delay in delivery a penalty of 1% per day of delay shall be deducted from total amount of the PO for a maximum of 10% | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
13.19 | In Case the bidder/supplier fails to deliver a feature , functionality or item that he had mentioned as compliant and included in the RFP response, then the following will be applied: • A penalty of 5% from the total amount of the project cost will be applied for each feature/functionality or item not delivered by the supplier. This amount will be deducted from the final acceptance payment. • If the penalty value exceeds the amount remaining to be paid for the project, then MIC1 has the right to cancel the project and the supplier will have to refund the total amount paid to the supplier without the need of any legal recourse . • If a feature , functionality or item is marked as killer and supplier/bidder fails to deliver it upon implementation then MIC1 have the right to cancel the project and the supplier will have to refund the total amount paid without the need of any legal recourse. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
14 | Compliance rules
14.1 | Bidder shall specify reference (the document, the page number & the section) for each of the requirement items | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
14.2 | The filled Compliance Matrix as well as the Offer and BoQ are an integral part of the PO to be issued by MIC1 following the selection of the Bidders. Bidders ‘abidance by and respect of their Offer, and more particularly on the delivery date mentioned therein, and based on which the PO is issued, is mandatory. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
14.3 | previous experience with bidder (support and after sales services delivered , accuracy of eqt delivered as per order, speed of response to alfa requests , seriousness and professionalism in the proposals expertise of his team, respects deadlines …. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 | 0
[11 empty] | SUPPLIER 1 SCORE | SUPPLIER 2 SCORE | SUPPLIER 3 SCORE | SUPPLIER 4 SCORE | SUPPLIER 5 SCORE | SUPPLIER 6 SCORE
* For Requirements defined as ''Killer'', a ‘’Fully Compliant’’ score should be the sole acceptable outcome. Failing to obtain a ‘’Fully Compliant’’ score on the requirements defined as Killers, will mandate immediate disqualification for bidders.
Note on D8: Entity (Department/ Unit) that identified the requirement and that will be responsible for its evaluation.
Note on E8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on F8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on G8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on H8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on I8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on J8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on E12: Evaluators Comments
Note on F12: Evaluators Comments
Note on G12: Evaluators Comments
Note on H12: Evaluators Comments
Note on I12: Evaluators Comments
Note on J12: Evaluators Comments
Note on E124: Evaluators Comments
Note on F124: Evaluators Comments
Note on G124: Evaluators Comments
Note on H124: Evaluators Comments
Note on I124: Evaluators Comments
Note on J124: Evaluators Comments
Note on E125: Evaluators Comments
Note on F125: Evaluators Comments
Note on G125: Evaluators Comments
Note on H125: Evaluators Comments
Note on I125: Evaluators Comments
Note on J125: Evaluators Comments

## Combined Scoring
| RFT Scoring Sheet |  | Reference Number | SF-CF-87
|  |  | Owner | PRO/PMO
|  |  | Revision Code | 3.0 | 3.0
|  |  | Implementation Date | 2024-05-01 | 2024-05-01
Project Name | Passive Cabling for Jdeideh Site
| Technical Score | 40%
| Commercial Score | 60%
| Combined Score | 100%