## SUMMARY
SUMMARY- Phase-1
HARBATA GOVERNMENTAL HOSPITAL / Phase-1 |  | Date: May, 2025
BILL OF QUANTITIES/ Phase-1
Item | Description | Total Cost
(US $)
A | BILL NO. 01 - PREAMBLES | Included
B | BILL NO. 02 - BILL OF QUANTITIES
1 | DIVISION 01 - GENERAL REQUIREMENTS
2 | DIVISION 31 - EARTHWORKS
3 | DIVISION 03 - CONCRETE
4 | DIVISION 04 - MASONRY
5 | DIVISION 05 - METALS
6 | DIVISION 06 - WOODWORK
7 | DIVISION 07 - THERMAL & MOISTURE PROTECTION
8 | DIVISION 08 - OPENINGS
9 | DIVISION 09 - FINISHES
10 | DIVISION 10 - SPECIALTIES
11 | DIVISION 15 -MECHANICAL WORKS
12 | DIVISION 16 -ELECTRICAL WORKS
TOTAL COST

## Pream
PREAMBLES
HARBATA GOVERNMENTAL HOSPITAL |  |  | Date: May, 2025
BILL OF QUANTITIES
Div. | Item | Description
No.
prices for preambles should be included in the total prices of the offer
31 | - | PREAMBLES - EARTWORKS
| A | Earthwork
Rates for earthworks shall include for the following:
| 1 | Clearing the site of all debris, rubbish etc., prior to the commencement of work.
| 2 | All kinds of Excavation in any ground and material including fill, rock to any depth.
| 3 | Trimming, levelling, ramming bottom of excavation, earthwork support and keeping excavations free of water
| 4 | Double and multiple handling
| 5 | Stockpiling
| 6 | Loading, transporting and carting away unwanted materials.
| 7 | Importing to site all selective materials to a tip to be provided by the Contractor
| 8 | Excavation shall be measured net. No allowance shall be made for earthwork support and working spaces
| 9 | The quantities for excavation are those in place before excavating. No allowance shall be made for increase of bulk after excavation.
| 10 | Rates for excavation and backfill shall include for finishing and grading to any falls, cross-falls, or slopes that may be required.
| 11 | The excavation quantities shall be as the topographic drawings and final executed as built drawings, irrespective of excavated volume due to equipment restrictions and method of excavation
| 12 | Unauthorized excavation and subsequent backfill shall be at the Contractor's expense
TOTAL PREAMBLES - EARTHWORKS
PREAMBLES - EXTERIOR IMPROVEMENTS
| B | EXTERIOR IMPROVEMENT
Unit Pavers
Rates for unit pavers shall include for:
| 1 | Loading, transporting and carting away unwanted materials
| 2 | Preparation of surfaces
| 3 | Any width or area and any location
| 4 | Levelling and compaction
TOTAL PREAMBLES - EXTERIOR IMPROVEMENTS
03 | - | PREAMBLES - CONCRETE
Rates for concrete shall include for the following:
| 1 | Pouring, placing, vibrating and packing between formwork and around reinforcing steel.
| 2 | Curing and sprinkling.
| 3 | Work of any cross-sectional area and at any height.
| 4 | Work in new or existing locations
| 5 | Grading, tamping, trowelling and floating.
| 6 | Reinforcement unless indicated otherwise, formwork and metal ties.
| 7 | Forming grooves, throats, holes chases, rebates, chamfers, splayed angles, mouldings and the like other than for fairfacing.
| 8 | Provision for all necessary sleeves, openings, embedded conduits or boxes as required prior to pouring of concrete.
| 9 | Forming mortices and grouting in.
| 10 | Narrow widths.
| 11 | Expansion, construction and control joints.
| 12 | Forming openings.
| 13 | Samples and mockup.
| 14 | Concrete mock-up for color sampling.
| 15 | Closing of all shafts and opennings between floors after installation of services
Concrete has been measured net in place. No deduction has been made for the following:
| 16 | Volume of concrete displaced by embedded steel.
| 17 | Voids not exceeding 0.10m2 in concrete measured superficially
| 18 | Voids not exceeding 0.05m3 in concrete measured cube.
Concrete has been measured as follows:
| 19 | Drops and up-stands, down-stands from face of the horizontal member.
| 20 | Columns from top of slab to bottom of soffits or drop beams
Rates for reinforcing steel shall include for the following:
| 21 | Bending, tying wires, distance pieces and spacers.
| 22 | Rods and bars in any location and at any height.
| 23 | Cutting and waste.
| 24 | Curved reinforcement.
| 25 | Shop drawings.
| 26 | Transport
| 27 | Samples
| 28 | Reinforcing steel will be measured net in place. No allowance will be made for laps unless shown on drawings.
| 29 | Reinforcing steel weights shall be measured in accordance with the weights per meter length of bars as published by British Steel.
Rates for concrete floor toppings (screed) shall include for the following:
| 30 | Cleaning down and preparing surfaces
| 31 | Work in any area height or width
| 32 | Reinforcement (wire or fibre)
| 33 | Hoisting, bedding, trowelling and floating
| 34 | Provision for all necessary sleeves, openings, etc…
| 35 | Laying to slopes, falls or crossfalls
| 36 | Screed has been measured net. No deduction has been made for voids not exceeding 0.25m2
TOTAL PREAMBLES - CONCRETE
04 | - | PREAMBLES - MASONRY
| A | Blockwork
Rates for blockwork shall include for the following:
| 1 | Work of all classifications in any location
| 2 | Rough and fair cutting
| 3 | Use of solid blocks where cutting is required
| 4 | Cutting or leaving holes, chases, grooves, mortices and sinkings including all making good
| 5 | Bedding and pointing plates and frames, and building in door and window frames and the like
| 6 | Cutting and pinning in ends of lintels, steps, timbers, rails, brackets, steel section and the like, including all making good
| 7 | Raking out joints or hacking surfaces
| 8 | Metal lathing and bonding including mesh strips at corners
| 9 | Samples and mock-up
| 10 | All blockwork has been measured net including mortar. No deduction has been made for lintels, sills and voids not exceeding 0.10m2
| B | Stonework
Rates for stone work shall include for:
| 11 | Templets and patterns
| 12 | All joints including joggle joints, sunk joints rebated and the like
| 13 | All dressing
| 14 | Work in any location or at any height
| 15 | Square ends, square reveals, square external angles of walls and the like
| 16 | Splayed ends, battered ends, battered external and internal angles of walls and the like.
| 17 | Stain-proof coating to unexposed faces of stones and high performance coating to all exposed faces of new and existing stone surfaces
| 18 | Wall ties, anchors, metal cramps and dowels. Load bearing fixings. Lead plugs and the like
| 19 | Rough and fair cutting
| 20 | Grooves, throats, rebates, margins, flutes, sinkings chamfered angles, founded angles and the like
| 21 | Stops and mitres
| 22 | Grooves for turned in flashings, nibs of skirtings and the like
| 23 | Horizontal raking and vertical chases
| 24 | Holes for pipes, tubes, bars, conduits, ducts and the like
| 25 | Elastic joints
| 26 | Shop Drawings
| 27 | Tests and amples
| 28 | Mock-up
| 29 | Waste
| 30 | All stonework have been measured net. No deductions have been made for voids not exceeding 0.25m2
TOTAL PREAMBLES - MASONRY
05 | - | PREAMBLES - METALS
Metalwork
Rate for metalwork shall include for the following:
| 1 | Submitting approved shop drawings
| 2 | Transporting hoisting, wedging and the like
| 3 | Assembling, welding and grinding
| 4 | Drilling, countersinking, bolting and riveting including all nuts and washer
| 5 | All cuttings, notches and making holes
| 6 | Anchors and lugs including fixing and building in.
| 7 | Sawn softwood dovetailed grounds, blockings and backings including all making good
| 8 | Temporarily fixing and re-fixing ironmongery
| 9 | Factory rust-proof painting or two primer coats of rust inhibiting before fixing as specified
| 10 | Curved work
| 11 | Samples and mock-up.
TOTAL PREAMBLES - METALS
06 | - | PREAMBLES - WOOD & PLASTICS (When existed)
Rates for wood shall include for the following:
| 1 | Any length ot cross-section
| 2 | All kinds of joints and all cutting and waste
| 3 | Raking, curved or circular work and labour
| 4 | Notching, morticing, borings, sinking, forming angles, and rounded edges, scribing and all other sundry items of the like nature required
| 5 | Plugging to concrete or blockwork including all making good
| 6 | Two coats of wood preservative to all non-exposed faces of timber
| 7 | Preparing surfaces to receive finishes
| 8 | Sawn grounds, sub-frames, blockings and backings
| 9 | Submitting approved shop drawings
| 10 | Tests samples and mockups
| 11 | Wrot faces on all timbers, unless otherwise stated
| 12 | Waste
TOTAL PREAMBLES - WOOD & PLASTICS
07 | - | PREAMBLES - THERMAL & MOISTURE PROTECTION
Rates for waterproofing shall include for the following:
| 1 | Cleaning down and preparing surfaces
| 2 | Any width or area, vertical and horizontal
| 3 | Fair and rounded edges, drips, arises and angle fillets
| 4 | Cutting to line, overlapping, turning into grooves and pointing
| 5 | Laying to slopes, falls or cross-falls
| 6 | Working into outlets, channels, gullies and the like
| 7 | Cutting, trimming, making holes and forming openings, etc., including working around pipes and openings and making good.
| 8 | Mastic pointing and protection of the whole work under this section.
| 9 | Tests, samples and mock-ups
| 10 | Submitting approved shop drawings
| 11 | Waste
| 12 | All necessary fixing accessories and backing such as steel plates, angles, wood blocking, and the like.
| 13 | All waterproofing works have been measured net. No deduction has been made for voids not exceeding 0.25m2.
TOTAL PREAMBLES - THERMAL & MOISTURE PROTECTION
08 | - | OPENINGS
| 1 | All sizes given are finished sizes
| 2 | All wood, steel and aluminium windows, doors, frames, curtain walls, etc.., shall be factory assembled and reinforced according to drawings, complete with hinges, glazing gaskets and anchors and all aluminium elements shall be protected from adjoining structures as specified.
| 3 | Where doors or windows have no structural member to which they may be secured the provision for rigidity of such doors or windows shall be provided
| 4 | All windows and doors to be weatherproof
| 5 | All dimensions of doors and windows must be adapted to fit the existing conditions of the site
Rates for doors, windows, etc… shall include for the following:
| 6 | Easing and adjusting doors and protection generally
| 7 | Tests, samples and mock-ups
| 8 | Shop drawings
| 9 | Anchors and fixing accessories
| 10 | Fixing in place
| 11 | Painting as specified including preparation of surfaces, rubbing down between coats, work in multi-colours and waste
Rates for glazing work shall include for the following:
| 12 | Any pattern, size and area
| 13 | Circular cutting and square cutting with rounded edge
| 14 | Glazing to wood or metal
| 15 | Bedding edges and labours to edges including rounding edges of all panes to prevent damage to gaskets
| 16 | Grinding and drilling holes
| 17 | Protection from damage and replacing and damaged unit
| 18 | Irregular shaped panes are measured as smallest rectangular area from which such shape can be obtained
| 19 | Samples and mock-up.
Rates for ironmongery shall include for the following:
| 20 | Screws and fixing accessories
| 21 | Temporarily fixing and refixing ironmongery
| 22 | Tests, samples and mock-ups
TOTAL PREAMBLES - OPENINGS
09 | - | FINISHES
Rates for in-situ finishes shall include for the following:
| 1 | Application to and preparation of any surface including guide screeds
| 2 | Wire mesh at junctions between differing materials around openings for pipes ducts etc.. and angle and stop beads
| 3 | Any width or area, any location and any height
| 4 | Finish to surfaces, to falls, cross-falls and slopes including making good after all trades
| 5 | Working into channels, around edges, sharp arises rounded angles, coved angles and the like
| 6 | Admixtures, samples
| 7 | Curved work
| 8 | Sample and mock-up
Rates for tile and slab finishings shall include for the following:
| 9 | Application to and preparation of any surfaces
| 10 | Sand bed to any thickness to floor tiling as shown on the drawings.
| 11 | Screed and mortar backing to any thickness as shown on the drawings
| 12 | Any width pattern or area, any location and any height
| 13 | Grouting pointing and polishing
| 14 | Finishing surfaces, to falls, crossfalls and slopes, including making good after all trades
| 15 | Fair, rebated, rounded, chamfered, splayed, bevelled and moulded edges, grooves, flutes and the like
| 16 | Square, raking and circular cutting
| 17 | Cutting and fitting into openings or recessed area, and fitting around any section
| 18 | Admixtures samples
| 19 | Samples and mock-up
| 20 | Shop drawings
| 21 | Curved work
Rates for painting shall include for the following:
| 22 | Preparation of paint and preparation of surfaces to be painted
| 23 | Any area or width in any location
| 24 | Work in multi-colours
| 25 | Cutting in edges and rubbing down between coats
| 26 | Attendance, protection and making good after all trades
| 27 | Curved and sloped work
| 28 | Samples and mock-up
Rates for suspended ceiling systems shall include for the following:
| 29 | Work of all classifications in any location.
| 30 | Any area or width, location and height
| 31 | All kinds of joints, cutting and waste
| 32 | All labour
| 33 | Fixing to concrete or wood including all making good
| 34 | Suspension metal system including fixing accessories
| 35 | Access panels.
| 36 | Attendance, protection and making good after all trades
| 37 | Samples and mock-up
| 38 | All finishings have been measured as the net area in contact with the base. No deduction has been made for voids not exceeding 0.25m2.
TOTAL PREAMBLES - FINISHES
10 | - | SPECIALTIES
Rates for specialties shall include the supply and installations of all specialty items such as
identification devices, and washroom accessories as described and shall
account for and include the following items:
| 1 | Labour, tools, equipment, supervision and transport.
| 2 | Backer boards, supports, brackets, clamps, clips and anchors
| 3 | Fixing including fasteners such as bolts, anchor bolts nuts, nails, screws, washers, masonry expansion bolts, drawings, material and the like
| 4 | Cutting, drilling, grouting, patching and making good.
| 5 | Cleaning
| 6 | Painting
TOTAL PREAMBLES - SPECIALTIES
14 | - | CONVEYING SYSTEMS
| A | Rates for the lifts and conveying system installation shall include for the following:
| 1 | Assembling, installing and fixing in position, including machines, pulleys, motors, motor assembly, car and auxiliaries, controller and control system with necessary fixing accessories, factory paint and painting complete and in perfect working order in accordance with the drawings and as directed fully in the specifications
| 2 | Cutting and forming holes, chases, etc…, including pipes sleeves and making good all works disturbed.
| 3 | Plugging and screwing
| 4 | Testing, guaranties and warranties
| 5 | Spare parts
| 6 | Preventive maintenance for one year after handing over.
| 7 | Shop drawings
| 8 | As-Built drawings
| 9 | Coordination with other trades
| 10 | Electrical connection
| 11 | Diagrams
| 12 | Maintenance and operation manuals
TOTAL PREAMBLES - CONVEYING SYSTEM
15 | A | PREAMBLES - MECHANICAL - PLUMBING
The Contractor shall furnish all the material, execute all the works necessary to the final accomplishment of the site according to the specifications and drawings. All secondary materials and accessories not mentioned in the bill of quantities shall also be supplied without any extra charge.
The prices also include installation cost, painting, transportation, equipment, materials, hand labor as well as all the charges incurred by the perfect execution of works, general overhead and profits.
Drawings of plumbing installation supplied with this schedule are primary plans necessary for the establishment of tender documents only.
Protection measures must be taken, specially accessories such as hangers, bolts, nuts, washers and all fixing accessories must be of non corrosive material similar to stainless steel.
Owner reserve the right to change or to eliminate quantities and quality of accessories and equipment’s before ordering of these goods is confirmed to the Contractor.
Contractor shall execute as per followings:
| A) | Rates for plumbing works, shall include for:
| 1 | Assembling and jointing including jointing materials.
| 2 | Factory priming paint.
| 3 | Fixing, including nails, bolts, nuts, holes, screws, plugs and the like.
| 4 | Cutting and pinning including all making good.
| 5 | Plugging and screwing.
| 6 | Testing all installations as specified including providing equipment and personnel necessary for testing.
| 7 | Protection of all works.
| 8 | Marking positions of holes, mortises, chases, etc.
| 9 | Cutting and forming holes, chases, etc. including pipe sleeves and making good all work.
| 10 | Cutting and pinning ends of supports to structures.
| 11 | Builders works and all grouting, base, antivibration mounting to be integrated in the over all unit price of each item, it should be a responsibility of the subcontractor who will coordinate and cooperate with the general contractor.
| 12 | Painting as specified.
| 13 | Necessary trench or pit excavation, backfilling and disposal of surplus excavated materials.
| 14 | Protection and maintaining the works in good order.
| 15 | Electrical installations including wiring, conduits.
| 16 | Preparation of plans or diagrams, shop drawings, as-built drawings, schedules, instruction manuals, etc.
| 17 | Insulation as it should exist on piping and equipment for heat dissipation protection and condensation protection.
| 18 | Tags, nameplates, belt guards and all accessories and appurtenances described in the specifications dealing with each item or equipment.
| 19 | Any necessary motors, starters and necessary wiring on the equipment having electrical goods together with such items as insulation, piping, instruments, controls and all other items mentioned or implied in specifications and drawings as being supplied with the equipment and not separately measured and enumerated in the Bills of Quantities.
| 20 | Rates for all items of equipment and materials shall be inclusive of all certificates samples tests, supply of all information and data, supply of catalogues, charts, curves, submittals, certified drawing, and all other information, services called for in the specification, all fully connected up and in good working order.
| 21 | All hangers and support shall be hot dip galvanized after fabrication.
| 22 | Necessary continuous support guide for plastic pipes for mechanical and expansion protection.
TOTAL PREAMBLES - MECHANICAL - PLUMBING
15 | B | PREAMBLES - MECHANICAL - HVAC
The Contractor shall furnish all the material; execute all the works necessary to the final accomplishment of the site according to the schedules and drawings. All secondary materials and accessories not mentioned in the bill of quantities shall also be supplied without any extra charge.
Drawings of air ventilation installation and for ventilation supplied with this schedule are primary plans necessary for the establishment of tender documents only, contractor to prepare the Shop Drawings.
Protection measures must be taken, especially accessories such as hangers, bolts, nuts, washers and all fixing accessories must be of non corrosive material similar to stainless steel.
Owner reserve the right to change or to eliminate quantities and quality of accessories and equipment’s before ordering of these goods is confirmed by the Contractor.
Contractor shall execute as per followings:
| A) | Rates for Air conditioning and Ventilation works shall include installing and fixing all the works, including also the followings:
| 1 | Assembling and jointing including jointing materials.
| 2 | Factory priming paint.
| 3 | Fixing, including nails, bolts, nuts, holes, screws, plugs and the like.
| 4 | Cutting and pinning including all making good.
| 5 | Plugging and screwing.
| 6 | Testing all installations as specified including providing equipment and personnel necessary for testing.
| 7 | Protection of all works.
| 8 | Marking positions of holes, mortises, chases, etc.
| 9 | Cutting and forming holes, chases, etc. including pipe sleeves and making good all work.
| 10 | Cutting and pinning ends of supports to structures.
| 11 | Painting as specified.
| 12 | Protection and maintaining the works in good order.
| 13 | Electrical installations including wiring, conduits.
| 14 | Preparation of plans or diagrams, shop drawings. As - built drawings, schedules, instruction manuals, etc.
| 15 | Tags, nameplates, belt guards and all accessories and appurtenances described in the specifications dealing with each item or equipment.
| 16 | Any necessary motors, starters and necessary wiring on the equipment having electrical goods together with such items as insulation, piping, instruments, controls and all other items mentioned or implied in specifications and drawings as being supplied with the equipment and not separately measured and enumerated in the Bills of Quantities.
| 17 | Rates for all items of equipment and materials shall be inclusive of all certificates samples tests, supply of all information and data, supply of catalogues, charts, curves, submittals, certified drawing, and all other information, services called for in the specification, all fully connected up and in good working order.
| 18 | Horizontal and vertical run for the refrigerant pipes control and power cables shall lay on cable tray with cover, hot dip after fabrication.
| B) | Rates for ducting shall include for supplying all materials and for installation:
(The measuring of duct weight is theoretically its visible part)
| 1 | All cutting and waste, etc.
| 2 | Fixing including all supports, clips, holder bats, hangers.
| 3 | Joints, bolts, washers, nuts and everything necessary for the satisfactory jointing of ducts to each other, to items of equipment, or for connecting ducts to voids, shafts, etc.,
| 4 | All duct fittings including all bends, junctions, offsets, reducers, adaptors, flanges, vanes, all dampers, flexible connections, cleaning eyes, dirt pockets, air vessels, etc.
| 5 | All metal and timber sleeves through structural elements, cleaning caps, inspection.
| 6 | All insulation protection with canvas and special paints, similar to Foster or equivalent.
| 7 | Mastic joints protection after fabrication of the duct.
| 8 | Protection of the internal lining with special canvas and points.
| C) | The mentioned static pressure head loss is a tentative one. Contractor shall calculate the effective pressure head loss and be responsible for this calculation.
| D) | The rates of the duct insulation shall be paid per m2. The insulation area shall be measured by multiplying the duct perimeter by the mean length. Extra over shall not be paid for fittings, bends…etc.
| E) | Builders works and all grouting, base, antivibration mounting to be integrated in the over all unit price of each item, it should be a responsibility of the subcontractor who will coordinate and cooperate with the general contractor.
TOTAL PREAMBLES - MECHANICAL - HVAC
26 | - | PREAMBLES - ELECTRICAL
Prior to signing the contract, the electrical contractor has to check the drawings, specifications and bill of quantities and has to inform the consultant in written about any conflict, contradiction between trades, specified materials or methods less than specified in the regulations.
Where no conflicts are drawn to the engineer’s attention prior to the contract signature, the contractor shall not ask, during the execution, for a variation orders due to any contradictions in design trades.
The materials used on this project shall be the standard product of a well known manufacturer of such kind of product supported by published catalogs giving full technical details of all components and finished product, standard applicable and evidence that the manufacturer has been involved for at least five years in the professional up-to-date production of such equipment.
Equipment generally is to be supplied in complete factory assembled units ready for installation on site.
The Contractor shall furnish all the material, execute all the works necessary to the final accomplishment of the site according to the specifications, bill of quantities and drawings.
All secondary materials and accessories not mentioned in the bill of quantities shall also be supplied without any extra charge.
The prices also include installation cost, painting, transportation, equipment, materials, hand labor as well as all the charges incurred by the perfect execution of works, general overhead and profits.
Drawings of electrical installation supplied with this schedule are primary plans necessary for the establishment of tender documents only, contractor is to prepare the Shop Drawings.
Protection measures must be taken, especially accessories such as hangers, bolts, nuts, washers and all fixing accessories must be of non corrosive material similar to stainless steel.
The approved Contractor for electrical work must, prior to the commencement of works, prepare a price breakdown showing the cost of equipment, hand labor, accessories, general overhead as well as the profits.
The owner could ask for the installation only of the fixture units without any price alteration as mentioned in the above mentioned breakdown.
Owner reserve the right to change or to eliminate quantities and quality of accessories and equipment’s before ordering of these goods is confirmed to the Contractor.
Contractor shall execute as per followings:
Rates for electrical works, shall include for:
| 1 | Assembling and jointing including jointing materials.
| 2 | Factory priming paint.
| 3 | Fixing, including nails, bolts, nuts, holes, screws, plugs and the like.
| 4 | Cutting and pinning including all making good.
| 5 | Plugging and screwing.
| 6 | Testing all installations including providing equipment and personnel necessary for testing.
| 7 | Protection of all works.
| 8 | Marking positions of holes, mortises, chases, etc.
| 9 | Cutting and forming holes, chases, etc. including pipe sleeves and making good all work.
| 10 | Cutting and pinning ends of supports to structures.
| 11 | Concrete bases, isolation pads, grouting, etc.
| 12 | Painting all metallic corrosion protection.
| 13 | Necessary trench or pit excavation, backfilling and disposal of surplus excavated materials.
| 14 | Protection and maintaining the works in good order.
| 15 | Electrical installations and connections including wiring, conduits.
| 16 | Preparation of plans or diagrams, shop drawings. as - built drawings, schedules, instruction manuals, etc.
| 17 | Insulation as required on equipment special isolator to be used for short and ARC protection.
| 18 | Adequate connectors and fixing of cables and wires.
| 19 | All PVC conduits and boxes to be not less than medium gauge.
| 20 | Tags, nameplates, belt guards and all accessories and appurtenances described dealing with each item or equipment. Labeling and identification with durable engraved metallic support.
| 21 | Any necessary motors, starters and necessary wiring on the equipment having electrical goods.
| 22 | Rates for all items of equipment and materials shall be inclusive of all certificates samples tests, supply of all information and data, supply of catalogues, charts, curves, submittals, certified drawing, and all other information, services called for in the specification, all fully connected up and in good working order.
TOTAL PREAMBLES - ELECTRICAL

## Div 1
DIVISION 1 GENERAL REQUIREMENTS
HARBATA GOVERNMENTAL HOSPITAL |  |  |  |  | Date: May, 2025
BILL OF QUANTITIES
Item | Description | Unit | Qty. | Unit Cost | Total Cost
|  |  |  | (US $) | (US $)
1.1 | GENERAL REQUIREMENTS
1.1.1 | General
| These Preliminaries are applicable to the whole of the works. If the | Item | 1
Tenderer wishes to price any of the items contained herein, then each such
item, clause, or sub-clause must be individual priced. Lump sums
covering more than one item shall not be inserted. Preliminary prices
shall not be adjusted in the event of any changes to the Contract Price due
to variations.
Where any item, clause or sub-clause has not been prices, the value of such
shall be deemed to be included in the rates for measured items
elsewhere in the Bills of Quantities.
Clear and prepare site areas generally, as required to enable and facilitate
all new construction, including removal of unwanted trees, planting, ware
houses and any structure. etc.
1.1.2 | Photographs
| Monthly progress photographs shall be provided in accordance with the | Item | 1
requirements of the General Specification.
1.1.3 | As-Built Drawings
| The Contractor shall allow for providing 'As-Built' drawing in accordance | Item | 1
with the General Specification. (Arch- Struc. - Elec - mech).
1.1.4 | Workshop Drawings
| The Contractor shall allow for providing workshop drawings as specified | Item | 1
for the disciplines under the relevant Sections. (Arch- Struc. - Elec -
mech).
1.1.5 | Permits, Etc.
| The Contractor shall allow for obtaining all permits necessary for carrying | Item | 1
out the works.The Contractor shall allow for obtaining all documentation
necessary for the timely provision of labour, plant and materials used for
the works.
1.1.6 | Protection of Services and Cables
| The Contractor shall ascertain the position of and protect or divert as | Item | 1
necessary all service lines and cables on or adjacent to the site as required
by the Engineer.
1.1.7 | Performance Bond
| The Contractor shall allow for providing a Performance Bond in | Item | 1
accordance with Clause 10 of the General Conditions of Contract. The
Bond shall be in accordance with the proforma in the Instructions to
Tenderers Section. The Bond shall be raised through the local branch of an
approved surety and shall be lodged with the Employer prior to the
Contractor submitting his first application for payment.
1.1.8 | Site Office
| The Contractor shall provide and maintain site office for Engineer | Item | 1
complete with all furniture and related work.
1.1.9 | Water and Electricity
| Water for the Works shall be provided by the Contractor. The Contractor | Item | 1
shall make all necessary provisions for transporting water to the site
including connections, pumps, pipework and storage facilities if necessary.
Electricity shall be provided by the Contractor and the cost of providing
generators, fuel , maintenance, etc. and all other necessary facilities shall be
borne by the Contractor. If mains power is available the Contractor pay
all charges incurred.
2010-01-01 | Telephone
| The Contractor shall provide a telephone and fax in the Engineer's | Item | 1
office and shall pay all charges in connection including the cost
of calls (local calls only).
2011-01-01 | Notice Boards
| Allow for providing and installation of substantial site notice board size | Item | 1
2.40 x 3.00 m as specified and to the approval of the Engineer.
2012-01-01 | Samples and Testing
| The Contractor shall allow for providing all samples of materials and | Item | 1
workmanship required by the Engineer. The Contractor shall allow for
testing all materials as required by the specifications or directed by
the Engineer. The Contractor shall apply all test certificates and other
documentation necessary to prove the suitability of materials for
incorporation in the Works.
2013-01-01 | Insurance
| The Contractor shall provide the insurance cover described elsewhere in | Item | 1
the Contract documents and shall submit to the Engineer, certificates and
receipts for premiums as required as proof of this cover.
The Contractor shall liaise and cooperate with other Contractors and afford
them all reasonable opportunity for carrying out their work.
2014-01-01 | Plant
| The Contractor shall provide and maintain all plant and equipment | Item | 1
necessary for carrying out the Works and shall remove such plant and
equipment on completion and make good disturbed areas to the Engineer's
satisfaction.
2015-01-01 | Safety and Security
| The Contractor shall comply with the requirements of all safety regulations | Item | 1
in force and ensure that his work-force, sub-contractors and any other
persons engaged on the Works also comply with their requirements.The
Contractor shall allow for all necessary watching for the security of the
Works and the protection of the public. The Contractor shall provide all
warning signs, barricades, screens, lamps, etc. as necessary.
2016-01-01 | Setting up the Site
| The Contractor shall allow for setting up the site including site | Item | 1
investigation, surveying and setting out and for providing the Engineer
with instruments and men for checking these operations.The Contractor
shall provide, maintain and eventually remove site offices, huts, toilets,
storage facilities and the like for his own workforce and subcontractors.The
Contractor shall allow for providing temporary fences, gates, entrances, etc.
for the protection of the site and removing on completion. All such
protective measures shall be to the approval of the Engineer.
2017-01-01 | Care of the Site
| The Contractor shall keep the Site in a clean and safe condition including | Item | 1
the orderly and tidy storage of materials, regular and prompt removal of
rubbish and debris as it appears and the immediate removal from the
construction area and tidy stacking of scaffolding and shuttering after used.
The Contractor shall protect works from the effects of the weather and
subsequent operations by the provision of dust sheets, barriers, etc. to
the satisfaction of the Engineer.The Contractor shall clear away all
temporary works at completion and shall make good all work disturbed, to
the satisfaction of the Engineer.
2018-01-01 | Protection of Existing Adjoining Structures
| The Contractor shall take all necessary measures to protect existing | Item | 1
adjoining structures from any damage resulting from the execution of the
works.
2019-01-01 | Description Generally
| The description included in the Bills of Quantities to describe the | Item | 1
workmanship and materials necessary for each item are not necessarily
complete. The Tenderer is referred to the Specifications, Conditions of
Contract and other documents and the Drawings for further information
concerning the works and no claim or variation will be considered on
account of his failure to acquaint himself with such information.
2020-01-01 | Measurement Generally
| All Quantities contained within these Bills of Quantities are intended to | Item | 1
give a reasonable indication of the works shown on the drawings. The
Contractor must check all quantities and allow in his rates for any
changes or mistakes. Unless otherwise stated, all work has been measured
nett as fixed in its place with no allowance made for laps or
waste.Generally, in setting down dimensions in the Bills, the sequence is
length width-height. All measurements have been taken up or down to the
nearest metre (or other units), and where exactly half metre (or other
units) measurements result, these have been taken up.
2021-01-01 | Pricing Generally
| Any arithmetical errors made by the Contractor in extensions or totals in | Item | 1
the Bills of Quantities shall be corrected.The Contractor will be
required by the Engineer to produce a detailed breakdown of all his rates
prior to the signing of the Contract. The Contractor shall liase on this
matter with the Engineer's representative. The Contractor should price all
items he considers have a value. If any items are not priced by the
Contractor they will be deemed to be of the other items.
2022-01-01 | Site Protection
| Protect, safeguard and support as necessary existing buildings, structures, | Item | 1
facilities, site areas, trees and planting, services and utilities; etc., which are
to remain upon completion, from damage due to construction operations
and activities. Restore and rehabilitate all existing boundary walls/fences:
overhaul, repair, patch and make good existing boundary wall and fence
facades and components, including gates and finishes as necessary and
required; AND redecorate complete, to approval.
2023-01-01 | Conditions of Contract
| The Contractor shall allow for complying with the General and Special | Item | 1
Conditions of Contract and any other obligations not included
elsewhere in the Tender Documents.
TOTAL AMOUNT GENERAL REQUIREMENTS

## Div3
Division 03 - CONCRETE
HARBATA GOVERNMENTAL HOSPITAL |  |  |  |  | Date: May, 2025
BILL OF QUANTITIES
Item | Description of Material | Unit | Quantity | Unit Cost | Total Cost
No. |  |  |  | (US $) | (US $)
3.1 | Vibrated Concrete " F'c "= 20Mpa (cylindical compressive strength), with Ordinary Portland Cement (Ref. to specs) Including Clean Sawn Formwork (Ref. to specs).
3.1.1 | Blinding. | m3 | 292
3.2 | Vibrated Reinforced Concrete" F'c "= 25Mpa (cylindical compressive strength), with Ordinary Portland Cement (Ref. to specs) Including Clean Sawn Formwork (Ref. to specs),Water Stop with special water resistance admixtures (Ref. to specs)as shown in shop drawing, Mechanical and Electrical Sleeves as Per Structural shop Drawings, all structural elements with contact with soil must be applied with liquid waterproofing including sub strata preparation, primer protection:
3.2.1 | Footings | m3 | 451
3.2.2 | Retaining Wall (Site) | m3
3.2.3 | Water Tank walls and cover | m3
3.3 | Vibrated Reinforced Concrete" F'c "= 25Mpa (cylindical compressive strength), with Ordinary Portland Cement (Ref. to specs) Including Clean Sawn Formwork, Water Stop (Ref. to specs)as shown in shop drawing, Mechanical and Electrical Sleeves as Per Structural shop Drawings, all structural elements with contact with soil must be applied with liquid waterproofing including sub strata preparation, primer protection:
3.3.1 | 10 cm Slab on Grade including sunken slab | m3 | 384
3.3.2 | 150 mm thick, Slab on Grade to external ramp | m3
3.3.3 | Tie Beams | m3 | 320
3.4 | Vibrated Reinforced Concrete" F'c "= 30Mpa , (cylindical compressive strength),with Ordinary Portland Cement (Ref. to specs) Including Clean Sawn Formwork (Ref. to specs), Mechanical and Electrical Sleeves as Per Structural shop Drawings:
3.4.1 | Columns | m3 | 131
3.4.2 | Shear Walls | m3 | 124
3.5 | Vibrated Reinforced Concrete" F'c "= 25Mpa (cylindical compressive strength),with Ordinary Portland Cement (Ref. to specs) Including Clean Sawn Formwork (Ref. to specs) expension joint (Ref. to specs) Mechanical and Electrical Sleeves as Per StructuralShop Drawings:
Suspended ribbed (Hourdi) slabs or solid slab; concrete topped, hollow concrete masonry block including ribs and embedded beams and Drop Beams as noted on the Drawings.
3.5.1 | Solid Slabs overall (ts = 25cm) including staircases | m3 | 990
3.5.2 | Drop Beams | m3 | 39
3.5.3 | Suspended staircases; including flights, landings and beams | m3 | 0
3.5.4 | Parapets, balustrades, planter walls, sunbrakers kerbs, upstands, eaves drainage channels. | m3 | 15
3.7 | Steel Reinforcment
3.7.1 | Mild and high yield steel reinforcing bars, including bending and tie wires, as specified up and down as shown on the drawings. | ton | 280
3.8 | Section 035300 - Concrete Floor Topping
3.8.1 | Standard Floor Topping
Supply and pour concrete floor topping having a 28 day compressive strength of 24 Mpa; include steel wire mesh, and all necessary material and accessories; as per the specifications and drawings
3.8.1.1 | Screed; laid on concrete to a minimu thickness of 50mm; to received waterproofing for wet area | m2 | 187
3.8.1.2 | Screed; laid on concrete to a minimu thickness of 50mm; to received epoxy paint | m2 | 147
TOTAL AMOUNT CONCRETE WORKS

## Div4
Division 04 - MASONRY
HARBATA GOVERNMENTAL HOSPITAL |  |  |  |  | Date: May, 2025
BILL OF QUANTITIES
Item | Description of Material | Unit | Quantity | Unit Cost | Total Cost
No. |  |  |  | (US $) | (US $)
DIVISION 4 - MASONRY
4.1 | SECTION 042000 - UNIT MASONRY
Hollow concrete unit masonry precast block smooth finish of styandard size, bedded and jointed in Ordinary Portland Cement and salt free sand mortar (1:3), as specified and detailed, installed complete; INCLUDING for joint and steel reinforcement, beads, grout filled cells, wall ties and anchors; cutting. bonding and forming openings; precast or cast in place concrete lintels and sills; closures, control joints and weepholes; formwork to cast insitu works, and all fixings and accessories with all other related ancillaries as indicated or required.
Walls and partitions:
4.1.1 | 100mm thick | m2 | 778
4.1.2 | 120mm thick | m2 | 3982
4.1.3 | 150mm thick | m2 | 744
4.1.4 | 200mm thick | m2 | 36
4.2 | STONEWORK
Exterior Stonework as specified and/or detailed, installed complete; wet fixation (Mortar method); INCLUDING for substrate preparation; backing coats; sand, cement, supports and fixings; rebates, grooves, chamfers and the like; setting, jointing, grouting and finishing; trim and accessories; and all other related ancillaries as indicated or required
Reveals to openings: sills, soffits and jambs, stone1st choice unless otherwise noted, polished finish.
4.2.1 | 2 cm thick - 18 cm width | m | 7
4.2.2 | 2 cm thick - 31 cm width | m | 730
TOTAL AMOUNT MASONRY

## Div5
Division 05 - METALS
HARBATA GOVERNMENTAL HOSPITAL |  |  |  |  | Date: May, 2025
BILL OF QUANTITIES
Item | Description of Material | Unit | Quantity | Unit Cost | Total Cost
No. |  |  |  | (US $) | (US $)
DIVISON 5 - METALWORK
5.1 | SECTION 055000 - METAL FABRICATIONS
Metalwork components and assemblies as specified and detailed, fabricated and installed complete; INCLUDING for supports, brackets, anchorages, escutcheon ring, grout fixings and fasteners; hardware, accessories, trim and finishing, including finish painting; and all other related ancillaries as indicated or required.
5.1.1 | Handrail Staircase
Supply and install wall mounted galvanized steel hollow core tubular handrail including scrapping and applying two coats of anti corrosion protection & applying 3 coats of required paint and all related hand works and paste workmanship complete as shown on drawing and to the approval of the engineer
5.1.1.1 | Fixed to wall handrail for Stairs A&B | lm | 32
Floor Mounted galvanized steel handrail
Fabricate ,Supply and install floor mounted galvanized steel handrail ø 50mm which are composed of high quality steel durable with fixation angles with hardware and accessories and protective coating and finisher painting complete ready to use complete with engineer approval.
5.1.1.2 | Wall mounted handrail to Stairs A&B | lm | 32
Fabricate ,Supply and install floor mounted galvanized steel handrail ø 50mm which are composed of high quality steel durable with fixation angles with all related fixing and accessories and protective coating and finisher painting complete ready to use complete with engineer approval.
5.1.1.3 | Wall mounted handrail at external ramp | lm | 132
5.1.2 | Ladders
5.1.2.1 | Water tank access ladder; tubular stainless steel assembly. | No | 1
5.1.2.2 | top of Roof access ladders; galvanized tubular steel assembly. | No | 1
5.1.2.3 | Galvanized steel access hatch cover for water tank, including key rench; steel checkered plate, hinges, neoprene seal, etc…, and accessories as required by the engineer. | No | 1
5.1.3 | Canopy
Supply and install canopy complete, including covers glazing or as per selection of the Engineer, galvanized steel tube, supports, welds, steel plate fixed to concrete slab , tension rod, Bolts, fittings; and all necessary fixing and accessories, as specified and/or as shown on drawings
5.1.3.1 | Canopy at ground floor above entrances,2550 x 3800 mm or as shown on drawings | No | 9
5.1.4 | External fence
Supply and install external fence complete, including galvanized steel tube, supports, welds, steel plate, fixed to reinforced concrete upstand where required, fittings; paint and all necessary fixing and accessories, as specified and/or as shown on drawings
5.1.4.1 | 1200 mm high, External galvanized steel tube to fence distributed as shown on drawing | lm | 523
5.1.5 | Bollards
Supply and install external bollards complete, including stainless steel tube diameter 114 mm brushed finish grade 316, deep 500 mm, excavation backfilling, supports, welds, steel plate, fixed to concrete base unless otherwise noted, fittings; paint and all necessary fixing and accessories, as specified and/or as shown on drawings
5.1.5.1 | 1000 mm raised height, External stainless steel bollards as shown on drawing | No | 11
TOTAL AMOUNT METAL WORKS

## Div6
Division 6 - WOOD,PLASTIC AND COMPOSITE
HARBATA GOVERNMENTAL HOSPITAL |  |  |  |  | Date: May, 2025
BILL OF QUANTITIES
Item | Description of Material | Unit | Quantity | Unit Cost | Total Cost
No. |  |  |  | (US $) | (US $)
DIVISION 6 - WOODWORK
6.1 | SECTION 064023 - INTERIOR ARCHITECTURAL WOODWORK
Joinery and architectural woodwork assemblies and components as specified and detailed, fabricated and installed complete; INCLUDING for supports, brackets, anchorages, fixings and fasteners; hardware, ironmongery, accessories, trim and finishing, including finish painting; and all other related ancillaries as indicated or required.
Counters
Composite counter units complete; 20 mm marble cladding construction generally; including reinforced concrete backing and support walls, plaster and paint, 4 mm thick plywood board and paint with timber supported, finishing and decoration, curved shapes where required …etc. all as shown and detailed with 20mm first choice polished marble work top. refer to drawing
The Contractor shall submit complete shop drawing for each counter for approval by the engineer.
6.1.1 | Counter type C01,750 mm wide x 110 high x (365+223 mm) length or as shown on drawings, location reception hall GF01. | Item | 1
6.1.2 | Counter type C02,750 mm wide x 110 high x (284 mm) length or as shown on drawings, location secretary GF29 | Item | 1
6.1.3 | Counter type C03,750 mm wide x 110 high x (200+233 mm) length or as shown on drawings, location Secretary GF08 | Item | 1
6.1.4 | Counter type C04,750 mm wide x 110 high x (587 mm) length or as shown on drawings, location Nurse station GF67 | Item | 1
6.1.5 | Counter type C05,750 mm wide x 110 high x (551 mm) length or as shown on drawings, location Nurse station GF55 | Item | 1
6.2 | Resin Corian Counter work top
NOTE: Provide openings in Resin worktops for sinks, Work top counters units, and assemblies complete construction generally; including concrete plinths and resin worktops; floor mounted base cabinets and wall hung cabinets over where applicable, including for drawer units, adjustable shelves, under cabinet lighting fixtures, etc., all as shown on drawing.
6.2.1 | Countertop 600 mm wide, to Meat Preparation (length 7200 mm) | Item | 1
6.2.2 | Countertop 600 mm wide, to Vegetable Preparation (length 7500 mm) | Item | 1
6.2.3 | Countertop 600 mm wide, to Service (length 2200 mm) | Item | 1
6.2.4 | Countertop 600 mm wide, to washing & Disinfection area (length 3480 mm) | Item | 1
6.2.5 | Countertop 600 mm wide, to scrub up (length 2100 mm) | Item | 1
6.2.6 | Countertop 600 mm wide, to dirty corridor (length 1260 mm) | Item | 1
6.2.7 | Countertop 600 mm wide, to DU (length 2400 mm) | Item | 1
6.2.8 | Countertop 600 mm wide, to staff area (length 1160 mm) | Item | 1
6.2.9 | Countertop 600 mm wide, to receiving & separation (length 3500 mm) | Item | 1
6.2.10 | Countertop 600 mm wide, to nurse rest room (length 1880 mm) | Item | 1
TOTAL AMOUNT WOOD WORKS

## Div7
Division 07 - THERMAL & MOISTURE PROTECTION
HARBATA GOVERNMENTAL HOSPITAL |  |  |  |  | Date: May, 2025
BILL OF QUANTITIES
Item | Description of Material | Unit | Quantity | Unit Cost | Total Cost
No. |  |  |  | (US $) | (US $)
DIVISION 7 - THERMAL AND MOISTURE PROTECTION
7.1 | SECTION 075216 - SHEET WATERPROOFING
Sheet waterproofing membranes as specified and detailed, installed complete; INCLUDING for substrate preparation, primers and adhesives; joint laps, coatings, flashings and accessories; and all other related ancillaries as indicated or required
7.1.1 | Polyethylene sheet; vapour barrier, under concrete ground slabs | m2 | 3400
SBS modified bituminous sheet tanking to baried concrete structures; including for all preparatory work and protective course coverings
7.1.2 | Membrane protection to footing:Tilting fillet, primer, membrane angle reinforcement, two layer SBS modified bituminous membrane, 180g/m2 polyester, first layer 4mm thick & second Layer 4mm, 3cm concrete protection; must copl with the shoring system & sea water. | m2 | 3800
SBS modified bituminous coating waterproofing under façade aluminum composite column cladding; including for all preperation works and related ancillaries.
7.1.3 | Bituminous Coating to façade under alubond including; two coats of liquid bituminous cold applied as per manufacturer method statement requirment. | m2 | 680
7.2 | MEMBRANE ROOFING
SBS modified bituminous membrane roofing and deck assemblies as specified and detailed, installed in according to manufacturer instructions; INCLUDING for substrate preparation, primers, bonders, beds, fasteners and fixings; jointing and finishing; and all other related ancillaries as indicated or required.
Waterproofing system to roof
7.2.1 | Roofing comprising: | m2 | 3190
Concrete roof screed;
double layer modified bituminous membrane; (4mm thick) each
Protection sheet layer;
Area finish by sika tiles (or approved equal) including mastic sealant, support with all related fixing & accessories, all as specified or as shown on drawing
7.3 | SECTION 071416 - COLD FLUID-APPLIED WATERPROOFING
Supply and apply cold fluid Liquid applied waterproofing (PU) Complete; including primer, geotextile, preparation and all works required; as specified and as shown on Drawings
7.3.1 | To floors and perimeter of wet areas (minimum 30cm) | m2 | 294.1
7.4 | SECTION 075216 - ALUMINIUM CLADDING
Aluminium Composite Panels facing:
4mm thick aluminium composite panels cladding materials to facade as indicated on the drawings.
The surface is finished with fluocarbon coating top side surface finish and color as per consultant, as manufactorized by ALUCOBOND, ALUBOND or approved equivalent.
Price include galvanized steel supporting structure and structure finish with epoxy based paint.
7.4.1 | Aluminium composite panels cladding (external facade) | m2 | 366
7.5 | SECTION 0781413 - FIRE SAFING INSULATION
7.5.1 | Provide and install all fire safing insulation materials and components as specified, detailed and necessarily required; including but limited to openings and penetration through fire rated enclosures at mechanical and electrical shafts, ducts, sleeves and the like; INCLUDING for supports, anchors and fasteners; mastic sealer; and all other related ancillaries as indicated or required | L.S. | 1
7.6 | SECTION 079500 - EXPANSION CONTROL JOINTS
Provide and install expansion joint filler and sealer materials and components as specified, detailed, shown on Drawings and necessarily required, including recommended sealant, term bar-with lip/flat, joint filler, all related ancillaries as indicated or required (Refer to drawing)
7.6.1 | Preformed compressible joint filler | lm | 470
7.6.2 | Backing rod and mastic joint sealant; externally or internally, ceiling or roof surfaces (Aluminum section assembly for floor to floor expansion joint ) as shown on drawings. | lm | 188
7.6.3 | Backing rod and mastic joint sealant; externally or internally, wall to wall (Aluminum section assembly for wall to wall expansion joint ) as shown on drawings. | lm | 72
7.6.4 | Backing rod and mastic joint sealant; externally or internally wall to roof, (Aluminum section assembly for wall to roof expansion joint) as shown on drawings. | lm | 22
7.6.5 | Architectural, aluminum section expansion joint assemblies; complete including mastic joint sealant, backer rod; to floor finishes as specified and shown on drawings | lm | 188
TOTAL AMOUNT THERMAL AND MOISTURE PROTECTION

## Div8
Division 08 - OPENINGS
HARBATA GOVERNMENTAL HOSPITAL |  |  |  |  | Date: May, 2025
BILL OF QUANTITIES
Item | Description of Material | Unit | Quantity | Unit Cost | Total Cost
No. |  |  |  | (US $) | (US $)
DIVISION 8 - OPENINGS
* Price of Fire Rated Doors and Frames shall be deemed to include in the price.
* Price to be included card reader units
* Price to be included 6 mm thick clean glass with radiation shieldding (according to Door Schedule)
8.1 | SECTION 081113 - METAL DOOR FRAMES
Pressed steel profile door frames as specified and detailed; fabricated, supplied and installed completely to suit individual door dimensions stated and various wall thicknesses indicated ; INCLUDING for supports, anchors, grout filling, fasteners and fixings; protective coatings, sealants and finish painting; frame, fire rated where required and all other related ancillaries as indicated or required to the consent of the engineer and to his approval. (Refer to drawing)
8.1.1 | Door Type D140/LOUV, Steel hinged one leaf door louvered type, Dimension 1400x2200mm | No | 5
8.2 | SECTION 081416 - WOOD DOORS
Anti-bacterial high pressure Plastic laminate faced wood doors as specified, detailed and scheduled, installed complete; INCLUDING for door hardware sets anti-microbial, glass vision panels, and aluminium louvres; linings, edges, frame, fire rated where required, marble saddles or thresholds, trim and accessories; intemescent strip; prefinishing or finish painting; and all other related ancillaries as indicated or required
Door Schedules
8.2.1 | Door Type D125/T, Hinged- one leaf, Flush Door Solid Core Plastic Laminated With Beeches Edges FIRE RATED DOOR (1 hr), Dimension 1250x2200mm | No | 11
8.2.2 | Door Type D90/T, Hinged- one leaf, Flush Door Solid Core Plastic Laminated With Beeches Edges, Dimension 900x2200mm | No | 57
8.2.3 | Door Type D75/T, Hinged- one leaf, Flush Door Solid Core Plastic Laminated With Beeches Edges, Dimension 750x2200mm | No | 45
8.2.4 | Door Type D100/T, Hinged- one leaf, Flush Door Solid Core Plastic Laminated With Beeches Edges, Dimension 1000x2200mm | No | 7
8.2.5 | Door Type D80/T, Hinged- one leaf, Flush Door Solid Core Plastic Laminated With Beeches Edges, Dimension 800x2200mm | No | 12
8.2.6 | Door Type D160/OR, Hinged- two leaves, Flush Door Solid Core Plastic Laminated With Beeches Edges, Dimension 1600x2200mm | No | 2
8.2.7 | Door Type D160/GL, Hinged- two leaves with glass opening, Flush Door Solid Core Plastic Laminated With Beeches Edges, Dimension 1600x2200mm | No | 2
8.2.8 | Door Type D160/T, Hinged- two leaves, Flush Door Solid Core Plastic Laminated With Beeches Edges, Dimension 1600x2200mm | No | 2
8.2.9 | Door Type D140/T, Hinged- two leaves, Flush Door Solid Core Plastic Laminated With Beeches Edges, Dimension 1400x2200mm | No | 0
8.2.10 | Door Type D140/GL, Hinged- two leaves with glass opening, Flush Door Solid Core Plastic Laminated With Beeches Edges FIRE RATED DOOR(2hrs), Dimension 1400x2200mm | No | 21
8.3 | SECTION 085113 - ALUMINIUM DOORS AND WINDOWS
Aluminium powder coated framed door, window, entrance, and partition units as specified and detailed, installed complete; INCLUDING for sub-frames, transoms and mullions; glass, glazing and aluminium louvres; supports, anchors, fasteners and fixings; protective coatings and sealants; hardware, ironmongery, accessories and trim; frame and all other related ancillaries as indicated or required on drawings.
All aluminum section should be heavy dutty to take the double glazing and from available manufacturers, subject to compliance with requirements which may be incorporated in the work (Technal / Sedum or equal).
The contractor should submit complete shop drawing and samples showings all the details and accessories to be used.
Note: price to be include card reader unit where required
Aluminum Doors
8.3.1 | Door Type D100/AL, Hinged- two leaves opening, Aluminum Door Sedum 2000 + Glass, Dimension 1000x2200mm | No | 4
8.3.2 | Door Type D230/AL, Hinged- two leaves opening, Aluminum Door Sedum 2000 + Glass, Dimension 2300x2200mm | No | 1
8.3.3 | Door Type D100/CR, Hinged- one leaf opening, characteristics shall be specified by the manufacturer recommendation and approved of the Engineer, Dimension 1000x2200mm | No | 0
8.3.4 | Door Type D165/ACCO, Sliding- one leaf, slide door Accordeon core plastic, Dimension 1650x2200mm | No | 0
8.3.5 | Door Type D125/ACCO, Sliding- one leaf, slide door Accordeon core plastic, Dimension 1250x2200mm | No | 5
8.3.6 | Door Type D90/ACCO, Sliding- one leaf, slide door Accordeon core plastic, Dimension 900x2200mm | No | 2
8.3.7 | Door Type D73/ACCO, Sliding- one leaf, slide door Accordeon core plastic, Dimension 730x2200mm | No | 1
Access Door Type for Mechanical and electrical Shaft and where shown on drawings
8.3.8 | Door D148/ACCE, Access Door with aluminum frame, Door hinged two leaves Type (Aluminum + Fiber) at roof and where shown on drawings, Dimension 1480 x 1700 mm | No | 1
8.3.9 | Door D80/ACCE, Access Door with aluminum frame, Door hinged one leaf Type (Aluminum + Fiber) at roof and where shown on drawings, Dimension 800 x 1700 mm | No | 9
8.3.10 | Door D63/ACCE, Access Door with aluminum frame, Door hinged one leaf Type (Aluminum + Fiber) at roof and where shown on drawings, Dimension 630 x 1700 mm | No | 0
8.3.11 | Door D43/ACCE, Access Door with aluminum frame, Door hinged one leaf Type (Aluminum + Fiber) at roof and where shown on drawings, Dimension 430 x 1700 mm | No | 1
Aluminum Windows as shown on drawings
8.3.12 | W 253/AL, Sedum 2000 Aluminum Window, fixed panel, Dimension (2530 mm w x 1100 mm h) | No | 0
8.3.13 | W 455/AL, Sedum 2000 Aluminum Window, fixed panel, Dimension (4550 mm w x 1100 mm h) | No | 0
8.3.14 | W 285/AL, Sedum 2000 Aluminum Window, fixed panel, Dimension (2850 mm w x 1100 mm h) | No | 0
8.3.15 | W 160/AL, Sedum 2000 Aluminum Window, fixed panel, Dimension (1600 mm w x 1100 mm h) | No | 1
8.3.16 | W 375/AL, Sedum 2000 Aluminum Window, fixed panel, Dimension (3750 mm w x 1100 mm h) | No | 1
8.3.17 | W 165/AL, Sedum 2000 Aluminum Window, fixed panel, Dimension (1650 mm w x 1100 mm h) | No | 2
8.3.18 | W 90/AL, Sedum 2000 Aluminum Window, fixed panel, Dimension (900 mm w x 2390 mm h) | No | 1
8.3.19 | W 164'/AL, Sedum 2000 Aluminum Window, sliding two panels, Dimension (1940 mm w x 1100 mm h) | No | 3
8.3.20 | W 100'/AL, Sedum 2000 Aluminum Window, hinged-one leaf, Dimension (2530 mm w x 1100 mm h) | No | 2
8.3.21 | W 120/AL, Sedum 2000 Aluminum Window, sliding two panels, Dimension (1200 mm w x 1100 mm h) | No | 2
8.3.22 | W 100/AL, Sedum 2000 Aluminum Window, fixed panel, Dimension (1000 mm w x 1100 mm h) | No | 2
8.3.23 | W 194/AL, Sedum 2000 Aluminum Window, sliding two panels, Dimension (1940 mm w x 1100 mm h) | No | 24
8.3.24 | W 253/AL, Sedum 2000 Aluminum Window, fixed panel Dimension (2530 mm w x 1100 mm h) | No | 0
8.3.25 | W 64/AL, Sedum 2000 Aluminum Window, fixed panel Dimension (640 mm w x 640 mm h) | No | 11
8.3.26 | W 150/AL, Sedum 2000 Aluminum Window, sl;iding two panels, Dimension (1500 mm w x 1100 mm h) | No | 1
8.3.27 | W 194''/AL, Sedum 2000 Aluminum Window, fixed panel, Dimension (1940 mm w x 1100 mm h) | No | 3
8.3.28 | W 166/AL, Sedum 2000 Aluminum Window, fixed panel, Dimension (1660 mm w x 1100 mm h) | No | 1
8.3.29 | W 204/AL, Sedum 2000 Aluminum Window, fixed panel, Dimension (2040 mm w x 1100 mm h) | No | 2
8.3.30 | W 181/AL, Sedum 2000 Aluminum Window, fixed panel, Dimension (1810 mm w x 1100 mm h) | No | 1
8.3.31 | W 433/AL, Sedum 2000 Aluminum Window, fixed panel, Dimension (4330 mm w x 1100 mm h) | No | 3
8.4 | SECTION 088300 - MIRRORS
Supply and install recessed clear glass mirror, 6mm thick, framed or frameless unless otherwise noted including waterproof plywood backing and all necessary fixing accessories, as specified and/or as shown on drawings
8.4.1 | Mirror, dimensions 1030 mm wide x 687.5 mm high or as shown on drawings | No | 38
TOTAL AMOUNT OPENINGS

## Div9
Division 09 - FINISHES
HARBATA GOVERNMENTAL HOSPITAL |  |  |  |  | Date: May, 2025
BILL OF QUANTITIES
Item | Description of Material | Unit | Quantity | Unit Cost | Total Cost
No. |  |  |  | (US $) | (US $)
DIVISION 9- FINISHES
Section 092400 - Portland Cement Plaster
9.1 | Plaster to Receive Paint Finish
Prepare surfaces, spatter dash, supply and apply ordinary
Portland cement and sand plaster coat to a min. thickness of
20mm, include metal lath 1mm thick having approximately 50
nets per m2 where required, and all expanded metal angle and
stop beads at corners and abutments; scratching under layers
troweling to a smooth final layer unless noted otherwise. Inc-
lude forming drip over opening; as per specs and drawings
(1 undercoat of min.8mm, 1 undercoat of min. 6mm, 1 finish coat
of min. 6mm)
9.1.1 | To internal soffits | m2 | 810
9.1.1 | To internal walls | m2 | 2624
9.1.1 | W5; Barium plaster to walls as per X-ray machine manufacturer instructions | m2 | 110
9.1.1 | C7; Barium plaster to soffit as per X-ray machine manufacturer instructions | m2 | 33
9.1.1 | To external walls | m2 | 2710
9.2 | Plaster to Receive Tile Finish
Supply and apply 2 layers of Portland cement & sand plaster; minimum thickness of 8+8 mm; scratched upon completion to a maximum depth of 6mm; include all necessary material and accessories; as per the specifications and/or drawings
9.2.1 | To walls to receive tile finish | m2 | 2289
9.3 | Plaster to Unexposed Surfaces
Supply and apply 1 layer of Portland cement and sand plaster; minimum of 8mm thickness; include all necessary material and accessories; as per the specifications and drawings
9.3.1 | To internal soffits (Above false ceiling) | m2 | 1554
9.3.2 | To internal walls (Above false ceiling) | m2 | 1100
9.4 | Section 092900 - Gypsum Board Assemblies
Supply and install joint less gypsum board false ceiling; include suspension system, MDF visit traps, form of opening to electromechanical items, support and all necessary material and accessories; as per the specifications and/or drawings
9.4.1 | C6; Gypsum board suspended ceiling | m2 | 192
9.5 | Section 093000 - Ceramic Tile
Supply and place tile with bedding mortar and sand bed under floor tiles; including grouting, pointing, cleaning and all necessary material and accessories; as per the specifications and/or as per drawings
9.5.1 | F2; Industrial ceramic tiles 300x300mm (Quarry); 1st choice | m2 | 51
9.5.2 | F3; Non slip ceramic tiles 200x200mm | m2 | 1554
9.5.3 | S3; 100mm high industrial ceramic coved (Quarry) skirting | lm | 1323
9.5.4 | W1; 200x200mm glazed ceramic tiles | m2 | 1556
9.5.5 | S4; 100mm high ceramic coved skirting | lm | 40
Supply and install terrazzo tiles; include fine gravels bed, mortar, grout, cleaning, polishing, and all necessary material and accessories; as per the specifications and drawings
9.5.6 | F4,F5;Terrazzo tiles 200x200mm; 20mm thick (Under Vinyl) | m2 | 252
9.6 | Section 096340 - Dimension Stone Tiles
Supply and place tile with bedding mortar and sand bed under floor tiles; including grouting, pointing, cleaning polishing, and all necessary material and accessories; as per the specifications and/or drawings
9.6.1 | W6; 800x800x20 mm thick ؛Botticitino Marble; grade A; polished | m2 | 665
9.6.2 | F6; Botticino marble; grade A; polished risers, treads and landing | m2 | 250
9.6.3 | F7; 400X400X50 mm. Thick Cement tiles with exposed medium aggregate | m2 | 27
9.6.4 | S1; 100mm. High x 10mm. Thick serpeggaiante marble grade "A" polished skirting | lm | 1422
9.7 | Section 095123 - Acoustical Tile Ceilings
Supply and install false ceiling panels; include suspension system, anchors, form of opening to electromechanical works, and all necessary material and accessories; as per the specifications and/or drawings
9.7.1 | C5; Aseptic tiles antibacterial 60x60 Gypsum board vinyl faced and aluminum back | m2 | 311
9.8 | Section 095133 - Acoustical Metal Pan Ceilings
Supply and install false ceiling panels; include suspension system, anchors,, gypsum board where required and all necessary material and accessories; as per the specifications and drawings
9.8.1 | C3; Perforated Aluminum panels suspended ceiling; 600x600mm; | m2 | 287
9.8.2 | C4; Aluminum panels suspended ceiling; 600x600mm; | m2 | 764
9.9 | Section 095423 - Linear Metal Pan Ceilings
Supply and install false ceiling panels; include suspension system, anchors, and all necessary material and accessories; as per the specifications and drawings
9.9.1 | C2; Aluminum linear ceiling; 100mm wide | m2 | 0
9.10 | Section 096516 - Sheet Vinyl Floor Covering
Supply and install sheet vinyl floor covering antibacterial; include welding for the joints, adhesive, and all necessary material and accessories; as per the specifications and drawings
9.10.1 | F4; Anti static PVC sheet; welded joint conductive flooring; | m2 | 114
9.10.2 | F5; PVC sheet; welded joint conductive flooring; | m2 | 324
9.10.3 | S2; 100mm. High P.V.C. skirting coved & plied from the main P.V.C flooring sheet. joint shall be welded | lm | 199
9.10.4 | S5; 100mm. High Anti- Static P.V.C. skirting coved & plied from the main P.V.C flooring sheet. joint shall be welded | lm | 119
9.11 | Section 099123 - Paints
Latex Paint
Prepare surface, supply and apply antibacterial and hygiene paint consist of acrylic sealer, min. 3 coats of putty, one water base undercoat, three finish coats of Latex base acrylic odorless paint; as per the specifications and/or drawings
9.11.1 | To gypsum board suspended ceiling; Aseptic paint class 1 | m2 | 192
Solvent Base Paint
Prepare surface, supply and apply anti-bacterial and hygiene Enameled paint mat finish unless otherwise noted consist of acrylic sealer, 3 coats of putty, one solvent base undercoat, three finish coats of solvent base odorless paint; as per the specifications and drawings
9.11.2 | C1; To internal ceilings | m2 | 810
9.11.3 | W2; internal walls | m2 | 4299
9.11.4 | W5; internal walls | m2 | 110
Paint for Areas Above False Ceiling
Prepare surface, supply and apply anti-bacterial paint one coat of solvent borne alkali resistant acrylic primer, and two finish coats of highly effective acrylic paint (able to resist mold, algal and fungal growth); include all necessary material; as per the specifications and drawings
9.11.4 | To ceiling and walls | m2 | 2654
External Paint
Prepare surfaces, supply and apply from Tinol or equivalent approved one coat of waterproofing primer, an intermediate waterproofing paint coat, and one finish coat of medium textured as per the specifications and drawings.
9.11.5 | Scratched Paint to Façade white color type E01 | m2 | 1772
9.11.6 | Scratched Paint to Façade grey color type E02 | m2 | 109
9.12 | Section 099600 - High Performance Coatings
Prepare surface (shot blasting), supply and apply 1 coat of a two component polyamide cured sealer and 1 coat of a solvent free, two component high build polyamine cured epoxy paint "ASADOUR LB OF MAECO" Belgium or approved equal; as per the specifications and drawings
9.12.1 | F1; Epoxy paint to floor over screed (last measured separately) | m2 | 0
9.12.2 | W4; Non-toxic Epoxy paint min 400gr/m3 to wall | m2 | 199
TOTAL AMOUNT FINISHES

## Div10
Division 10 - SPECIALTIES
HARBATA GOVERNMENTAL HOSPITAL |  |  |  |  | Date: May, 2025
BILL OF QUANTITIES
Item | Description of Material | Unit | Quantity | Unit Cost | Total Cost
No. |  |  |  | (US $) | (US $)
DIVISION 10 - SPECIALITIES
10.1 | SECTION 101400 - SIGNAGE
Supply and install galvanized steel signage complete to road including concrete base, excavation backfilling, aluminum sign sheet with shape as indicated on drawing fixed to post by stainless steel clip, ghalvanized steel post diameter 76 mm (3.2 mm wall thickness) with gray paint deep 110 and raised 2550mm, mild steel plate 300x300x10 mm thick, weld End cap to post and all necessary fixing accessories, as specified and/or as shown on drawings
10.1.1 | Handicape parking signage | No | 2
10.1.2 | Give way signage | No | 35
10.1.3 | Pass Either side signage | No | 1
10.1.4 | Direction signage with variable shape as shon on drawing | No | 17
10.1.5 | Do not Enter signage | No | 3
10.1.6 | Stop signage | No | 1
10.1.7 | room signage | No | 125
TOTAL AMOUNT SPECIALITIES

## DIV 15
Division 15 - MECHANICAL WORKS
HARBATA GOVERNMENTAL HOSPITAL |  |  |  |  | Date: May, 2025
BILL OF QUANTITIES
Item | Description | Unit | Qty. | Unit Price US.$. | Total Price US.$.
15 - MECHANICAL WORKS
15.1 | GENERAL TECHNICAL REQUIREMENTS
Allow for compliance in full with the General Technical Requirements section of the specifications :
Scope regulations and standards .
Installation general
Electrical Services installation
Noise and vibration control
Inspection testing and commissioning
Handover procedures and documentation Below Ground Drainage
15.2 | SURFACE WATER MANHOLES
Surface water manholes complete as specified ; inver levels as required ; include manhole covers channels , fittings and accessories as required ; include excavation and disposal ;
15.2.1 | with heavy duty cover (1000x1000mm)- MH-3 | No | 2
15.2.1 | with heavy duty cover (800x800mm)- MH-2 | No | 1
15.2.2 | with heavy duty cover (600x600mm)- MH-1 | No | 48
15.3 | FOUL DRAINAGE
Below ground foul drainage pipewater installation complete as specified ; invert levels as required ; include all clean outs sleeves , fittings and accessories ; excavation and disposal ; bedding and surround to pipework ; pipe diameter
15.3.1 | 80mm | m | 25
15.3.2 | 100mm | m | 140
15.3.3 | 125mm | m | 120
15.3.4 | 150mm | m | 200
15.3.5 | 200mm | m | 110
15.3.6 | 250mm | m | 20
15.4 | FOUL MANHOLES
Foul manholes complete as specified ; invert levels as required ; include manhole covers , channels , fittings and accesssories as required , include excavation and diposal
15.4.1 | Grease trap complete as specified ; include fittings and accessories , excavation and disposal , concrete work etc . | No | 0
15.5 | SEWAGE TREATMENT PLANT
Supply, install and test package type sewage treatment plant complete with all required work including excavation, protection, waterproofing, civil works all as specified and as directed by the Engineer.
15.5.1 | SEWAGE TREATMENT PLANT OF CAPACITY 6M3/HR | No | 1
15.6 | Shop drawings and as built | No | 1
15.7 | SANITARY FIXTURES
15.7.1 | LAVATORIES
To be complete with all interconnecting pipework valves , mixers, installation and all accessories as specified
| LAV - 1 (half pedestal wash basin) | No | 8
| LAV - 2 (with pedestal wash basin) | No | 50
15.8 | WATER CLOSETS
15.8.1 | EWC - 1 (wall hang with concealed flush tank) | No | 8
15.8.2 | EWC - 2 (floor mounted with exposed flush tank) | No | 29
15.8.3 | Ablution spray complete with hand spray, flexible hose | No | 37
15.9 | SHOWER
Shower Tray with trap /strainer complete/shower
| fittings/drains/mixer..etc. | No | 8
15.1 | SINKS
15.10.1 | Dirty unit sink | No | 5
15.10.2 | Janitor unit sink | No | 4
15.10.3 | Sink- single bowl | No | 10
15.10.4 | Sink- double bowl | No | 0
15.10.5 | Scrubs | No | 3
15.11 | SANITARY PIPEWORKS
Sanitary fittings complete as specified ; include all necessary support , hangers , hoses , valves , traps , accessories and connections to services and wastes ;
Contractor to select appropriate tap sand thermostatic mixing unit , where required . Sanitary pipework complete as specified ; include all necessary supports , hanger , clean out , sleeves , openings fittings and accessories ; pipe diameter
15.11.1 | 50mm WITH INUSLATION FOR AC DRAIN | m | 1050
15.11.2 | 50mm | m | 950
15.11.3 | 80mm | m | 360
15.11.4 | 100mm | m | 430
NOTE:
1- ITEM 12.14 INCLUDES UPVC RAIN WATER, SOIL DRAIN PIPES AND VENT PIPES.
15.12 | FLOOR DRAIN
Floor drains complete as specified ; include all necessary supports , flashings strainers and accessories ; type F.D. - 1 ; size
A | 80mm | No | 112
B | FCO-100mm | No | 30
C | FCO - 80mm | No | 1
D | Gutter drain 100 with p- trap | No | 0
NOTE: | 1 / ITEM 12.14 INCLUDES UPVC RAIN WATER AND SOIL DRAIN PIPES .
15.13 | LABORATORY DRAINS
Laboratory drains complete as specified:include all necessary supports, flashing, strainers and accessories
A | 50mm dia | m | 24
B | 80mm dia | m | 18
15.14 | TRAPS FOR LABS
A | Traps for lab fixtures complete with accessories as required | item | 1
B | Neutralizing Pit (Full set with all eccessories and fittings) | item | 1
15.15 | RAINWATER PIPEWORK
Rainwater pipework complete as specified ; include all necessary supports , hangers clean outs , sleeves , openings , fittings and accessories ; include paint finish where required ; pipe diameter
| 80mm | m | 155
15.16 | RAINWATER ROOF DRAIN
Rainwater roof drains complete as specified ; include elevated dome strainer , flashing clamp collar , integral gravel guard , fittings and accessories ; type RD - 1 ; diameter
A | 80mm | No | 34
15.17 | RADIATORS
Supply and installation of radiators complete with manual air vent, return balancing valve, supports and all necessary accessories.
15.17.1 | 4 Elements | No | 1
15.17.2 | 7 Elements | No | 1
15.17.3 | 8 Elements | No | 2
15.17.4 | 9 Elements | No | 3
15.17.5 | 10 Elements | No | 14
15.17.6 | 11 Elements | No | 3
15.17.7 | 12 Elements | No | 1
15.17.8 | 13 Elements | No | 8
15.17.9 | 14 Elements | No | 7
15.17.10 | 15 Elements | No | 14
15.17.11 | 16 Elements | No | 8
15.17.15 | 17 Elements | No | 3
15.17.13 | 18 Elements | No | 4
15.17.14 | 20 Elements | No | 14
15.17.15 | 21 Elements | No | 3
15.17.16 | 22 Elements | No | 1
15.17.17 | 23 Elements | No | 6
15.17.18 | 24 Elements | No | 2
15.17.19 | 25 Elements | No | 11
15.17.20 | 28 Elements | No | 1
15.18 | DOMESTIC HOT AND COLD WATER
Domestic hot and cold water , softened water pipework as specified ; include all fittings bends ,tees , vents , and drains well , isolating and non return values , strainers , commissioning sets ,temperature and pressure ganges , flexible connections and other accessories , fire stops ,sleeves , joints , brackets and hangers for a complete installation ; include attendance to automatic control specialist and fitting of control devices ;pipe diameter
1 | Pipes
A | Cold water pipes hidden in walls and exposed @ ceiling level (PPR )
| 20 diameter. | m | 480
| 25 diameter. | m | 450
| 32 diameter. | m | 282
| 40 diameter | m | 132
| 50 diameter | m | 148
| 63 diameter | m | 170
| 75 diameter | m | 24
B | Hot water pipes hidden in walls and exposed @ ceiling level with insulation as specified (PPR with fiberglass layer)
| 20diameter. | m | 826
| 25 diameter. | m | 247
| 32 diameter. | m | 107
| 40 diameter | m | 143
| 50 diameter | m | 80
| 63 diameter | m | 19
C | Soft Cold Water Pipes (PPR)
| 20 diameter. | m | 38
| 25 diameter. | m | 160
| 32 diameter. | m | 30
| 40 diameter | m | 40
D | Soft Hot Water Pipes (PPR with fiber glass layer with insulation where specified)
| 20 diameter. | m | 115
| 25 diameter. | m | 95
| 32 diameter. | m | 35
| 40 diameter | m
E | HEATING SYSTEM PIPES
Heating pipework as specified ; include all fittings bends , tees , vents and drains wells , isolating and non return values , strainers , commissioning sets , temerature and pressure ganges , flexible connections and other accessories , fire stops , sleeves , joints , brackets and hangers for a complete installation ; include attenance to automatic control specialist and fitting of control devices ;
| Ø 20MM (1/2") | m | 585
| Ø 25MM (3/4") | m | 278
| Ø 32MM (1") | m | 215
| Ø 40MM (1 1/4") | m | 113
| Ø 50MM (1 1/2") | m | 128
| Ø 63MM (2") | m | 175
| Ø 75MM (2 1/2") | m | 4
| Ø 90MM (3") | m | 36
F | Fuel System Pipes (Black Steel Pipes)
| 1/2" diameter. | m | 12
| 3/4" diameter. | m | 6
| 1 1/4" diameter. | m | 30
| 2" diameter. | m | 15
2 | Valves
Supply, Install and Test the Following Fittings Complete as Specified and as Shown on Drawings:
A | Ball Valve
1/2" diameter.
| 3/4" diameter. | NB | 65
| 1" diameter. | NB | 100
| 11/4'' diameter. | NB | 13
| 11/2'' diameter. | NB | 4
| 2'' diameter. | NB | 1
| 21/2'' daiameter | NB | 1
B | Globe valve
| 3/4" diameter. | NB | 69
C | Water Meter Manhole
| Concrete Manhole including plastering hunching and benching, cover and frame manhole to be cast iron as manufactured by ok for 3 tons, including water meter WM-1 as above,Including strainer,check valve, valves complete with all accessories & fittings as detailed on the drawings… | NB | 1
D | Fuel filling cistern connection 1 1/4" (gate valve + check valve) | NB | 1
15.19 | EMERGENCY SHOWER
Emergency shower units for use in labs
| Complete as required | No | 1
15.2 | EXPANSION/CONTRACTION TANK SCHEDULE
| ET-1 (50liters) | No | 2
15.21 | CIRCULATING PUMPS
Circulating pumps as specified and scheduled ; include all pipework connections via anti vibration flexible connections , anti vibration base and mounts , control and power wiring from MCC , motor as specified , pressure and temperature gauges and tapping and non return valves , strainers , thermal insulation , bonding and identification System numbers
A | Circulting pump HWCP-R-1,2 | SET | 1
B | Circulting pump SHWCP-R-1,2 | SET | 1
C | Circulting pump HCP-GF-1,2 | SET | 1
D | Circulting pump HCP-GF-3,4,5 | SET | 1
15.22 | Connections to city water supply | LOT | 1
15.23 | COLD WATER PACKEGED BOOSTER PUMP SETS
Booster pumps as specified and scheduled ; include all pipework connections via anti vibration flexible connections , anti vibration base and mounts , control and power wiring from MCC , motor as specified , pressure and temperature gauges and tapping and non return valves , strainers , thermal insulation , bonding and identification System numbers
A | Booster pumps type BP-R-1,2,3 | SET | 1
B | Booster pumps type SWBP-R-1,2 | SET | 1
15.24 | COLD WATER TRANSFER PUMP SETS
Transfer pumps as specified and scheduled ; include all pipework connections via anti vibration flexible connections , anti vibration base and mounts , control and power wiring from MCC , motor as specified , pressure and temperature gauges and tapping and non return valves , strainers , thermal insulation , bonding and identification System numbers
A | TP-GF-1,2,3 | SET | 1
15.25 | Fuel Transfer Pump set
Fuel Transfer pumps as specified and scheduled ; include all pipework connections via anti vibration flexible connections , anti vibration base and mounts , control and power wiring from MCC , motor as specified , pressure and temperature gauges and tapping and non return valves , strainers , thermal insulation , bonding and identification System numbers
A | GO-GF-1,2 | SET | 1
15.26 | TANKS
A | CONCRETE WATER TANKS PREPARATION | No | 2
B | Under ground fuel tank 20m3 | No | 1
C | Daily Fuel tank 3m3 | No | 2
D | PE WATER TANKS (NTG) 8M3 | No | 5
E | PE WATER TANKS (NTG) 4M3 | No | 1
15.27 | HOT WATER STORAGE CALORIFIERS
A | HWST-R-1-1,2 | No | 2
B | SHWST-R-1-1 | No | 1
MEDICAL GASES INSTALLATION
15.28 | PREAMBLES
The contractor shall include for the design and installation of the system complete to achieve the requirements of the specification and the number of oulets as defined in the schedules , and the coordination with other trades Central plant associated with each system shall be identified as a cost item to include all elements not specifically indentified elsewhere costs for each outlets shall include the outlet points pipework and all costs not indicate elsewhere .
AGSS costs shall include for the associated wiring/control costs
Alarm panel costs shall include the panel , all associated wiring , pressure sensors , connection to local power supply etc .
Costs associated with pendants shall include all outlets , power points , fixing , support etc .
15.29 | CENTRAL SYSTEM
A | Oxygen Automatic Manifold | item | 1
Oxygen manifold with 12 cylinder on line, 6 reserve, 7 emergency capacity of each cylinder 9070 liter complete with all related works.
B | Duplex Medical Compressed Air Plant | item | 1
Plant net output 800LPM
Plant includes: three screen compressors with 15 kw each, air receiver, dryer assay, filter assay, valves, antivibration & Associated pipe work, electrical supply , complies with HTM 2022.
C | Duplex Pressure Reducing Station(10bar to 4bar) | item | 1
PRS comprises: Regulators with downstream press., Gauge, Pressure relief valves, isolation valve, Fittings and & all Necessary Accessories and Connections as Specified and as Shown on Drawings:
D | Duplex Pressure Reducing Station(10bar to 7bar) | item | 1
PRS comprises: Regulators with downstream press., Gauge, Pressure relief valves, isolation valve, Fittings and & all Necessary Accessories and Connections as Specified and as Shown on Drawings:
E | Nitrous oxide manifold with 4 cylinders on line, 4 emergency cylinders, capacity of each cylinder 9070 liter complete with all related works. | item | 1
F | Duplex Medical Vacuum Plant | item | 1
Plant: net output 2000 LPM
Plant includes: two pumps 15hp each 800lit/min. , vacuum receiver, bacterial filter assay, control panel, anti vibration, valves & associated pipe work, electrical supply, Complies with HTM 2022.
G | Duplex AGSS exhauster unit | item | 1
pump units & control equipment is mounted on A steel chassis together with necessary connections for installation & FRV included in the assay, electrical supply, complies with HTM 2022.
15.3 | OUTLETS (bed head unit price is included)
A | Oxygene - Wall mounted | No | 6
B | Oxygene - BHU mounted | No | 35
C | Nitrous Oxide - BHU mounted | No | 4
D | Air - 4 bar - BHU mounted | No | 33
E | Air - 7 bar - BHU mounted | No | 8
F | Vacuum - Wall mounted | No | 6
G | Vacuum - BHU mounted | No | 35
H | AGSS - BHU mounted | No | 4
15.31 | ALARMS INSTALLATION
Alarm Panels + valve box
A | Two outlets zone | No | 1
B | Three outlets | No | 3
C | Six outlets | No | 1
15.32 | PENDANTS
| OPT | No | 2
15.33 | LPG
A | LPG system serves kitchen and laboratory equipment . For kitchen etc . equipment Contractor to allow for upto & including final isolation valve, final connection . For laboratory Contractor to allow for isolating valve and 3m of pipework for each bech , capped off for extension | item | 0
B | Installation to comprise tanks , complete emergency shut off valves, drain , valves , contents gauges , safety control valves vents and fill points and pipework , temperature indicators pressure regulators , vapour balance pipework and fill point , pressure gauges on outflow and distribution pipework , all to comply with drawings and specification Tanks as above | No | 0
15.34 | COPPER PIPEWORK
Pipework complete with waterproof adhesive tape where buried , colour banding throughout all safety and isolating valves , outlets points as specified etc . to from a complete installation
A | copeer : 15mm | m | 243
B | copeer : 20mm | m | 154
C | copeer : 25mm | m | 318
D | copeer : 32mm | m | 24
E | copeer : 40mm | m | 26
15.35 | BOILER PLANT
| HOT WATER boilers as specified and scheduled, | No | 2
B-GF-1
15.36 | AIR HANDLING UNITS
Air handling units as specified and scheduled include all ductworks , pipeworks connections via flexible connections , control and power wiring , volume control dampers , attenuators , actuators , control ,drainage to nearest stack via glass traps , protection to drainage pipework , identification ,bonding and sundry ftments and accessories .
A | AHU-RF-1 | item | 1
B | AHU-RF-2 | item | 1
C | AHU-RF-3 | item | 1
D | FA-AHU-RF-1 | item | 1
E | FA-AHU-RF-2 | item | 1
F | FA-AHU-RF-3 | item | 1
G | FA-AHU-RF-4 | item | 1
NOTE:
1- ITEMS INCLUDES HEPA FILTER WHERE REQUIRED
15.37 | ROOM FAN COIL UNITS
Fan coil units specified and scheduled ; include heating and cooling coils , copper pipework , , thermostat(s) / sensor (s)s , control and small power wiring , and final connections , units to be 3 speed type with filter and insulated panels for quiet operation in accordance with the scheduled room noise limits; include insulated drain pans and drainage connection via running traps to the vertical soil stacks , bonding , identification and all sundry fittings , insulation and valve boxes.
15.37.1 | FCU-GF-01 | No | 1
15.37.2 | FCU-GF-02 | No | 1
15.37.3 | FCU-GF-03 | No | 1
15.37.4 | FCU-GF-04 | No | 1
15.37.5 | FCU-GF-05 | No | 1
15.37.6 | FCU-GF-06 | No | 1
15.37.7 | FCU-GF-07 | No | 0
15.37.8 | FCU-GF-08 | No | 0
15.37.9 | FCU-GF-09 | No | 1
15.37.10 | FCU-GF-10 | No | 1
15.37.11 | FCU-GF-11 | No | 1
15.37.15 | FCU-GF-12 | No | 1
15.37.13 | FCU-GF-13 | No | 1
15.37.14 | FCU-GF-14 | No | 1
15.37.15 | FCU-GF-15 | No | 1
15.37.16 | FCU-GF-16 | No | 1
15.37.17 | FCU-GF-17 | No | 1
15.37.18 | FCU-GF-18 | No | 1
15.37.19 | FCU-GF-19 | No | 1
15.37.20 | FCU-GF-20 | No | 1
15.37.21 | FCU-GF-21 | No | 1
15.37.22 | FCU-GF-22 | No | 1
15.37.23 | FCU-GF-23 | No | 1
15.37.24 | FCU-GF-24 | No | 1
15.37.25 | FCU-GF-25 | No | 0
15.38 | SPLIT SYSTEM
Split system air conditioning units , duty /standby , units n° . external condensing units as specified and detailed ; include refrigerant pipework , on board controls , external controls , and power wiring from MCC and internal control panels ; include acoustic canopy consisting of louvres , doors, wall and ceiling treatment as detail drawings , anti vibration mounting and fittings designed for quiet operation , as per specified room noise limits ; precharged with refrigerant , off loading , sitting testing and commissioning
15.38.1 | SP-9000 | No | 17
15.38.2 | SP-12000 | No | 13
15.38.3 | SP-18000 | No | 15
15.38.4 | SP-24000 | No | 17
15.39 | Refrigerant Pipes
| Supply, lay, connect and test the following copper pipes including all necessary fixing Accessories Insulation and Fittings complete as specified and as shown on drawings: | lm | 1800
15.4 | VENTILATION FANS
Supply fans as specified and scheduled include all ductwork connections via flexible connections , local isolators , power and control wiring , volume control dampers attenuations ductwork and inspections doors , identification and bonding and all accessories and sundry items
15.40.1 | FAF-RF-1 | No | 0
15.41 | EXTRACT FANS
Extract fans as specified and scheduled including all ductwork connections via flexible connections , local isolators , power and control wiring , volume control dampers attenuators , acoustic cladding to connections ductwork , and inspection doors , identification and bonding all sundry items System number :-
15.41.1 | EF-GF-1 | No | 1
15.41.2 | EF-RF-1 | No | 1
15.41.3 | EF-RF-2 | No | 1
15.41.4 | EF-RF-3 | No | 1
15.41.5 | EF-RF-4 | No | 1
15.41.6 | EF-RF-5 | No | 1
15.41.7 | EF-RF-6 | No | 0
15.41.8 | EF-TRF-1 | No | 3
15.41.9 | EF-TRF-2 | No | 1
15.42 | GALVANIZED STEEL METAL DUCTWORK
Galvanized sheet metal ductwork as specified access panels , turning vanes , test points , instrument points , accessories , supports , hangers and fittings , bonding and sundry fitments
15.42.1 | Supply & Return Air ductwork ( insulation is included) | Kg | 9100
15.42.2 | Exhaust ductwork | Kg | 1800
15.42.3 | FA ductwork (INSULATION IS INCLUDED) | Kg | 3000
15.42.4 | fire dampers | PC | 25
15.42.5 | volume control dampers | PC | 63
15.42.6 | Door grill 20*10 | PC | 36
15.43 | AIR DIFFUSERS SD
Supply air diffusers as specified ; include in built volume control damper , directional core, secret fixing to dutwork ; include coordination with room data sheets , engineer and ceiling erector , balancing and commissioning Supply Air Diffuser SD :-
15.43.1 | 300*300 | No | 11
15.43.2 | 450*450mm | No | 85
15.43.3 | 600*600mm | No | 0
15.44 | AIR REGISTER SR
15.44.1 | Exhaust ceiling diffuser
A | ECD 22.5*22.5 | No | 2
B | ECD 15*15 | No | 22
15.44.2 | FAG
A | FAG 15*10 | No | 23
B | FAG 15*15 | No | 13
C | FAG 20*10 | No | 2
D | FAG 20*15 | No | 2
E | FAG 20*20 | No | 1
15.45 | Laminar Flow Diffuser
| LFD 120X60 WITH 4-WAY SIDE CURTAINS | No | 2
15.46 | RETURN AIR DIFFUSERS RD / ED
Return air diffusers as specified ; include inbuilt volume control damper , matching core to supply air diffuser , secret fixing to ductwork , include coordination with room data sheets , architect and ceiling erector , balancing and commissioning Retun Air Diffusers RD : -
A | 300*300 | No | 11
B | 450*450 | No | 85
C | 600*600 | No | 0
15.47 | SOUND ATTENUATIONS
| Sound attenuators by specialist to air handling units , fans , as specified ; specialist to size attenuators and other acoustic measures to achieve specified room noise limits | item | 1
15.48 | FIRE PROTECTION
15.48.1 | PIPEWORK
Supply, Install, Connect and test fire fighting pipe laid horizontal and vertical including necessary valves, fittings, accessories and connections all as shown on drawings and as specified for a complete installation with all interconnecting pipework , booster pump valves , hoses(or racks ) cabinets , power supply and controls to MCC and all items to provide a complete system in compliance with NFPA
15.48.1 | 1" | m | 6
15.48.2 | 1 1/2" | m | 112
15.48.3 | 2 1/2" | m | 62
15.48.4 | 3" | m | 12
15.48.5 | 4" | m | 177
15.49 | Valves | item | 1
15.5 | Siamese connection unit | No | 2
15.51 | STANDPIPE PUMPS
Fire Pump Supply , Instal and Test, Set complete including pipe within pump room, valves, flexible connections, pressure vessel, pipe, strainer, vibration isolators, pre-wired control panels and electrical connection to local outlets complete as specified and as shown on drawings
A | Fire Pump FP - GF-1 | Item | 1
15.52 | Supply & Install Fire Hose Reels , fully Automatic 25mm X 30m Swing type Wall mounted cabinet with necessary fittings, accessories, valves , Landing valve a set of 5kg CO2 and 4.5kg fire dry chemical portable fire extinguisher etc,.. complete all as Specified, shown on drawings and to the Engineer's and Local Authorities Approval (Icluding pressure reducing Valves).
A | Hose reel and/or racks with Stand pipe | No | 10
15.53 | FIRST AID
First aid fire appliances as specified
15.53.1 | Wall mounted dry powder extinguishers (6Kg) | No | 30
15.53.3 | Wall mounted CO2 extinguishers ( 6Kgs) | No | 2
15.53.4 | Ceiling mounted dry powder extinguisher (9Kg) | No | 2
15.54 | FOAM INSTALLATION
Foam installation complete with all wiring , valves, tanks, sprinklers etc…
| FM200 System | item | 2
15.55 | WATER SOFTENER
Water softening Installation include :- Specialist advice , softeners / filters , brink tank controls , clorinator , wiring , connection to CCMS etc . as a complete operational system .System numbers :-
| SOFTNER-1 | item | 1
15.56 | RO SYSTEM
| RO-1 | item | 1
15.57 | THERMAL INSULATION AND IDENTIFICATION OF SERVICES
THERMAL INSULATION
Thermal insulation as specified complete with identification , all mastics , adhesive , mechanical fixings , final coverings and protective and decorative finishes
A | Pipework insulation , including ranges and | item | 1
B | valve boxes (Identification of Services) | item | 1
C | Chimney (Boiles, Fire Pump, Generators) | item | 1
TOTAL AMOUNT OF DIVISION 15

## DIV 16
HARBATA GOVERNMENTAL HOSPITAL |  |  |  |  | Date: May, 2025
Division 16 - ELECTRICAL WORKS
BILL OF QUANTITIES
Item | Description | Unit | Qty. | Unit Price US.$. | Total Price US.$.
CHAPTER 16- ELECTRICAL &TELEPHONE CONNECTIONS
16.1 | Wires and Cables
Cu/PVC/PVC: Supply, install and connect the following cables, PVC insulated, and copper conductors, complete including accessories, connectors, lugs, supports, clamps, and cable trays as shown on the drawings and as specified
Main Feeder Cables ( Cable De Liban )
16.1.1 | 3x4+4 mm2 | MR | 700
16.1.2 | 3x6+6 mm2 | MR | 300
16.1.3 | 4x2.5+2.5 mm2 | MR | 200
16.1.4 | 4x4+45 mm2 | MR | 400
16.1.5 | 4x6+6 mm2 | MR | 860
16.1.6 | 4x10+10 mm2 | MR | 450
16.1.7 | 4x16+10 mm2 | MR | 260
16.1.8 | 4x25+16 mm2 | MR | 95
16.1.9 | 4x35+16 mm2 | MR | 23
16.1.10 | 4x70+35 mm2 | MR | 80
16.1.11 | 4x95+35 mm2 | MR | 105
11.1.12 | 4x70mm2 | MR | 22
16.1.13 | 4x185mm2 | MR | 46
16.1.14 | 2(4x185mm2) | MR | 55
16.1.15 | 4x6 mm2 - FP 200 | MR | 25
16.1.16 | 4x10 mm2 - FP 200 | MR | 120
16.1.17 | 4x16 mm2 - FP 200 | MR | 48
16.1.18 | 4x2.5 mm2 (for floating switch and control) | Item | 1
16.2 | Electrical Cabinet, Boxes and Fittings
Supply, install and connect the following outlet boxes, complete including cabling/conduit works back to receptive panel boards, accessories as shown on the drawings and as specified (PVC or EMT conduit as per specification)
16.2.1 | Electrical outlet box rated 2x10 amp/220V | No | 25
16.2.2 | Electrical outlet box rated 2x16 amp/220 V | No | 1
16.2.3 | Electrical outlet box rated 2x20 amp/220 V | No | 62
16.2.4 | Electrical outlet box rated 4x10 amp/380 V | No | 9
16.2.5 | Electrical outlet box rated 4x16 amp/380 V | No | 5
16.2.6 | Electrical outlet box rated 4x20 amp/380 V | No | 5
16.2.7 | Electrical outlet box rated 4x25 amp/380 V | No | 9
16.2.8 | Electrical outlet box rated 4x32 amp/380 V | No | 1
16.2.9 | Electrical outlet box rated 4x40 amp/380 V | No | 5
16.2.10 | Electrical outlet box rated 4x63 amp/380 V | No | 2
16.2.11 | Electrical outlet box rated 4x160 amp/380 V | No | 2
11.3 | Cable Tray
Supply, install the following cable tray, hot dip galvanized complete including cable tray, support and all related accessories as shown on the drawings and as specified
16.3.1 | Cable tray 10x5 cm | MR | 30
16.3.2 | Cable tray 15x5 cm | MR | 117
16.3.3 | Cable tray 20x5 cm | MR | 123
16.3.4 | Cable tray 30x5 cm | MR | 135
16.3.5 | Cable tray 40x5 cm | MR | 10
16.3.6 | Cable tray 50x5 cm | MR | 141
16.4 | LIGHT POINT AND FIXTURES
Supply , install and connect lighting points including conduits, accessories and supports, junction, derivation and outlet boxes, conductors, connectors and all the accessories, as shown on the drawings and as specified NOTE : Conduits exposed above false ceiling and in slab shall be PVC rigid type heavy gauge and in mechanical room shall be EMT type
16.4.1 | 120cm LED recessed mounted panel, 33w, 4000k light color | No | 60
16.4.2 | 120cm LED recessed mounted panel, 33w, 4000k light color with 2 hours emergency kit | No | 15
16.4.3 | 20cm LED recessed mounted down light, 18w, 4000k light color | No | 51
16.4.4 | 20cm LED recessed mounted down light, 18w, 4000k light color with 2 hours emergency kit | No | 14
16.4.5 | 20cm LED recessed mounted panel, 25w, 4000k light color | No | 328
16.4.6 | 20cm LED recessed mounted panel, 25w, 4000k light color with 2 hours emergency kit | No | 95
16.4.7 | 20cm LED surface mounted panel, 25w, 4000k light color | No | 48
16.4.8 | 20cm LED surface mounted panel, 25w, 4000k light color with 2 hours emergency kit | No | 10
16.4.9 | 60cm LED surface mounted panel, 40w, 4000k light color | No | 10
16.4.10 | 60cm LED surface mounted panel, 40w, 4000k light color with 2 hours emergency kit | No | 3
16.4.11 | 60cm LED recessed mounted panel, 40w, 4000k light color | No | 71
16.4.12 | 60cm LED recessed mounted panel, 40w, 4000k light color with 2 hours emergency kit | No | 30
16.4.13 | 10w LED surface wall mounted lighting fixture, 4000k light color | No | 6
16.4.14 | 120cm led recessed mounted panel, 44.5w, 4000k light color, anti bacterial special for operation theaters. | No | 26
16.4.15 | Busy Led Lighting fixture | No | 4
16.4.16 | Decorative LED post lantern, 30w, warm white color,IP67 | No | 40
16.4.17 | Decorative LED post top led fixture, 50w, warm white color, IP67 | No | 25
16.4.18 | Surface mounted non maintained emergency lighting fixture, equipped with 1x1.3w LED lamp (3 hours duration). | No | 35
16.4.19 | Lighting outlet points | No | 871
16.4.20 | Galvanized Lighting mast, 6 meters | No | 21
16.5 | Wiring Devices
Supply, install and connect the following wiring devices, complete including cabling/conduit works back to receptive panel boards, accessories as shown on the drawings and as specified . NOTE : Conduits exposed above false ceiling shall be PVC rigid type and in mechanical room shall be EMT type,Bticino Matix,Legrand Arteor ,Vimar Plana or equivalent
16.5.1 | Wall mounted one way, one gang light switch | No | 127
16.5.2 | Wall mounted one way, two gang light switch | No | 36
16.5.3 | Wall mounted one way, three gang light switch | No | 10
16.5.4 | Wall mounted two way, one gang light switch | No | 58
16.5.5 | Wall mounted two way, two gang light switch | No | 29
16.5.6 | Wall mounted two way, three gang light switch | No | 6
16.5.7 | Wall mounted simplex socket outlet (2P+E) shouco type | No | 225
16.5.8 | Wall mounted simplex socket outlet (2P+E) shouco typem for TV Unit | No | 32
16.5.9 | Wall mounted simplex socket outlet (2P+E) shouco type , water proof | No | 12
16.5.10 | Wall mounted duplex socket outlet (2P+E) shouco type | No | 78
16.5.11 | Wall mounted simplex UPS socket outlet (2P+E), shouco red type | No | 45
16.5.12 | Wall mounted duplex UPS socket outlet (2P+E), shouco red type | No | 91
16.5.13 | Isolating transformer , 15 KVA used in operation theatre | No | 1
16.5.14 | Isolating transformer , 6 KVA used in ICU | No | 1
16.6 | Disconnecter Switches
Supply, install and connect the following isolating dissconnect complete including cabling/conduit works back to respective panelboards,with all related accessories as shown on drawings and as specified , ABB , Katco or equal
16.6.1 | Isolating switch rated 2x10A IP 65 | No | 13
16.6.2 | Isolating switch rated 2x16A IP 65 | No | 1
16.6.3 | Isolating switch rated 2x20A IP 65 | No | 5
16.6.4 | Isolating switch rated 4x10A IP 65 | No | 5
16.6.5 | Isolating switch rated 4x16A IP 65 | No | 5
16.6.6 | Isolating switch rated 4x20A IP 65 | No | 7
16.6.7 | Isolating switch rated 4x25A IP 65 | No | 1
16.6.8 | Isolating switch rated 4x32A IP 65 | No | 4
16.6.9 | Isolating switch rated 4x40A IP 65 | No | 1
16.6.10 | Isolating switch rated 4x63A IP 65 | No | 2
16.6.11 | Isolating switch rated 4x160A IP 65 | No | 1
16.7 | Supply, install and connect the following:
16.7.1 | Conduits and control wiring related to mechanical system (all pumps,AC and Fans) | LS | 1
16.8 | Earthing
| Earthing system shall be made by closed circuit cable of 95mm2 bare copper coductor with earth rods supplied installed, connected and tested complete with all the equipment and accessories,to ensure a resistance less than 5 ohms, including grounding of main electrical room, technical services, voids, attics, and fixed machinery / equipment as specified | LS | 1
16.9 | Panel Boards
Supply, install and connect the following panelboards, complete including protective devices, measuring devices, contactors, auxiliaries, and all related accessories as shown on drawings and as specified , ABB , Schneider or equal
16.9.1 | ATS, 4x630A | No | 1
16.9.2 | MDB | No | 1
16.9.3 | UMDB | No | 1
16.9.4 | USDB-XRAY | No | 1
16.9.5 | FDB-ER | No | 1
16.9.6 | FDB-OPD | No | 1
16.9.7 | FDB-PR | No | 1
16.9.8 | FDB-REC | No | 1
16.9.9 | FDB-CLNC | No | 1
16.9.10 | FDB-ICU | No | 1
16.9.11 | FDB-XRAY | No | 1
16.9.12 | FDB-LAB | No | 1
16.9.13 | FDB-EMR | No | 1
16.9.14 | FDB-SPL | No | 1
16.9.15 | FDB-ER-AC | No | 1
16.9.16 | FDB-OPD-AC | No | 1
16.9.17 | FDB-REC-AC | No | 1
16.9.18 | FDB-PR-AC | No | 1
16.9.19 | FDB-TF | No | 1
16.9.20 | FDB-ATS | No | 1
16.9.21 | UFDB-ER | No | 1
16.9.22 | UFDB-PR | No | 1
16.9.23 | UFDB-CLNC | No | 1
16.9.24 | UFDB-REC | No | 1
16.9.25 | UFDB-EMR | No | 1
16.9.26 | UFDB-ICU | No | 1
16.9.27 | UFDB-LAB | No | 1
16.9.28 | UFDB-OPD | No | 1
16.9.29 | UFDB-OR | No | 1
16.9.30 | UFDB-XRAY | No | 1
16.9.31 | MCC-1 | No | 1
16.9.32 | MCC-TF | No | 1
16.9.33 | MCC-FANS | No | 1
16.9.34 | ATS/EMERGENCY | No | 1
16.9.35 | ATS-FP | No | 1
16.9.36 | FDB-LIFT1 | No | 1
16.9.37 | FDB-LIFT2 | No | 1
16.1 | Uninterruptible power supply system UPS
Supply, install connect, test and commission the following uninterruptible power supply Units complete with batteries ,15 min, autonomy , and all needed cables panel board,Control interfaces software , Socomec , Schneider or equal
16.10.1 | UPS 15 KVA, 3Phase Input, 3 Phase Output | No | 1
16.10.2 | UPS 100 KVA,3Phase Input, 3 Phase Output | No | 2
16.16 | Lightning Protection System
| Supply, install connect, test and commission a complete lightning Protection System, including conductors, air terminals, down conductors, earth pits and all needed accessories etc, as specified and as shown in the drawing | LS | 1
16.12 | Telephone Distribution
Supply, install and connect the following telephone distribution fittings including all conduits, conduit fittings, boxes, fixing, accessories and wiring as specified and as shown on the drawings
16.12.1 | MDF Telephone cabinet (200 Pair) including surge arrestor | No. | 1
16.12.2 | Wall mounted telephone outlet RJ11 | No. | 73
16.12.3 | TEL. terminal box TC (60 Pair) | No | 1
16.12.4 | TEL. terminal box TC (50 Pair) | No | 2
16.12.5 | 50P Telephone cables Cat 3 | MR | 160
16.12.6 | 60P Telephone cables Cat 3 | MR | 90
16.13 | Electronic Private Automatic Branch Exchange
Supply, install and connect the following PABX complete including fixing,main key, accessories and batteries as specified and as shown on the drawings , Panasonic or equal
16.13.1 | PABX 100 Extension and 8 External line expendable | LS | 1
16.14 | Data Distribution
Supply, install and connect the following data distribution fittings including all conduits, conduit fittings, boxes, fixing, accessories and wiring as specified and as shown on the drawings , made in Europe or equal
16.14.1 | Main Data cabinet | LS | 1
16.14.2 | Floor Data cabinet | LS | 3
16.14.3 | Wall mounted data outlet UTP Cat 6, RJ45 | No | 71
16.14.4 | Wall/Ceiling mounted camera data outlet UTP Cat 6, RJ45 | No | 82
16.14.5 | Wall mounted access point data outlet UTP Cat 6, RJ45 | No | 22
16.15 | Addressable Fire Alarm System
Sypply, installed, connected and tested, complete working system including conduits, boxes, special conductors, junction derivation and outlet boxes, connectors, fittings and all the accessories and back batteries, as specified and shown on drawings , Simplex or Equal , Fire Cable FP 200 fire rated
16.15.1 | Fire Alarm Control Panel FACP, 4 Loops | LS | 1
16.15.2 | Addressable Smoke detector | No | 166
16.15.3 | Addressable Heat detector | No | 13
16.15.4 | Addressable electronic sounder | No | 13
16.15.5 | Addressable manual break glass | LS | 1
16.15.6 | Control and monitor module | No | 1
Dot Matrix Printer
16.16 | NURSE CALL SYSTEM
Sypply, install, connect and test, complete working system including conduits, boxes, special conductors, junction derivation and outlet boxes, connectors, fittings and all the accessories, including nurse call extension and push button lamp for each patient room , nurse call main unit at secretary counter , panic push button and cord push button
16.16.1 | Nurse Call System - Pateients DPT | Item | 1
16.16.2 | Nurse Call System - Emergency DPT | Item | 1
16.16.3 | Nurse Call System - ICU DPT | Item | 1
16.17 | Public Address System
Sypply, installed, connected and tested, complete working system including conduits, boxes, special conductors, junction derivation and outlet boxes, connectors, fittings and all the accessories, as specified and shown on drawings (all cables should be fire rated)
16.17.1 | Speakers , Quest or equal | No | 58
16.17.2 | Amplifiers , Quest or equal | Item | 1
16.17.3 | Stand Microphone , Quest or equal | No | 2
16.17.4 | Public address pull box | No | 1
16.17.5 | Public Address cabinet | No | 1
16.18 | Generators
Supply install and connect the following stand-by generating set complete including sound-proofing room, exhaust system, daily fuel tanks, anti-vibration absorbers, pipes, starting system, batteries and charger, sound-proofing works, connection to main fuel storage tank with all related auxiliaries and accessories required for proper operation as recommended by the manufacturer , Auto starter Battery changer
16.18.1 | Diesel generator set of 200 KVA | No. | 2
16.18.2 | Diesel generator set of 100 KVA | No. | 1
16.18.3 | Synchronization panel for two 200KVA and one 100KVA generators | No. | 1
16.18.4 | Installation of generator system , exhaust piping with stainless jacketing, hot air discharge system, daily fuel tank 2000L, fuel pump connected to the main tank, residential Muffler, floating concrete base for the Genset, etc… | LS | 1
16.19 | Satellite TV System :
Supply, install and connect the following TV system fittings including dishes, conduits, conduit fittings, fixing accessories, line amplifiers, splitters, tee-units, IF/RF switches and wiring as specified and as shown on the drawings with roof surge arrestor
16.19.1 | TV head end equipment Including all the dishes, the filters, the amplifiers & all needed accessories | LS | 1
16.19.2 | TV socket | LS | 19
16.19.3 | TV Wall mounted terminal box | No. | 4
16.19.4 | 9 input, 9 output Multiswitch | No. | 3
16.19.5 | 9 input, 6 output Multiswitch | No. | 1
16.2 | Closed Circuit TV System
Supply, install and connect CCTV Central console including multiplexer, switcher, switching relay modules, keyboard, monitors, time lapse DVR and all related accessories, supports, cable trunking, complete as shown on drawings and as specified and as recommended by the manufacturer.
16.20.1 | IP POE Colored Fixed Mini Dome Camera | No. | 43
16.20.2 | IP POE outdoor colored CCTV camera including | No. | 39
16.20.3 | Network video recorder (NVR), 64 Channels, 20 days storage | LS | 1
16.20.4 | Network video recorder (NVR), 32 Channels, 20 days storage | LS | 1
16.20.5 | 55" color LED video monitor | No. | 2
16.21 | BED HEAD UNIT SYSTEM
Supply, Install and Test bed head units for Single Bed Head Unit with all related accessories ,
16.21.1 | Bed Head unit of Single bed | No. | 30
16.22 | Supply , install and test Electrical lock, door card reader , card reader panel . | LS | 1
16.23 | Supply , install and test audio interphone. | LS | 1
16.24 | Transformer
Supply , install and connect 400 KVA transformer , oil type with Buchholz Relay , step down from 11.5 KV to 380 V , with voltage regulation , Switch gears and all related Accessories .
| Transformer , 400 KVA , oil type with 3 switch gears , 1 incoming , 1 outgoing and 1 for portection | LS | 1
16.25 | External works
16.25.1 | Supply , Install and connect main power supply(from EDL to transformer)and the telephone main cable , including power and telephone manholes , pipes , sleeves and all nessecary works and accessories (Excavation , duct banks , conduits , ect …)
16.25.2 | Power Manholes & Pipes | LS | 1
16.25.3 | Telephone Manholes & Pipes | LS | 1
16.25.4 | Allow for connecting the electrical and low current installations to site mains(3 pipes of 6 inches and 1 pipe of 2 inches) | LS | 1
16.26 | Allow for testing and commissioning of the entire electrical and low current works | LS | 1
16.27 | Allow for providing shop drawings for the entire of electrical and low current works | LS | 1
16.28 | Allow for providing as-built drawings for the entire of electrical and low current works | LS | 1
TOTAL AMOUNT OF DIVISION 16

## Div31
Division 31 - EARTHWORK
HARBATA GOVERNMENTAL HOSPITAL |  |  |  |  | Date: May, 2025
BILL OF QUANTITIES
Item | Description of Material | Unit | Quantity | Unit Cost | Total Cost
No. |  |  |  | (US $) | (US $)
DIVISION 31- EXCAVATION AND FILLING
N.B: Excavation quantities are measured net - allow in unit rate for the cost of all supplementary and excess quantities required for working space, side batter, volume bulking, compaction and the like.
A | Excavate to any depth in any type of material, INCLUDING for breaking out any existing walls, pavings, footings, underground walls, obstructions, utilities and the like; supporting sides of excavations; shoring, strutting, supporting and protecting existing structures adjacent; dewatering (if deemed necessary); trimming, compacting and testing; backfilling and filling to final design elevations; removal of surplus excavated material from site; and all other related ancillaries as indicated or required
N.B. No excavated sand to be removed or used for any type of work (refill, plaster, concrete, etc.) without the written approval of the engineer. All unsuitable excavation should be removed from site as per the engineer instruction. The excavation natural component are: - Agricultural soil. - Sand Cost of all the above should be included in the cost of the items below.
1 | Excavation to level as base line phase 1. The contractor must submit full shop drawings for all the excavation works showing all the levels, sections, and any required drawings, to be approved by the consultant. | m3 | 9400
B | Filling
Allow for backfilling with selected fill; include compaction of layers of 25cm and all necessary works; as per the specifications and drawings
2 | Under Building |  | 11486
C | Base Course
3 | Granular hardcore base course layer under grade slabs; 150mm compacted thickness; include subgrade preparation and compaction as required | m3 | 500
TOTAL AMOUNT EARTH WORK