## 650KVA BoQ
ADMA SWITCH
Supply of 2x 650KVA Generators
BILL OF QUANTITIES
ITEM | DESCRIPTION | UNIT | QTY | UNIT PRICE USD | TOTAL USD
Diesel-Engine-Driven Generator Set
A | 2.1 - Diesel-Engine-Driven Generator Set SECTION - 26 32 13.13.DG12 PRIME POWER 650KVA, 380Vac, 3ph, 50Hz | Ea. | 2 |  | 0
including the following:
2.2 - DIESEL ENGINE
2.3 - Electronic Governor
2.4 - ALTERNATOR
2.5 - AUTOMATIC VOLTAGE REGULATOR, 3-phase sensing
2.6 - PERMANENT MAGNET GENERATOR
2.7 - CONTROL PANEL - DSE 8610 or similar
2.10 - PROTECTION AND CONTROL EQUIPMENT shall include: Circuit breaker, 1000A, 4 Poles, 50kA at 415VAC, fixed, manually operated, with electronic trip control unit, and two (20 open/close position contacts (OF), Voltage release (MX), similar to Schneider ComPacT NS1000N with MicroLogic 5.0. Installation shall include all necessary accessories including terminal shields, intrephase barriers, etc.
Residual current protection relay, range 30mA - 30A, 220VAC 50Hz, front panel installation with sensor rated 1000A sensor, ratio 1/1000, similar to Schneider VigiPacT RHUs, and VigiPacT L1 type
2.11 - STARTER BATTERY - 12Vdc - Rating 200 AH, 1150 CCA
2.12 - BATTERY CHARGER, 10A, 24V, Similar to Deep Sea Electronics DSE 9470 MKII
2.13 - FUEL HOSES
2.15 - ENGINE COOLANT HEATER, 1000W, 220Vac, with preset thermostat
2.16 - MANUAL SUMP PUMP
2.17 - ENGINE EXHAUST SYSTEM - MUFFLER Rated sound level reduction of 37 dBA or more in order to ensure 63±2dBA at 1m.
2.18 - NEUTRAL CONNECTION
2.19 - EARTH BAR 300x100x10mm
B | Equip the generator ciruit breaker with necessary copper extension bars and space to terminate 4 sets of [4x185mm²] power cables and related earth cables 2 sets of [1x185mm²] with proper physical insulation between bars. | Ea. | 2 |  | 0
C | Remote monitoring of the two (2) generators using dedicated software with full read/write accessibility using Alfa LAN network. Recommended Software Deep Sea Electronics DSE8005 SCADA Suite. | Ea. | 1 |  | 0
D | 2.21 - Sound Proof Canopy ensuring a sound level of 63dBA ± 2dBA at 1m from source from all directions, at 100% load, according to noise criteria NC-55. Color code: RAL 7015 Final dimensions of the canopy shall be approved by Alfa engineer prior to execution to fit in the allocated space. Note: only one generator will be installed outdoor and the other generator will be installed inside existing generator room. | Ea. | 1 |  | 0
E | Supply and installation of the following exhaust system including, exhaust pipe, stack head, DPF, and Catalytic Converter. Metallic flanges shall be used to connect the different parts of the exhaust system. All steel parts shall be field-painted by a minimum of one base coat of primer and one finish coat of corrosion resistant and temperature resistant up to 600-650°C paint.
E1 | Diesel Particle Filter (DPF) known as soot filter - as per Section 44 11 00.00.DPF with filtration efficiency greater than 95%. DPF shall have a regeneration temperature ranges between 500°C – 600°C and pressure drop less than 300psi. The DPF shall be thermally insulated and suitable for outdoor installation and has a maintenance interval of 6000 hours. Shall be compliant to MoE 4/1 dated 1 Aug 2024. | Ea. | 2 |  | 0
E2 | DPF Monitoring System A. The monitoring system will notify the operator of possible system issues and will ensure a problem free operation during the whole life span of the system. Shall be compliant to MoE 4/1 dated 1 Aug 2024. The system shall consist of the following items: | Ea. | 2 |  | 0
a. Screen: 4.3-inch TFT color screen with sealed buttons b. Interface: 2x Ports, CAN 2.0B - SAE J1939 standard c. Memory: 256 MB Flash Memory SD Storage d. Protocols: 2 x CAN 2.0B e. Power supply: 8Vdc – 30Vdc f. Dry Contact: General Alarm dry contact (NC) g. Protection: IP66 h. Temperature Range: -20 to +85°C
Sensors: 1. Two (2) temperature sensors to monitor the DPF inlet/outlet temperatures in real time. 2. One (1) differential pressure sensor to monitor the DPF backpressure in real time.
E3 | Catalytic Converter to regulate CO, NOx, & SOx gases with 10 years / 22,000 hours life expectancy, and temperature ranges between 500°C – 600°C. Shall be compliant to MoE 4/1 dated 1 Aug 2024. | Ea. | 2 |  | 0
E4 | Catalytic Converter Monitoring System A. The monitoring system will notify the operator of possible system issues and will ensure a problem free operation during the whole life span of the system. Shall be compliant to MoE 4/1 dated 1 Aug 2024. The system shall consist of the following items: | Ea. | 2 |  | 0
a. Screen: 4.3-inch TFT color screen with sealed buttons b. Interface: 2x Ports, CAN 2.0B - SAE J1939 standard c. Memory: 256 MB Flash Memory SD Storage d. Protocols: 2 x CAN 2.0B e. Power supply: 8Vdc – 30Vdc f. Dry Contact: General Alarm dry contact (NC) g. Protection: IP66 h. Temperature Range: -20 to +85°C
Sensors: 1. Two (2) temperature sensors to monitor the DPF inlet/outlet temperatures in real time. 2. One (1) NOx sensor to monitor the upstream and downstream NOx concentraton and reducton efficiency in real time.
E5 | Stack Head for 8inch exhaust pipe for the outdoor generator with canopy only. Refer to attached drawing - MP602 - Chimney Stackhead - V1.03-8inch | Ea. | 1 |  | 0
E6 | Black steel pipe 8 inch of thickness 3mm with 50mm insulation of Rockwool and stainless steel 304 jacketing fixed to wall metellic supports with anti-vibration springs. | Lm | 5 |  | 0
E7 | Provision of 2 inch opening in the 8 inch exhaust pipe for emissions measurements. The opening shall be extruded and closed with flanged cover which can be easily removed. The opening should be thermally insulated. | Ea. | 2 |  | 0
F | Delivery FOT of the generators to ADMA Switch at Fatqa | Ea. | 2 |  | 0
G | Witness test of the new generator at factory | Ea. | 2 |  | 0
H | Commissioning of the new generator on site including testing, fine tuning, configuration, remote monitoring, etc. | Ea. | 2 |  | 0
|  |  |  | TOTAL | 0