# Technical Requirements – RFP for Rectifiers and Lithium Batteries for Core Sites

## 1 Scope

This Request for Proposal (RFP) covers the supply, delivery, installation, testing, and commissioning of DC power systems for core sites, including Rectifier systems (DC power plants), Lithium battery backup systems, and associated accessories, communication interfaces, and monitoring integration with the existing infrastructure. The objective is to ensure reliable, efficient, and scalable DC power to support core network and data equipment.

## 2 General Requirements

All proposed equipment shall be telecom-grade, designed for continuous 24/7 operation in indoor technical environments.

All equipment shall comply with IEC, UL, or equivalent international standards for safety, EMC, and performance.

The bidder shall provide complete documentation, including datasheets, system drawings, and interconnection diagrams.

The proposed systems shall be compatible with existing 48V DC architecture at the sites.

Equipment shall include remote monitoring and management capability (via SNMP/Modbus/TCP or equivalent).

The bidder shall provide a minimum five (5) years warranty for all supplied components.

Local technical support and spare parts availability shall be ensured.

The supplier shall be fully responsible for warehousing, handling, and safe storage of all supplied materials and equipment throughout the project execution period, until delivery, installation, and acceptance at the respective sites.

The warehousing facilities shall ensure proper environmental conditions, security, and protection against dust, humidity, and temperature variations, in accordance with the manufacturers’ recommendations.

The supplier shall be responsible for all implementation activities, including installation, interconnection, testing, system configuration, and commissioning of both rectifiers and battery systems, ensuring full operational readiness upon handover

The supplier shall ensure that all project activities — including engineering, installation, commissioning, and testing — are performed by qualified and certified personnel with relevant technical expertise in DC power systems and lithium battery integration.

The supplier shall provide an organizational chart and CVs of the key project team members, identifying their roles, qualifications, and years of experience.

At minimum, the supplier’s proposed project team shall include:

- Project Manager: with at least 5 years of experience in managing telecom or data center power infrastructure projects.

- Electrical/Power Engineer: certified or licensed, with a minimum of 3 years of experience in DC power system design and installation.

- Commissioning and Testing Engineer/Technician: trained on rectifier and LiFePO₄ battery commissioning, with vendor or OEM certification preferred.

The supplier shall provide a service and support plan describing:

- The implementation methodology, work schedule, and testing procedures.

- The warranty and after-sales support process, including response time, spare parts availability, and contact escalation matrix.

- The maintenance services available post-installation, including preventive and corrective maintenance coverage.

The supplier shall maintain a qualified service team based in Lebanon (either directly or through an authorized local partner) capable of providing on-site technical support within 24 hours of a fault notification during the warranty period.

The supplier may reuse the existing AC and DC power cables, provided that their condition, sizing, and insulation quality are verified and deemed suitable for the new installation.

Any reused cables shall comply with applicable electrical and safety standards.

A mandatory site visit will be scheduled prior to offer submission to allow bidders to assess the existing installation, cable routing, and power distribution setup.

The supplier shall include in their offer any required modifications, terminations, or replacements identified during the site visit

The supplier shall submit a detailed Project Implementation Plan (PIP) as part of the technical offer.

The PIP shall outline all project stages, including design review, factory acceptance (if applicable), material delivery, installation, testing, commissioning, and final acceptance.

The plan shall clearly define milestones, deliverables, dependencies, and responsibilities.

The total project implementation duration shall not exceed six (6) months from the date of Purchase Order (PO) issuance.

The PIP shall also include:

- A Gantt chart showing activities and timelines for each core site (Jdeideh, Justice, Bir Hassan, Tripoli, and Saida).

- Identification of critical path activities and risk mitigation measures.

- The required resources and manpower allocation per site.

Any delay in project completion beyond the approved timeline shall be subject to contractual penalties as defined in the contract.

The supplier shall be responsible for ensuring timely delivery of equipment, and adherence to safety and quality procedures during all implementation phases.

Progress reports shall be submitted bi-weekly to MIC2, detailing achieved milestones, pending actions, and forecasted completion.

## 3 Lithium Battery System Requirements

- General Requirements

| Parameter | Minimum Specification |
| --- | --- |
| Battery Type | Lithium Iron Phosphate (LiFePO₄ – LFP) |
| Nominal System Voltage | 48 VDC (compatible with existing DC bus) |
| Capacity | As per section 8 |
| Cycle Life | ≥ 6000 cycles @ 80% DoD, 25°C |
| Design Life | ≥ 10 years |
| Operating Temperature Range | −10°C to +55°C |
| Charge/Discharge rate | 1C minimum |
| Storage Temperature Range | −20°C to +60°C |
| Round Trip Efficiency | ≥ 95% |
| Communication Interface | RS485 / CAN / SNMP compatible with site DC controller |
| Battery Management System (BMS) | Integrated BMS with protection for voltage, current, temperature, and short-circuit |
| Enclosure Protection | IP20 minimum (indoor), cabinet form factor |
| Certifications | IEC 62619, UN 38.3, UL 1973 or equivalent |
| Safety Features | Flame-retardant casing, automatic isolation during fault, no thermal runaway propagation |
| Monitoring | Voltage, current, SOC, SOH, temperature via BMS |
| Installation | Modular, front-access design suitable for indoor racks |

- Compatibility Requirement:

- The supplied lithium battery systems shall be fully compatible with the existing DC power

- (rectifier) systems currently installed at the sites.

- In case direct electrical or communication compatibility is not achievable, the bidder must

- provide and include any necessary third-party interface equipment, converters, or

- communication adaptors required to ensure full and safe integration between the proposed

- batteries and the existing rectifiers.

- All additional components shall comply with the same safety, monitoring, and warranty

- conditions as the main equipment.

#### Fire Suppression System Requirements

Each battery cabinet shall be equipped with a dedicated automatic aerosol fire suppression unit:

- Type: Condensed aerosol, suitable for Class A, B, C, and electrical fires

- Activation: The aerosol units shall be automatically activated either by an integrated thermal sensor (rated between 68 °C and 93 °C) or electrically triggered through the site’s fire detection/alarm system.

- The activation threshold shall ensure rapid response before temperature or smoke levels reach hazardous conditions inside the cabinet.

- Compliance: UL 2775, NFPA 2010, or equivalent

- Safe for lithium battery applications (non-conductive, non-corrosive, no residue)

- Integrated status/alarm contacts for monitoring

- Maintenance-free for at least 10 years

- One aerosol unit per cabinet, sized according to internal volume

## 4 Rectifier System Requirements

| Parameter | Minimum Specification |
| --- | --- |
| Input Voltage | 230/400 VAC ±15%, 50 Hz |
| Output Voltage | Nominal −48 VDC, adjustable range −42 V to −58 V |
| Power Capacity | Scalable modular system, ≥ 96 kW per rack, expandable |
| Rectifier Module Rating | ≥3 kW hot-swappable modules |
| Efficiency | ≥ 95% (typical 96% at 50% load) |
| Power Factor | ≥ 0.99 |
| Redundancy | N+1 minimum configuration |
| Control and Monitoring | Integrated controller with LCD/LED display and SNMP/Modbus interface |
| Protections | Input surge, over-voltage, under-voltage, short-circuit, over-temperature, and reverse polarity protection |
| Alarm & Logging | Configurable alarms (dry contacts, SNMP traps) |
| Operating Temperature | −5°C to +45°C |
| Relative Humidity | Up to 95% non-condensing |
| Enclosure Protection | IP20 minimum (indoor type) |
| EMC & Safety Compliance | IEC 60950-1 / IEC 62368-1, EN 61000-6-2/4 |
| Monitoring Integration | Must integrate with existing site management system (via SNMP or similar protocol) |
| Warranty | Minimum 5 years |
| Installation | Rack-mounted or cabinet-based modular system, hot-swappable rectifiers |

### 5 DC Distribution Unit (DCDU) Requirements

The supplier shall provide DC Distribution Units (DCDUs) integrated or standalone, suitable for telecom-grade −48 VDC systems.
The DCDUs shall distribute DC power from the rectifier system to multiple load circuits and battery connections, providing isolation, protection, and monitoring as required.

| Parameter | Minimum Specification |
| --- | --- |
| Nominal Output Voltage | −48 VDC (adjustable up to 54.0 VDC) |
| Maximum Output Current Capacity | 3000 A continuous |
| Load Bus Bar – Fuse Type | Minimum 20 isolator fuse outputs, each rated 300 A |
| Load Bus Bar – circuit breaker | minimum 25 CB 63Amps and 15 CB 125Amps |
| Battery Connection | Four (4) battery fuse disconnections, each rated 1000 A |
| Bus Bar Material | Copper, tin-plated or equivalent corrosion-resistant finish |
| Protection Degree | IP20 or better (indoor installation) |
| Monitoring & Alarms | Voltage, current, fuse/CB status, battery disconnection status via dry contacts or SNMP interface |
| Installation | Rack or cabinet mount compatible with rectifier system |
| Compliance | IEC 60950-1 / IEC 62368-1 and EN 61000-6-2/4 or equivalent |
| Safety Features | Overcurrent, short-circuit, and reverse-polarity protection with visual and remote alarm indicators |

## 6 Documentation and Training

1. Supplier shall provide installation manuals, user manuals, and configuration guides for both systems.

2. Supplier shall conduct onsite training for the technical team covering operation, safety, and maintenance procedures.

## 7 Acceptance and Testing

All systems shall undergo Factory Acceptance Test (FAT) and Site Acceptance Test (SAT) witnessed by the client’s representatives. Acceptance criteria shall include verification of rated capacity, communication functions, and safety protections.

## 8 Quantities and Sizing – Core Locations

The following table lists the core locations and their required quantities/sizing for rectifiers and battery systems.

| Site Location | Rectifier System Size (kW) | Battery Bank Capacity (kWh) | DCDU | Number of Battery Strings | Notes / Remarks |
| --- | --- | --- | --- | --- | --- |
| Jdeideh | 288 | 672 | 0 | At least 4 strings per rack |  |
| Justice | 240 | 576 | 0 | At least 4 strings per rack |  |
| Bir Hassan | 240 | 576 | 0 | At least 4 strings per rack |  |
| Tripoli | 2 rectifiers 96kW each | 384 | 2 | At least 4 strings per rack |  |
| Saida |  | 384 | 0 | At least 4 strings per rack |  |