## Grade of Compliance Range
| RFT Scoring Sheet | Reference Number | SF-CF-87
|  | Owner | PRO/PMO
|  | Revision Code | 5.0
|  | Implementation Date | 2024-11-01
Grade of Compliance range from 0 to 2:
2 : Fully compliant
1 : Partially compliant
0 : Not compliant
K : Disqualification
* For Requirements defined as ''Killer'', a ‘’Fully Compliant’’ score should be the sole acceptable outcome. Failing to obtain a ‘’Fully Compliant’’ score on the requirements defined as Killers, will mandate immediate disqualification for bidders.

## Technical Scoring
| RFT Scoring Sheet | [11 empty] | Reference Number |  | SF-CF-87
[13 empty] | Owner |  | PRO/PMO
[13 empty] | Revision Code |  | 5.0
[13 empty] | Implementation Date |  | 2024-11-01
Project Name | Backup Batteries 1200AH
Article | Requirements | Weight | Responsible Entity | Supplier 1 | Supplier 2 | Supplier 3 | Supplier 4 | Supplier 5 | Supplier 6 | Remarks | Supplier 1 Final | Supplier 2 Final | Supplier 3 Final | Supplier 4 Final | Supplier 5 Final | Supplier 6 Final
0 | Introduction :This Document includes the technical specifications of Batteries working within the voltage range 48 V (Nominal voltage 54V, End of voltage of pilot Cells 43V, Single Cell voltage 1.8V at 25°C). | 10 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
1 | Codes and standards: The battery system must utilize well-established and reliable technology, substantiated by a minimum of 10 years of documented field performance. Additionally, it should be supported by a comprehensive global service network to ensure consistent maintenance and technical assistance worldwide. | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
2 | Type and operating mode: Lead acid, Valve regulated, and gas combining mode. | 50 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
3 | Quantity : . 432 Cells, each rated at 2V with a capacity of 1200AH, arranged across . 18 Metal racks designed to hold the batteries in a horizontal orientation | 10 | [8 empty] | 0 | 0 | 0 | 0 | 0
4 | Nominal voltage: It shall be 2 Volts per cell. | 10 | [8 empty] | 0 | 0 | 0 | 0 | 0
5 | Capacity: Each cell shall have 10 Hours capacity at 25°C to 1.80V/Cell, with 1200AH. That means: in case of Power failure the battery must be able to supply a discharge current of 120A during 10h at 25°C. The end of discharge voltage should be 43V/Rack (1.8V/Cell). | 100 | [8 empty] | 0 | 0 | 0 | 0 | 0
6 | Internal resistance: Each cell shall not have an internal resistance more than 1 milliohms at 25°C.B23 | 70 | [8 empty] | 0 | 0 | 0 | 0 | 0
7 | Short circuit current: Lab test with the short circuit current of each cell shall be in Amperes more than 1000A | 20 | [8 empty] | 0 | 0 | 0 | 0 | 0
8 | Recommended charging current: It shall not be less than 120 Amperes. | 20 | [8 empty] | 0 | 0 | 0 | 0 | 0
9 | Float voltage: It shall be in between 2.23 and 2.27 Volts per cell at 25°C, and shall remain stable ( + /- 0.05 V from average) throughout the battery life. | 10 | [8 empty] | 0 | 0 | 0 | 0 | 0
10 | Cycling: Each battery shall provide 1200 cycles to 80% depth of discharge or 5000 cycles to 20% depth of discharge. Cycle capabilities must be confirmed through lab testing. | 100 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
11 | Deep discharge: Following an equalisation charge, battery shall be capable of being recharged to rated capacity, from a discharge down to 1.5 Volts per cell. | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
12 | Flat discharge: Upon flat discharge (down to nearly 1.5 Volts), each cell shall provide at least five to six recoveries, with no special recharge procedure. | 20 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
13 | Self discharge: The battery shall have a maximum self-discharge rate of 0.5% per week at 25°C. | 20 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
14 | Recharge rate: The battery shall be capable of a 90% recharge within 12 hours when adhering to the above defined recharging parameters. | 20 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
15 | Initial Voltage drop : Initial voltage drop during discharge, shall not fall below 2.05 Volt per cell. | 20 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
16 | Recombination efficiency: It shall be of 97% or greater at 25°C operated at the specified float voltages. Water addition shall not be required due to container permeability, positive grid oxygen consumption, or the venting of un-combined gases. | 20 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
17 | Operating temperature: The battery shall be capable of operating in temperatures ranging from - 10°C to +40°C. Battery shall withstand hard freezing, without damage to the alloy, plates, or cell containment assembly. | 10 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
18 | Life time: It should be of twenty years, (or better). 1600 cycles at 60% DoD (C10, 20 °C) with design life 20 years | 100 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
19 | Ventilation: No special ventilation shall be required, and no special room shall be required, for battery house during operation. | 30 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
20 | Plates: The positive grid alloy shall be capable of deep cycle operation with low gassing, low corrosion rate, and low water loss characteristics. The negative grid shall offer a service life compatible with the positive plates | 30 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
21 | Separator: The positive and negative plates shall be separated by low resistance absorbent micro porous and chock proof material to immobilise and retain the battery electrolyte. The separator shall be compressed sufficiently to maintain separator to plate contact throughout the life of the cell (or better). | 30 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
22 | Electrolyte: The electrolyte shall be introduced to the cell through a computer-controlled fill-by-weight process (or better). | 30 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
23 | Container and cover: Valve regulated cell containers shall be impact and heat resistant. The cover should be attached to the container using a heat based double sealing process. The heat seal bead shall be smoothed to increase the cover-container bond strength. Container and cover shall be constructed of Flame retardant. | 100 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
24 | Pressure relief valve: Each cell shall have a self-releasing safety valve that operates under a minimum pressure of 3PSI. With a maximum of 10PSI. A flame arrestor shall be incorporated in the valve design. The valve assembly shall be removable and replaceable. | 10 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
25 | Design: a - All the cells must have the same recent manufacturing date; the manufacturing date must be labelled on each cell. b - The batteries received should not be older than five months. c - The batteries shall be installed in a horizontal position on suitable metal racks provided as part of the current offer | 150 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
26 | Product Identification Label: Each battery shall have a self adhering label identifying the product manufacturer, model, Origin of manufacturing, date of manufacturing, nominal voltage and nominal AH capacity. The label must be readily visible. | 30 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
27 | Manuals: The supplier shall provide a minimum of one complete set of installation and maintenance manuals. The instruction manual shall include a technical specifications, installation and maintenance procedures and the manufacturer’s recommended torque for connector bolts. | 10 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
28 | Warranty: The supplier shall provide, 2 years full Warranty covering battery repair and replacement. MIC1 team accepts that the installer will be present with them during the first 24 hours of the first recharge. | 150 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
29 | Recycling services: Both the battery and the metal rack must be suitable for recycling | 30 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
30 | Accessories: Each battery system shall be supplied with the necessary inter cell and inter module connectors. The connectors shall be lead plated copper. Lifting straps and other necessary hardware to complete the installation shall be provided. | 70 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
31 | Delivery: Batteries should be available and stored in supplier’s warehouse within 3 Months upon reception of order Confirmation. Delivery to MIC1 premises will be done according to MIC1 installation schedule. | 150 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
32 | Storing: The supplier shall provide, on his own expenses, housing for storing the batteries upon import and before installation. | 50 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
33 | Installation: Cells shall be mounted horizontally in the racks, allowing for easy testing and maintenance Cells shall be installed and designed to facilitate removal and replacement. | 100 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
34 | Labour work: Transport of batteries to the sites, labour work expenses for the installation of new batteries, dismounting of old batteries, and transport of spent batteries to destination of disposal at MIC 1, are full charge on the supplier expenses. That for the supplier should provide skilled workmen for the above tasks, as well as the transport vehicle. Transportation of batteries to the sites is full charge on the supplier expenses. | 200 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
35 | Installation schedule: The schedule of the installation on sites will be provided to the supplier upon receiving the batteries by the supplier. | 50 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
36 | Supervising: MIC1 will provide technical assistance for its GSM equipments in sites during installation of batteries. During the installation or reparation or replacement of the batteries, any damage caused to already existing equipment in sites and due to supplier, will be fully charged on the supplier’s expenses. | 10 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
37 | Offers: Supplier’s proposals and offers shall include the following information: detailed warranty proposals, prices, technical specifications that include all the characteristics mentioned above as well as certificate of origin and manufacturing of the batteries. | 100 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  | 1940 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
[11 empty] | SUPPLIER 1 SCORE | SUPPLIER 2 SCORE | SUPPLIER 3 SCORE | SUPPLIER 4 SCORE | SUPPLIER 5 SCORE | SUPPLIER 6 SCORE
* For Requirements defined as ''Killer'', a ‘’Fully Compliant’’ score should be the sole acceptable outcome. Failing to obtain a ‘’Fully Compliant’’ score on the requirements defined as Killers, will mandate immediate disqualification for bidders.
Note on D8: Entity (Department/ Unit) that identified the requirement and that will be responsible for its evaluation.
Note on E8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on F8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on G8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on H8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on I8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on J8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on E19: Evaluators Comments
Note on F19: Evaluators Comments
Note on G19: Evaluators Comments
Note on H19: Evaluators Comments
Note on I19: Evaluators Comments
Note on J19: Evaluators Comments
Note on E20: Evaluators Comments
Note on F20: Evaluators Comments
Note on G20: Evaluators Comments
Note on H20: Evaluators Comments
Note on I20: Evaluators Comments
Note on J20: Evaluators Comments
Note on E21: Evaluators Comments
Note on F21: Evaluators Comments
Note on G21: Evaluators Comments
Note on H21: Evaluators Comments
Note on I21: Evaluators Comments
Note on J21: Evaluators Comments
Note on E23: Evaluators Comments
Note on F23: Evaluators Comments
Note on G23: Evaluators Comments
Note on H23: Evaluators Comments
Note on I23: Evaluators Comments
Note on J23: Evaluators Comments
Note on E24: Evaluators Comments
Note on F24: Evaluators Comments
Note on G24: Evaluators Comments
Note on H24: Evaluators Comments
Note on I24: Evaluators Comments
Note on J24: Evaluators Comments

## Commercial Scoring
| RFT Scoring Sheet | [11 empty] | Reference Number |  | SF-CF-87
[13 empty] | Owner |  | PRO/PMO
[13 empty] | Revision Code |  | 5.0
[13 empty] | Implementation Date |  | 2024-11-01
Project Name
Article | Requirements | Weight | Responsible Entity | Supplier 1 | Supplier 2 | Supplier 3 | Supplier 4 | Supplier 5 | Supplier 6 | Remarks | Supplier 1 Final | Supplier 2 Final | Supplier 3 Final | Supplier 4 Final | Supplier 5 Final | Supplier 6 Final
1 | ARTICLE 1 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
1.1 | Sub-Article 1.1 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
1.1.1 | Item 1.1.1 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
1.1.1.1 | Requirement 1.1.1.1 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
1.1.1.2 | Requirement 1.1.1.2 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
1.1.1.3 | Requirement 1.1.1.3 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
1.1.2 | Item 1.1.2 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
1.1.2.1 | Requirement 1.1.2.1 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
1.1.2.2 | Requirement 1.1.2.2 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
1.1.2.3 | Requirement 1.1.2.3 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 | 0
[11 empty] | SUPPLIER 1 SCORE | SUPPLIER 2 SCORE | SUPPLIER 3 SCORE | SUPPLIER 4 SCORE | SUPPLIER 5 SCORE | SUPPLIER 6 SCORE
* For Requirements defined as ''Killer'', a ‘’Fully Compliant’’ score should be the sole acceptable outcome. Failing to obtain a ‘’Fully Compliant’’ score on the requirements defined as Killers, will mandate immediate disqualification for bidders.
Note on D8: Entity (Department/ Unit) that identified the requirement and that will be responsible for its evaluation.
Note on E8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on F8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on G8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on H8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on I8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on J8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on E12: Evaluators Comments
Note on F12: Evaluators Comments
Note on G12: Evaluators Comments
Note on H12: Evaluators Comments
Note on I12: Evaluators Comments
Note on J12: Evaluators Comments
Note on E13: Evaluators Comments
Note on F13: Evaluators Comments
Note on G13: Evaluators Comments
Note on H13: Evaluators Comments
Note on I13: Evaluators Comments
Note on J13: Evaluators Comments
Note on E14: Evaluators Comments
Note on F14: Evaluators Comments
Note on G14: Evaluators Comments
Note on H14: Evaluators Comments
Note on I14: Evaluators Comments
Note on J14: Evaluators Comments
Note on E16: Evaluators Comments
Note on F16: Evaluators Comments
Note on G16: Evaluators Comments
Note on H16: Evaluators Comments
Note on I16: Evaluators Comments
Note on J16: Evaluators Comments
Note on E17: Evaluators Comments
Note on F17: Evaluators Comments
Note on G17: Evaluators Comments
Note on H17: Evaluators Comments
Note on I17: Evaluators Comments
Note on J17: Evaluators Comments
Note on E18: Evaluators Comments
Note on F18: Evaluators Comments
Note on G18: Evaluators Comments
Note on H18: Evaluators Comments
Note on I18: Evaluators Comments
Note on J18: Evaluators Comments