## MIC2 requirements
Rectifiers and batteries for core sites | Compliance C1: Comply C2: Partially comply C3: Not comply * Except for the Killinng Factors it should be fully comply to avoid direct disqalification | Vendor Remarks Please indicate the reference of your compliance in the table under Vendor remarks ( Document, page, Etc.. )
Killing Factors
The offered rectifiers and batteries shall have been successfully installed and operational in at least five (5) Data Centers located in the European Union, USA, Gulf region, Far East, or Canada.
The bidder must provide at least three (3) project references executed during the last five (5) years with different major customers, demonstrating similar scope and complexity. However, in case the bidder does not directly hold such references, companies that are in an official joint venture or partnership with a well-established and internationally recognized company in the field of power and energy systems shall also be considered eligible, provided that:
The international partner possesses the required project references demonstrating similar scope and complexity; and
Valid documentation of the joint venture or partnership agreement is submitted as part of the technical offer; and
The bidder includes the international partner’s project references and credentials within the submission.
The bidder shall commit to execute the full project scope as defined in this RFP, including supply, installation, testing, commissioning, and training.
All proposed equipment shall be telecom-grade, designed for continuous 24/7 operation in indoor technical environments.
The proposed batteries must be Lithium Iron Phosphate (LiFePO4) chemistry.
The proposed batteries must be fully compatible with existing rectifiers that are not planned for replacement.
Batteries must be manufactured within a maximum of six (6) months prior to the purchase date
The batteries shall possess valid international safety certifications:· -IEC 62619 (Industrial Lithium Cells/Batteries) -UN 38.3 (Transport Safety) -UL 1973 and/or UL 9540A, or equivalent recognized standards.
The battery system must include an integrated Battery Management System (BMS) with: -Cell voltage balancing -Temperature, voltage, and current protection -Overcharge, over-discharge, short-circuit, and over-temperature protection -Automatic isolation under fault conditions
The proposed rectifiers must be fully compatible with the supplied LiFePO batteries, including but not limited to: -Charge voltage window -Communication protocols (CAN, RS485, Modbus, SNMP, etc.) -BMS integration and data exchange
Rectifiers must comply with IEC 62368-1 or IEC 60950-1 standards.
Both rectifiers and batteries must be UL/US or CE/EN listed.
All provided equipment shall be procured from licensed distributors operating in the Lebanese market
The bidder shall comply with the provisions of: Article 2 (Sub-clause 30, item C) Article 8 (Sub-clause 1, item B) of the Public Procurement Law no. 244/2022, whereby only one offer may be submitted. A valid Bid Bond shall be included in the sealed technical envelope. Any figures, prices, or price indicators mentioned in the technical offer shall lead to immediate disqualification of the bidder.
Any company whose shareholder, partner, manager, or board member has demonstrated hostility, defamation, or disrespect toward MIC2 or any of its managers or employees—whether verbally, in writing, or through any other means—shall be automatically disqualified from participating in the tender.
If such behavior occurs after the proposal submission, the company shall be immediately disqualified without liability to MIC2 and without any judicial action being required.
General Requirements
All proposed equipment shall be telecom-grade, designed for continuous 24/7 operation in indoor technical environments.
All equipment shall comply with IEC, UL, or equivalent international standards for safety, EMC, and performance.
The bidder shall provide complete documentation, including datasheets, system drawings, and interconnection diagrams.
The proposed systems shall be compatible with existing 48V DC architecture at the sites.
Equipment shall include remote monitoring and management capability (via SNMP/Modbus/TCP or equivalent).
The bidder shall provide a minimum five (5) years warranty for all supplied components.
Local technical support and spare parts availability shall be ensured.
The supplier shall be fully responsible for warehousing, handling, and safe storage of all supplied materials and equipment throughout the project execution period, until delivery, installation, and acceptance at the respective sites.
The warehousing facilities shall ensure proper environmental conditions, security, and protection against dust, humidity, and temperature variations, in accordance with the manufacturers’ recommendations.
The supplier shall be responsible for all implementation activities, including installation, interconnection, testing, system configuration, and commissioning of both rectifiers and battery systems, ensuring full operational readiness upon handover
The supplier shall ensure that all project activities — including engineering, installation, commissioning, and testing — are performed by qualified and certified personnel with relevant technical expertise in DC power systems and lithium battery integration.
The supplier shall provide an organizational chart and CVs of the key project team members, identifying their roles, qualifications, and years of experience.
At minimum, the supplier’s proposed project team shall include: -Project Manager: with at least 5 years of experience in managing telecom or data center power infrastructure projects. -Electrical/Power Engineer: certified or licensed, with a minimum of 3 years of experience in DC power system design and installation. -Commissioning and Testing Engineer/Technician: trained on rectifier and LiFePO₄ battery commissioning, with vendor or OEM certification preferred.
The supplier shall provide a service and support plan describing: -The implementation methodology, work schedule, and testing procedures. -The warranty and after-sales support process, including response time, spare parts availability, and contact escalation matrix. -The maintenance services available post-installation, including preventive and corrective maintenance coverage.
The supplier shall maintain a qualified service team based in Lebanon (either directly or through an authorized local partner) capable of providing on-site technical support within 24 hours of a fault notification during the warranty period.
The supplier may reuse the existing AC and DC power cables, provided that their condition, sizing, and insulation quality are verified and deemed suitable for the new installation.
Any reused cables shall comply with applicable electrical and safety standards.
A mandatory site visit will be scheduled prior to offer submission to allow bidders to assess the existing installation, cable routing, and power distribution setup.
The supplier shall include in their offer any required modifications, terminations, or replacements identified during the site visit
The supplier shall submit a detailed Project Implementation Plan (PIP) as part of the technical offer.
The PIP shall outline all project stages, including design review, factory acceptance (if applicable), material delivery, installation, testing, commissioning, and final acceptance.
The plan shall clearly define milestones, deliverables, dependencies, and responsibilities.
The total project implementation duration shall not exceed six (6) months from the date of Purchase Order (PO) issuance.
The PIP shall also include: -A Gantt chart showing activities and timelines for each core site (Jdeideh, Justice, Bir Hassan, Tripoli, and Saida). -Identification of critical path activities and risk mitigation measures. -The required resources and manpower allocation per site.
Any delay in project completion beyond the approved timeline shall be subject to contractual penalties as defined in the contract.
The supplier shall be responsible for ensuring timely delivery of equipment, and adherence to safety and quality procedures during all implementation phases.
Progress reports shall be submitted bi-weekly to MIC2, detailing achieved milestones, pending actions, and forecasted completion.
Lithium Battery System Requirements
Battery Type: Lithium Iron Phosphate (LiFePO₄ – LFP)
Nominal System Voltage: 48 VDC (compatible with existing DC bus)
Cycle Life: 6000 cycles @ 80% DoD, 25°C
Design Life: ≥ 10 years
Operating Temperature Range: −10°C to +55°C
Charge/Discharge rate: 1C minimum
Storage Temperature Range: −20°C to +60°C
Round Trip Efficiency: ≥ 95%
Communication Interface: RS485 / CAN / SNMP compatible with site DC controller
Battery Management System (BMS): Integrated BMS with protection for voltage, current, temperature, and short-circuit
Enclosure Protection: IP20 minimum (indoor), rack or cabinet form factor
Certifications: IEC 62619, UN 38.3, UL 1973 or equivalent
Safety Features: Flame-retardant casing, automatic isolation during fault, no thermal runaway propagation
Monitoring: Voltage, current, SOC, SOH, temperature via BMS
Installation: Modular, front-access design suitable for indoor racks
The supplied lithium battery systems shall be fully compatible with the existing DC power (rectifier) systems currently installed at the sites.
In case direct electrical or communication compatibility is not achievable, the bidder must provide and include any necessary third-party interface equipment, converters, or communication adaptors required to ensure full and safe integration between the proposed
All additional components shall comply with the same safety, monitoring, and warranty conditions as the main equipment.
Each battery cabinet shall be equipped with a dedicated automatic aerosol fire suppression unit: • Type: Condensed aerosol, suitable for Class A, B, C, and electrical fires • Activation: The aerosol units shall be automatically activated either by an integrated thermal sensor (rated between 68 °C and 93 °C) or electrically triggered through the site’s fire detection/alarm system. • The activation threshold shall ensure rapid response before temperature or smoke levels reach hazardous conditions inside the cabinet. • Compliance: UL 2775, NFPA 2010, or equivalent • Safe for lithium battery applications (non-conductive, non-corrosive, no residue) • Integrated status/alarm contacts for monitoring • Maintenance-free for at least 10 years • One aerosol unit per cabinet, sized according to internal volume
Rectifier System Requirements
Input Voltage: 230/400 VAC ±15%, 50 Hz
Output Voltage: Nominal −48 VDC, adjustable range −42 V to −58 V
Power Capacity: Scalable modular system, ≥ 96 kW per rack, expandable
Rectifier Module Rating: ≥3 kW hot-swappable modules
Efficiency: ≥ 95% (typical 96% at 50% load)
Power Factor: ≥ 0.99
Redundancy: N+1 minimum configuration
Control and Monitoring: Integrated controller with LCD/LED display and SNMP/Modbus interface
Protections: Input surge, over-voltage, under-voltage, short-circuit, over-temperature, and reverse polarity protection
Alarm & Logging: Configurable alarms (dry contacts, SNMP traps)
Operating Temperature: −5°C to +45°C
Relative Humidity: Up to 95% non-condensing
Enclosure Protection: IP20 minimum (indoor type)
EMC & Safety Compliance: IEC 60950-1 / IEC 62368-1, EN 61000-6-2/4
Monitoring Integration: Must integrate with existing site management system (via SNMP or similar protocol)
Warranty: Minimum 5 years
Installation: Rack-mounted or cabinet-based modular system, hot-swappable rectifiers
DC Distribution Unit (DCDU) Requirements
The supplier shall provide DC Distribution Units (DCDUs) integrated or standalone, suitable for telecom-grade −48 VDC systems.
The DCDUs shall distribute DC power from the rectifier system to multiple load circuits and battery connections, providing isolation, protection, and monitoring as required.
Nominal Output Voltage:−48 VDC (adjustable up to 54.0 VDC)
Maximum Output Current Capacity: 3000 A continuous
Load Bus Bar – Fuse Type: Minimum 20 isolator fuse outputs, each rated 300 A
Load Bus Bar – circuit breaker: minimum 25 CB 63Amps and 15 CB 125Amps
Battery Connection: Four (4) battery fuse disconnections, each rated 1000 A
Bus Bar Material: Copper, tin-plated or equivalent corrosion-resistant finish
Protection Degree: IP20 or better (indoor installation)
Monitoring & Alarms: Voltage, current, fuse/CB status, battery disconnection status via dry contacts or SNMP interface
Installation: Rack or cabinet mount compatible with rectifier system
Safety Features: Overcurrent, short-circuit, and reverse-polarity protection with visual and remote alarm indicators
Documentation and Training
Supplier shall provide installation manuals, user manuals, and configuration guides for both systems.
Supplier shall conduct onsite training for the technical team covering operation, safety, and maintenance procedures.
Acceptance and Testing
All systems shall undergo Factory Acceptance Test (FAT) and Site Acceptance Test (SAT) witnessed by the client’s representatives. Acceptance criteria shall include verification of rated capacity, communication functions, and safety protections.