## Grade of Compliance Range
| RFT Scoring Sheet | Reference Number | SF-CF-87
|  | Owner | PRO/PMO
|  | Revision Code | 5.0
|  | Implementation Date | 2024-11-01
Grade of Compliance range from 0 to 2:
2 : Fully compliant
1 : Partially compliant
0 : Not compliant
K : Disqualification
* For Requirements defined as ''Killer'', a ‘’Fully Compliant’’ score should be the sole acceptable outcome. Failing to obtain a ‘’Fully Compliant’’ score on the requirements defined as Killers, will mandate immediate disqualification for bidders.

## Technical Scoring
| RFT Scoring Sheet | [11 empty] | Reference Number |  | SF-CF-87
[13 empty] | Owner |  | PRO/PMO
[13 empty] | Revision Code |  | 5.0
[13 empty] | Implementation Date |  | 2024-11-01
Project Name | Backup Batteries 100AH
Article | Requirements | Weight | Responsible Entity | Supplier 1 | Supplier 2 | Supplier 3 | Supplier 4 | Supplier 5 | Supplier 6 | Remarks | Supplier 1 Final | Supplier 2 Final | Supplier 3 Final | Supplier 4 Final | Supplier 5 Final | Supplier 6 Final
1 | Introduction : This Document defines the characteristics and requirements of batteries working within the voltage range 48V (12V per block). In case of mains failure, the requested batteries must be able to deliver a backup discharge current for 2KVA RBS or equivalent DC Load. These backup Batteries will supply power for transmission equipment, 2 G and 3 G Radio Base station 48 V DC per rack. Batteries will be installed inside a box where temperature ranges is variable between -10°C and 40°C. | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
2 | Codes and standards: The battery design shall be of proven technology, with a minimum of 10 years of document field experience, and with world wide service support. | 50 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
3 | Type and operating mode: Lead acid, Valve regulated, and gas combining mode. | 10 | [8 empty] | 0 | 0 | 0 | 0 | 0
4 | Quantity : 100 AH The requested quantities are 400 Batteries having 100AH capacity per bloc (12V) | 10 | [8 empty] | 0 | 0 | 0 | 0 | 0
5 | Capacity: Each Bloc shall have 100 AH In case of Power failure the battery must be able to supply a discharge current of 10A during 10H at 25°C. The end of discharge voltage should be 10.5V/Bloc (1.75V/Cell). | 100 | [8 empty] | 0 | 0 | 0 | 0 | 0
6 | Recommended charging current: It shall not be less than 10 % of the battery capacity. | 20 | [8 empty] | 0 | 0 | 0 | 0 | 0
7 | Float voltage: It shall be in between 13.5 and 13.75 Volts per bloc at 25°C, and shall remain stable (+ /- 0.1 V from average) throughout the battery life. | 10 | [8 empty] | 0 | 0 | 0 | 0 | 0
8 | Cycling: Each battery shall provide 600 cycles to 60% depth of discharge. Cycle capabilities must be confirmed through lab testing. | 150 | [8 empty] | 0 | 0 | 0 | 0 | 0
9 | Deep discharge: Following an equalisation charge, battery shall be capable of being recharged to rated capacity, from a discharge down to 10 Volts per cell. | 30 | [8 empty] | 0 | 0 | 0 | 0 | 0
10 | Flat discharge: Upon flat discharge (down to nearly 10 Volts), each cell shall provide at least five to six recoveries, with no special recharge procedure. | 10 | [8 empty] | 0 | 0 | 0 | 0 | 0
11 | Self discharge: The battery shall have a maximum self-discharge rate of 0.5% per week at 25°C. | 20 | [8 empty] | 0 | 0 | 0 | 0 | 0
12 | Recharge rate: The battery shall be capable of a 90% recharge within 12 hours when adhering to the above defined recharging parameters. | 20 | [8 empty] | 0 | 0 | 0 | 0 | 0
13 | Recombination efficiency: It shall be of 97% or greater at 25°C operated at the specified float voltages. Water addition shall not be required due to container permeability, positive grid oxygen consumption, or the venting of un-combined gases. | 20 | [8 empty] | 0 | 0 | 0 | 0 | 0
14 | Operating temperature: The battery shall be capable of operating in temperatures ranging from - 10°C to, +40°C. Battery shall withstand hard freezing, without damage to the alloy, plates, or cell containment assembly | 10 | [8 empty] | 0 | 0 | 0 | 0 | 0
15 | Life time: It should be of 10 years, when operated at float voltages at 25°C. | 100 | [8 empty] | 0 | 0 | 0 | 0 | 0
16 | Ventilation: No special ventilation shall be required, and no special room shall be required, for battery house during operation. | 10 | [8 empty] | 0 | 0 | 0 | 0 | 0
17 | Plates: The positive grid alloy shall be capable of deep cycle operation with low gassing, low corrosion rate, and low water loss characteristics. The negative grid shall offer a service life compatible with the positive plates. | 10 | [8 empty] | 0 | 0 | 0 | 0 | 0
18 | Container and cover: Valve regulated cell containers shall be impact and heat resistant. Container and cover shall be constructed of fire-resistant material. | 200 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
19 | Design: a - Batteries must have the same recent manufacturing date; the manufacturing date must be labelled on each Block. b - Nominal AH capacity must be labelled and visible. c - The batteries received should not be older than five months. d - The batteries should be oriented in vertical position. e - Terminal type - Threaded Insert | 200 | [8 empty] | 0 | 0 | 0 | 0 | 0
20 | Product Identification Label: Each battery shall have a self adhering label identifying the product manufacturer, model, Origin of manufacturing, date of manufacturing, nominal voltage and nominal AH capacity. The label must be readily visible. | 50 | [8 empty] | 0 | 0 | 0 | 0 | 0
21 | Manuals: The supplier shall provide a minimum of 1 complete set of installation and maintenance manuals. The instruction manual shall include technical specifications, installation and maintenance procedures, and the manufacturer’s recommended torque for connector bolts. | 20 | [8 empty] | 0 | 0 | 0 | 0 | 0
22 | Warranty: The supplier shall provide 2 year full Warranty covering battery repair and replacement. | 150 | [8 empty] | 0 | 0 | 0 | 0 | 0
23 | Accessories: Each battery system shall be supplied with the necessary inter cell and inter module connectors. The connectors shall be lead plated copper. Lifting straps and other necessary hardware to complete the installation shall be provided. | 150 | [8 empty] | 0 | 0 | 0 | 0 | 0
24 | Delivery: 100 AH Delivery to MIC1 premises will be done according to MIC1 installation schedule. Batteries to be provided within maximum 3 months after issuing the purchase order. Batteries should be available and stored in supplier’s warehouse for 3 months upon reception of order confirmation. Delivery to MIC1 premises will be done according to MIC1 installation schedule. | 150 | [8 empty] | 0 | 0 | 0 | 0 | 0
25 | Storing: The supplier shall provide on his own expenses, housing for storing the batteries upon import and before installation. (For at least 2 months). | 50 | [8 empty] | 0 | 0 | 0 | 0 | 0
26 | Installation: - The batteries should be installed in the existing racks already used in MIC1 Sites (refer to the battery dimension below for more details). - Each rack has the space for 4 batteries. - Cells shall be mounted in the racks in Vertical position. - Cells shall be installed and designed to facilitate removal and replacement. - The installation will be carried out by Alfa employees. | 80 | [8 empty] | 0 | 0 | 0 | 0 | 0
27 | Offers: Supplier’s proposals and offers shall include the following information: detailed warranty proposals, Prices should be based on unit price, technical specifications that includes all the characteristics mentioned above as well as certificate of batteries origin and manufacturing. | 50 | [8 empty] | 0 | 0 | 0 | 0 | 0
28 | Dimensions: Dimension should not exceed the following: For the 100 Ah Height < 28.7 cm Length < 39.6 cm, Width < 10,8cm. | 200 | [8 empty] | 0 | 0 | 0 | 0 | 0
|  | 1880 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0
[11 empty] | SUPPLIER 1 SCORE | SUPPLIER 2 SCORE | SUPPLIER 3 SCORE | SUPPLIER 4 SCORE | SUPPLIER 5 SCORE | SUPPLIER 6 SCORE
* For Requirements defined as ''Killer'', a ‘’Fully Compliant’’ score should be the sole acceptable outcome. Failing to obtain a ‘’Fully Compliant’’ score on the requirements defined as Killers, will mandate immediate disqualification for bidders.
Note on D8: Entity (Department/ Unit) that identified the requirement and that will be responsible for its evaluation.
Note on E8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on F8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on G8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on H8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on I8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on J8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements

## Commercial Scoring
| RFT Scoring Sheet | [11 empty] | Reference Number |  | SF-CF-87
[13 empty] | Owner |  | PRO/PMO
[13 empty] | Revision Code |  | 5.0
[13 empty] | Implementation Date |  | 2024-11-01
Project Name
Article | Requirements | Weight | Responsible Entity | Supplier 1 | Supplier 2 | Supplier 3 | Supplier 4 | Supplier 5 | Supplier 6 | Remarks | Supplier 1 Final | Supplier 2 Final | Supplier 3 Final | Supplier 4 Final | Supplier 5 Final | Supplier 6 Final
1 | ARTICLE 1 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
1.1 | Sub-Article 1.1 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
1.1.1 | Item 1.1.1 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
1.1.1.1 | Requirement 1.1.1.1 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
1.1.1.2 | Requirement 1.1.1.2 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
1.1.1.3 | Requirement 1.1.1.3 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
1.1.2 | Item 1.1.2 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
1.1.2.1 | Requirement 1.1.2.1 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
1.1.2.2 | Requirement 1.1.2.2 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
1.1.2.3 | Requirement 1.1.2.3 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 | 0
[11 empty] | SUPPLIER 1 SCORE | SUPPLIER 2 SCORE | SUPPLIER 3 SCORE | SUPPLIER 4 SCORE | SUPPLIER 5 SCORE | SUPPLIER 6 SCORE
* For Requirements defined as ''Killer'', a ‘’Fully Compliant’’ score should be the sole acceptable outcome. Failing to obtain a ‘’Fully Compliant’’ score on the requirements defined as Killers, will mandate immediate disqualification for bidders.
Note on D8: Entity (Department/ Unit) that identified the requirement and that will be responsible for its evaluation.
Note on E8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on F8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on G8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on H8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on I8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on J8: Grade of Compliance: K: disqualification 0: Not compliant +5: Partially compliant +10: Completely compliant +15: Compliant with additional value, not initially included in the requirements
Note on E12: Evaluators Comments
Note on F12: Evaluators Comments
Note on G12: Evaluators Comments
Note on H12: Evaluators Comments
Note on I12: Evaluators Comments
Note on J12: Evaluators Comments
Note on E13: Evaluators Comments
Note on F13: Evaluators Comments
Note on G13: Evaluators Comments
Note on H13: Evaluators Comments
Note on I13: Evaluators Comments
Note on J13: Evaluators Comments
Note on E14: Evaluators Comments
Note on F14: Evaluators Comments
Note on G14: Evaluators Comments
Note on H14: Evaluators Comments
Note on I14: Evaluators Comments
Note on J14: Evaluators Comments
Note on E16: Evaluators Comments
Note on F16: Evaluators Comments
Note on G16: Evaluators Comments
Note on H16: Evaluators Comments
Note on I16: Evaluators Comments
Note on J16: Evaluators Comments
Note on E17: Evaluators Comments
Note on F17: Evaluators Comments
Note on G17: Evaluators Comments
Note on H17: Evaluators Comments
Note on I17: Evaluators Comments
Note on J17: Evaluators Comments
Note on E18: Evaluators Comments
Note on F18: Evaluators Comments
Note on G18: Evaluators Comments
Note on H18: Evaluators Comments
Note on I18: Evaluators Comments
Note on J18: Evaluators Comments